## Sheet1
Number | Incident State | Incident Type | Incident Priority | Site ID | MTN ID | MTN Region | Region / Province | State/District | Impact | AIRTEL ID | AIRTEL Region | Short description | Created | Opened by | Alarm Start | Alarm End | Alarm Duration | Outage Start Time | Outage End Time | Outage Duration | Maintenance Vendor | Primary Cause | RCA 1 | RCA 2 | RCA 3 | Affected Tenant / On Site | Affected Tenants | Affected Tenants Count | SBC Field Engineer | SBC Field Engineer 2 | SBC Field Engineer 3 | SBC OPS Head | SBC Regional Manager | SBC Supervisor | IHS Field Engineer | IHS RTO | IHS Head of Operation | Site Priority | Country | Notify | Cascaded Site Count | Resolution Comments | Resolution notes
NOCINC0006456101 | External Reconciliation | Site Down | P1 | IHS_ANA_1078A | AN0083 | ASB | Asaba | Anambra | 3 - Low | AN0979 | SOUTH EAST |  | 2025-11-26 08:59 | Oluwatoyin Fagite | 2025-11-26 08:57 | 2025-11-26 09:47 | 2989 | 2025-11-25 11:01 | 2025-11-26 09:47 | 22:46 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG high temperature alarm due low coolant level, coolant was added (No diesel outage after validation). | DG high temperature alarm due low coolant level, coolant was added (No diesel outage after validation).
NOCINC0006443792 | External Reconciliation | Site Down | P1 | IHS_DEL_1044A | DL0415 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 20:55 | Quadri Ogundare | 2025-11-24 20:55 | 2025-11-25 13:06 | 58277 | 2025-11-24 20:55 | 2025-11-25 13:06 | 16:11 | BJ Bison NGA | Access Denial | Community | Community Demands Not Met | Access Issue - Community | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | IHS FSE confirmed access issue due to community demands not met,DG was powered manually | Access issue was resolved and DG was powered manually
NOCINC0006468552 | Internal Reconciliation | Site Down | P1 | IHS_WAR_0034B | DL0736 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 22:57 | Oluwatobiloba Are | 2025-11-27 22:53 | 2025-11-27 23:24 | 1847 | 2025-11-27 22:53 | 2025-11-28 10:09 | 11:16 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006435762 | External Reconciliation | Site Down | P1 | IHS_IBA_0074B | OY4200 | IBD | Ibadan | Oyo | 3 - Low | OY1031 | WEST |  | 2025-11-23 21:14 | Mutmainnah Saba | 2025-11-23 21:14 | 2025-11-24 10:05 | 46265 | 2025-11-24 | 2025-11-24 10:05 | 10:05 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | Airtel NG |  | SUNDAY MOSES |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG lost compression, site restored on solar
NOCINC0006444211 | External Reconciliation | Site Down | P4 | IHS_KWA_0850A | KW2321 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 21:57 | Praise Okezie | 2025-11-24 21:56 | 2025-11-25 07:00 | 32644 | 2025-11-24 21:56 | 2025-11-25 07:00 | 9:04 | IPT | Access Denial | Security | Security Concerns In Site Environs | Access Issue - Security | 1 / 1 | MTN NG |  | Enorch Dauda |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Access issue due to site located at high risk area with security concerns. RCA: Cut charging alternator cable was fixed.
NOCINC0006463074 | External Reconciliation | Site Down | P1 | IHS_WAR_0922B | DL3276 | ASB | Asaba | Delta | 3 - Low | DL0934 | SOUTH SOUTH |  | 2025-11-27 08:27 | Mary Odefemi | 2025-11-27 08:26 | 2025-11-27 17:13 | 31604 | 2025-11-27 08:26 | 2025-11-27 17:13 | 8:47 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Faulty injector pump on main DG; MDG was deployed and power was restored
NOCINC0006454274 | External Reconciliation | Site Down | P3 | IHS_ANA_0893A | T4141 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 01:06 | Abundance Otunola | 2025-11-26 01:05 | 2025-11-26 09:30 | 30301 | 2025-11-26 01:05 | 2025-11-26 09:30 | 8:25 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | DG loss compression 20KV was deployed (No diesel outage after validation). | DG loss compression 20KV was deployed (No diesel outage after validation).
NOCINC0006479989 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0915A | T3858 | IBD | Ibadan | Oyo | 3 - Low | OY1032 | WEST |  | 2025-11-29 13:20 | Aishat Oyedeji | 2025-11-29 13:19 | 2025-11-29 21:17 | 28683 | 2025-11-29 13:19 | 2025-11-29 21:17 | 7:58 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Radiator Leakage | 2 / 2 | MTN NG, Airtel NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | DG high temp due to faulty radiator, MDG deployed to power the site
NOCINC0006445609 | External Reconciliation | Site Down | P2 | IHS_DEL_0994A | DL0029 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 06:48 | Solomon Bankole | 2025-11-25 06:47 | 2025-11-25 11:50 | 18217 | 2025-11-25 06:47 | 2025-11-25 14:34 | 7:47 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Suspected passive issue, Awaiting RCA from FSE
NOCINC0006486047 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1230A | AN0621 | ASB | Asaba | Anambra | 3 - Low | AN0776 | SOUTH EAST |  | 2025-11-30 11:00 | Abundance Otunola | 2025-11-30 10:59 | 2025-11-30 18:13 | 26055 | 2025-11-30 10:59 | 2025-11-30 18:13 | 7:14 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset (No diesel outage after validation) | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006450332 | External Reconciliation | Site Down | P4 | IHS_ANA_0893A | T4141 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 16:59 | Oluwatoyin Fagite | 2025-11-25 16:55 | 2025-11-25 23:52 | 25009 | 2025-11-25 16:55 | 2025-11-25 23:52 | 6:57 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG loss compression 20KV was deployed (No diesel outage after validation). | DG loss compression 20KV was deployed (No diesel outage after validation).
NOCINC0006468157 | External Reconciliation | Site Down | P3 | IHS_SAP_0009C | DL0869 | ASB | Asaba | Delta | 3 - Low | DL0632 | SOUTH SOUTH |  | 2025-11-27 21:47 | Oluwatobiloba Are | 2025-11-27 21:47 | 2025-11-28 04:41 | 24834 | 2025-11-27 21:47 | 2025-11-28 04:41 | 6:54 | BJ Bison NGA | Access Denial | Lease Or Legal | Landlord Related Issues | Access Issue - Land Lord | 2 / 2 | MTN NG, Airtel NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | IHS FSE confirmed Land lord access issue due to unpaid rent, DG was powered manually
NOCINC0006469183 | External Reconciliation | Site Down | P2 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-28 00:49 | Osarieme Charles | 2025-11-28 00:39 | 2025-11-28 07:08 | 23311 | 2025-11-28 00:41 | 2025-11-28 07:08 | 6:27 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 5 | Access security issues due to high risk (banditry), Site was visited at dawn RES: Faulty lift pump was worked on
NOCINC0006444695 | External Reconciliation | Site Down | P1 | IHS_OND_0972A | OD4737 | IBD | Ibadan | Ondo | 3 - Low | ON0597 | WEST |  | 2025-11-24 23:56 | Maureen Uchehorke | 2025-11-24 23:52 | 2025-11-25 06:08 | 22562 | 2025-11-24 23:51 | 2025-11-25 06:08 | 6:17 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Crankshaft | 2 / 2 | MTN NG, Airtel NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty crankshaft, kick starter and hooked cylinder was worked on
NOCINC0006468272 | External Reconciliation | Site Down | P4 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 22:04 | Emmanuel Faleti | 2025-11-27 22:03 | 2025-11-27 22:17 | 848 | 2025-11-27 22:03 | 2025-11-28 04:18 | 6:15 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is affected by ED4860. (No diesel outage after validation) | POFC: Site is affected by ED4860. (No diesel outage after validation)
NOCINC0006439927 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST |  | 2025-11-24 12:54 | Aderonke Olowojoba | 2025-11-24 12:19 | 2025-11-24 16:47 | 16080 | 2025-11-24 12:19 | 2025-11-24 18:10 | 5:51 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG primed to start. (No diesel outage after validation) | Weak DG primed to start. (No diesel outage after validation)
NOCINC0006484078 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0795A | T3172 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-30 01:34 | Okusanya Joseph | 2025-11-30 01:33 | 2025-11-30 07:16 | 20611 | 2025-11-30 01:33 | 2025-11-30 07:16 | 5:44 | IPT | Site Asset Theft | Theft | Theft | Backup Batteries | 1 / 1 | MTN NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Cables / Backup batteries theft .DG powered manually to restore the site.
NOCINC0006435880 | External Reconciliation | Site Down | P2 | IHS_WAR_0034B | DL0736 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-23 21:41 | Bukola Olabanji | 2025-11-23 21:39 | 2025-11-24 05:41 | 28895 | 2025-11-24 | 2025-11-24 05:41 | 5:41 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Suspected passive, awaiting update
NOCINC0006461639 | External Reconciliation | Site Down | P4 | IHS_OSU_0992B | OS4741 | IBD | Ibadan | Osun | 3 - Low | OS0722 | WEST |  | 2025-11-27 00:20 | Precious Attah | 2025-11-27 00:18 | 2025-11-27 05:52 | 20022 | 2025-11-27 00:18 | 2025-11-27 05:52 | 5:34 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty AVR was worked on
NOCINC0006458528 | External Reconciliation | Site Down | P4 | IHS_OND_0961A | OD2524 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 15:11 | Mary Elaigwu | 2025-11-26 15:11 | 2025-11-26 20:28 | 19041 | 2025-11-26 15:11 | 2025-11-26 20:28 | 5:17 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Atilola Mutiu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | faulty DG battery, external DG battery as used to power site
NOCINC0006468538 | External Reconciliation | Site Down | P2 | IHS_DEL_1051A | DL0091 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 22:54 | Patrick Okoro | 2025-11-27 22:54 | 2025-11-28 04:09 | 18854 | 2025-11-27 22:54 | 2025-11-28 04:09 | 5:14 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | DG Low Battery | 1 / 1 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty DG battery, External starter battery was used to power the site | Faulty DG battery, External starter battery was used to power the site
NOCINC0006465017 | External Reconciliation | Site Down | P2 | IHS_OSU_0042B | OS4285 | IBD | Ibadan | Osun | 3 - Low | OS0738 | WEST |  | 2025-11-27 13:16 | Titus Tosin | 2025-11-27 13:14 | 2025-11-27 18:24 | 18587 | 2025-11-27 13:14 | 2025-11-27 18:24 | 5:10 | IPT | Access Denial | Community | Community Demands Not Met | Access Issue - Community | 2 / 2 | MTN NG, Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Access was was deny by community due to noise DG access was temporary granted - faulty injector pump was worked on
NOCINC0006476117 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1470B | AN3650 | ASB | Asaba | Anambra | 3 - Low | AN1080 | SOUTH EAST |  | 2025-11-28 22:28 | Akachukwu Ugwu | 2025-11-28 22:24 | 2025-11-29 03:31 | 18432 | 2025-11-28 22:24 | 2025-11-29 03:31 | 5:07 | Tyllium NGA | Access Denial | Lease Or Legal | Landlord Related Issues | Access Issue - Land Lord | 2 / 2 | MTN NG, Airtel NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Landlord denied team access to the site, access was granted and DG was powered manually(No diesel outage after validation) | Landlord denied team access to the site, access was granted and DG was powered manually(No diesel outage after validation)
NOCINC0006483959 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0878A | T3596 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 00:24 | Okusanya Joseph | 2025-11-30 00:23 | 2025-11-30 05:24 | 18038 | 2025-11-30 00:23 | 2025-11-30 05:24 | 5:01 | SPS | Access Denial | Security | Security Concerns In Site Environs | Access Issue - Security | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Access Restriction due to security concern at high risk area, RCA: Weak DG was primed to start
NOCINC0006472483 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1085A | AN0303 | ASB | Asaba | Anambra | 3 - Low | AN1045 | SOUTH EAST |  | 2025-11-28 13:20 | Kehinde Akinbowale | 2025-11-28 13:18 | 2025-11-28 18:11 | 17580 | 2025-11-28 13:18 | 2025-11-28 18:11 | 4:53 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | Airtel NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting Feedback from FSE | Suspected passive Issue on site, Awaiting Feedback from FSE
NOCINC0006476892 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1470B | AN3650 | ASB | Asaba | Anambra | 3 - Low | AN1080 | SOUTH EAST |  | 2025-11-29 03:34 | Akachukwu Ugwu | 2025-11-29 03:31 | 2025-11-29 08:03 | 16301 | 2025-11-29 03:31 | 2025-11-29 08:03 | 4:32 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | Airtel NG, MTN NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG high temperature due to low coolant level, Coolant was added(No diesel outage after validation) | DG high temperature due to low coolant level, Coolant was added(No diesel outage after validation)
NOCINC0006439492 | External Reconciliation | Site Down | P3 | IHS_EDO_0012B | ED5016 | IBD | Asaba | Edo | 3 - Low | ED0637 | SOUTH SOUTH |  | 2025-11-24 11:18 | Oluwatomisin Sogbesan | 2025-11-24 11:16 | 2025-11-24 11:29 | 808 | 2025-11-24 11:16 | 2025-11-24 15:28 | 4:12 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty rectifier module was replaced. (No diesel outage after validation). | Faulty rectifier module was replaced. (No diesel outage after validation).
NOCINC0006437511 | External Reconciliation | Site Down | P4 | IHS_KWA_0883A | KW2371 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 02:36 | Abisoye Olaleye | 2025-11-24 02:35 | 2025-11-24 06:35 | 14414 | 2025-11-24 02:35 | 2025-11-24 06:35 | 4:00 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | MTN NG |  | Adelola Dagunduro |  |  | Paul Akpomie | Adelola Dagunduro |  | Rilwan Akeem | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Low Frequency AVR was readjusted
NOCINC0006440638 | External Reconciliation | Site Down | P3 | IHS_EDO_1051C | ED6129 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 13:49 | Evelyn Emagurehor | 2025-11-24 13:46 | 2025-11-24 17:45 | 14346 | 2025-11-24 13:46 | 2025-11-24 17:45 | 3:59 | MPI NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation) | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006479707 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0882C | EK4514 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 12:46 | Maureen Uchehorke | 2025-11-29 12:45 | 2025-11-29 16:38 | 13955 | 2025-11-29 12:45 | 2025-11-29 16:38 | 3:53 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Charging Alternator | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | faulty charging alternator was replaced
NOCINC0006476455 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0760A | T3127 | IBD | Ibadan | Kwara | 3 - Low | KW0651 | WEST |  | 2025-11-29 00:08 | Titus Tosin | 2025-11-29 00:06 | 2025-11-29 03:53 | 13603 | 2025-11-29 00:06 | 2025-11-29 03:53 | 3:47 | IPT | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 1 / 2 | MTN NG |  | Enorch Dauda |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 5 | Grid to DG synchronization failure due to incomplete phase, DG was powered manually.
NOCINC0006459185 | External Reconciliation | Site Down | P2 | IHS_OSU_0929A | OS2725 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 16:52 | Ifechi Ugwueze | 2025-11-26 16:48 | 2025-11-26 20:12 | 12236 | 2025-11-26 16:48 | 2025-11-26 20:12 | 3:24 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | DG lost compression, engine was swapped
NOCINC0006470293 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0903A | KW4576 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 07:27 | Osarieme Charles | 2025-11-28 07:27 | 2025-11-28 10:48 | 12091 | 2025-11-28 07:27 | 2025-11-28 10:48 | 3:22 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006458001 | External Reconciliation | Site Down | P4 | IHS_EDO_1016A | ED2166 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 13:50 | Azeezat Badmus | 2025-11-26 13:48 | 2025-11-26 17:08 | 12004 | 2025-11-26 13:48 | 2025-11-26 17:08 | 3:20 | MPI NGA | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Mike Imomoh | Mike Imomoh | Mike Imomoh | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006469569 | External Reconciliation | Site Down | P2 | IHS_OND_0929A | OD2451 | IBD | Ibadan | Ondo | 3 - Low | ON0647 | WEST |  | 2025-11-28 03:03 | Mary Elaigwu | 2025-11-28 03:02 | 2025-11-28 06:18 | 11711 | 2025-11-28 03:02 | 2025-11-28 06:18 | 3:15 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Fan Belt Issue | 1 / 2 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Cut Fan Belt Was Replaced
NOCINC0006476623 | Internal Reconciliation | Site Down | P2 | IHS_ONT_0014V | - | - | Asaba | Anambra | 3 - Low | AN0468 | SOUTH EAST |  | 2025-11-29 01:11 | Femi Olanipekun | 2025-11-29 01:11 | 2025-11-29 04:25 | 11670 | 2025-11-29 01:11 | 2025-11-29 04:25 | 3:14 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, Smile |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Hooked injector pump was serviced (No diesel outage after validation) | Hooked injector pump was serviced (No diesel outage after validation)
NOCINC0006467793 | External Reconciliation | Site Down | P3 | IHS_OSU_0058B | OS4265 | IBD | Ibadan | Osun | 3 - Low | OS0701 | WEST |  | 2025-11-27 20:36 | Ifechi Ugwueze | 2025-11-27 20:32 | 2025-11-27 23:44 | 11487 | 2025-11-27 20:30 | 2025-11-27 23:44 | 3:13 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006437451 | External Reconciliation | Site Down | P1 | IHS_DEL_1151A | DL0675 | ASB | Asaba | Delta | 3 - Low | DL0761 | SOUTH SOUTH |  | 2025-11-24 02:13 | Bukola Olabanji | 2025-11-24 02:11 | 2025-11-24 05:25 | 11597 | 2025-11-24 02:11 | 2025-11-24 05:25 | 3:13 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fan Belt | 2 / 2 | MTN NG, Airtel NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Cut fan belt was replaced (no diesel outage after validation).
NOCINC0006474292 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0735A | T3463 | IBD | Ibadan | Ekiti | 3 - Low | EK0533 | WEST |  | 2025-11-28 17:44 | Testimony Akinyemi | 2025-11-28 17:42 | 2025-11-28 20:55 | 11552 | 2025-11-28 17:42 | 2025-11-28 20:55 | 3:13 | Biswal | Equipment Repair | Passive | Infrastructure | Armoured Cable | 2 / 2 | Airtel NG, MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | burnt load cable and breakers were reterminated
NOCINC0006445874 | External Reconciliation | Site Down | P1 | IHS_EDO_0020B | ED5108 | IBD | Asaba | Edo | 3 - Low | ED0952 | SOUTH SOUTH |  | 2025-11-25 07:58 | Azeezat Badmus | 2025-11-25 07:56 | 2025-11-25 11:08 | 11504 | 2025-11-25 07:56 | 2025-11-25 11:08 | 3:12 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | SAHEED SHONDE | Babatunde Olayiwola | Shonde Saheed | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Low oil pressure, oil was added to restore power on site (No diesel outage after validation) | Low oil pressure, oil was added to restore power on site
NOCINC0006478422 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0814A | T3178 | IBD | Ibadan | Kwara | 3 - Low | KW0454 | WEST |  | 2025-11-29 10:02 | Ayodele Oludare | 2025-11-29 10:02 | 2025-11-29 13:11 | 11341 | 2025-11-29 10:02 | 2025-11-29 13:11 | 3:09 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Faulty injector pump was worked on
NOCINC0006470252 | Internal Reconciliation | Site Down | P3 | IHS_OYO_0925A | T3872 | IBD | Ibadan | Oyo | 3 - Low | OY1270 | WEST |  | 2025-11-28 07:11 | Marvellous Emecheta | 2025-11-28 07:04 | 2025-11-28 10:07 | 10990 | 2025-11-28 07:04 | 2025-11-28 10:07 | 3:03 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Fatunwase Samuel |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Faulty refurbished DG generation with injector pump issue. Mixing Oil with diesel site is Temporary restored pending cutover to old DCDG | Faulty refurbished DG generation with injector pump issue. Mixing Oil with diesel site is Temporary restored pending cutover to old DCDG
NOCINC0006483326 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0755A | T0230 | IBD | Asaba | Edo | 3 - Low | ED0450 | SOUTH SOUTH |  | 2025-11-29 22:00 | Muhammed Hashirudeen | 2025-11-29 21:57 | 2025-11-30 00:57 | 10804 | 2025-11-29 21:57 | 2025-11-30 00:57 | 3:00 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 3 / 3 | MTN NG, Smile, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 16 | Faulty ATS contactor was bypassed pending replacement (No diesel outage after validation)
NOCINC0006445418 | External Reconciliation | Site Down | P2 | IHS_ANA_1096A | AN0408 | ASB | Asaba | Anambra | 3 - Low | - | - | Cascaded Incident from TTO6728280 - Cascade Removed From TTO6728280 | 2025-11-25 05:35 | Kehinde Akinbowale | 2025-11-25 05:31 | 2025-11-25 08:30 | 10730 | 2025-11-25 05:31 | 2025-11-25 08:30 | 2:59 | BJ Bison NGA | Site Asset Theft | Theft | Theft | DC Cable Stolen | 1 / 1 | MTN NG |  | Egbujor Victor | Ebenezer Babafemi | Ebenezer Babafemi | Henry Wanogho | Ifeanyi Chukusa |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | IHS FSE confirmed DC cable theft on site, cable was replaced to power site | IHS FSE confirmed DC cable theft on site, cable was replaced to power site
NOCINC0006438256 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST | NodeB Unavailable@2025-11-24 07:00:26@AN0681_U | 2025-11-24 07:21 | System Administrator | 2025-11-24 07:00 | 2025-11-24 09:59 | 10714 | 2025-11-24 07:00 | 2025-11-24 09:59 | 2:59 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG at site was primed to start to restore the site. (No diesel outage after validation) | Weak DG at site was primed to start to restore the site. (No diesel outage after validation)
NOCINC0006483836 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0839A | T2693 | IBD | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 23:40 | Uthman Akinola | 2025-11-29 23:40 | 2025-11-30 02:37 | 10604 | 2025-11-29 23:40 | 2025-11-30 02:37 | 2:57 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006440918 | External Reconciliation | Site Down | P1 | IHS_EDO_0891A | T3363 | IBD | Asaba | Edo | 3 - Low | - | - | NE Is Disconnected@2025-11-24 14:13:08@N3363 | 2025-11-24 14:27 | System Administrator | 2025-11-24 14:15 | 2025-11-24 15:51 | 5774 | 2025-11-24 14:15 | 2025-11-24 17:11 | 2:56 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 1 / 1 | MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty rectifier cabinet was worked on (No diesel outage after validation) | Faulty rectifier cabinet was worked on (No diesel outage after validation)
NOCINC0006469495 | External Reconciliation | Site Down | P3 | IHS_DEL_1133A | DL0683 | ASB | Asaba | Delta | 3 - Low | DL1153 | SOUTH SOUTH |  | 2025-11-28 02:28 | Patrick Okoro | 2025-11-28 02:28 | 2025-11-28 05:21 | 10404 | 2025-11-28 02:27 | 2025-11-28 05:21 | 2:54 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Injection Pump Calibration | 2 / 2 | MTN NG, Airtel NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006489178 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1079A | DL0401 | ASB | Asaba | Delta | 3 - Low | - | - | NE Is Disconnected@2025-11-30 18:41:20@NDL0401 | 2025-11-30 19:03 | System Administrator | 2025-11-30 18:41 | 2025-11-30 21:35 | 10393 | 2025-11-30 18:41 | 2025-11-30 21:35 | 2:53 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty AVR was replaced ( No diesel outage after validation) | Faulty AVR was replaced ( No diesel outage after validation)
NOCINC0006440205 | External Reconciliation | Site Down | P1 | IHS_IBA_0074B | OY4200 | IBD | Ibadan | Oyo | 3 - Low | OY1031 | WEST |  | 2025-11-24 13:12 | Aishat Oyedeji | 2025-11-24 13:12 | 2025-11-24 16:04 | 10318 | 2025-11-24 13:12 | 2025-11-24 16:04 | 2:52 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | Airtel NG |  | SUNDAY MOSES |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG lost compression, site restored on solar | DG lost compression, site restored on solar
NOCINC0006462334 | External Reconciliation | Site Down | P4 | IHS_ANA_1185A | AN0665 | ASB | Asaba | Anambra | 3 - Low | AN1133 | SOUTH EAST |  | 2025-11-27 05:10 | Aderonke Olowojoba | 2025-11-27 05:02 | 2025-11-27 07:52 | 10183 | 2025-11-27 05:02 | 2025-11-27 07:52 | 2:50 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Ezimeruwe ANTHONY |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty AVR was worked on (No diesel outage after validation). | Faulty AVR was worked on (No diesel outage after validation).
NOCINC0006476786 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0774A | T0090 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 02:34 | Bosede Kutelu | 2025-11-29 02:31 | 2025-11-29 05:19 | 10074 | 2025-11-29 02:31 | 2025-11-29 05:19 | 2:48 | SPS | Fuel Outage (Probable) | Passive | Diesel | Fuel Line Issue | 2 / 3 | MTN NG, Smile |  | BASHIR ABDULRASAQ | Yusuf Gyang |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Block fuel line was flushed
NOCINC0006470328 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0904A | KW4575 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 07:40 | Marvellous Emecheta | 2025-11-28 07:04 | 2025-11-28 09:52 | 10050 | 2025-11-28 07:04 | 2025-11-28 09:52 | 2:47 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Failed ful pump was serviced
NOCINC0006460400 | External Reconciliation | Site Down | P1 | IHS_OSU_0781A | T3091 | IBD | Ibadan | Osun | 3 - Low | OS0661 | WEST | NE3SWS AGENT NOT RESPONDING TO REQUESTS@2025-11-26 20:03:25@MRBTS-920661 | 2025-11-26 20:24 | System Administrator | 2025-11-26 20:03 | 2025-11-26 22:49 | 9957 | 2025-11-26 20:03 | 2025-11-26 22:49 | 2:46 | IPT | Fuel Outage (Probable) | Passive | DCDG Gen | DCDG - Fuel Pump | 2 / 2 | Airtel NG, MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked
NOCINC0006469104 | External Reconciliation | Site Down | P1 | IHS_EKI_0809A | T3917 | IBD | Ibadan | Ekiti | 3 - Low | EK0500 | WEST |  | 2025-11-28 00:34 | Mary Elaigwu | 2025-11-28 00:34 | 2025-11-28 03:20 | 9937 | 2025-11-28 00:34 | 2025-11-28 03:20 | 2:46 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gas Flow | 2 / 2 | MTN NG, Airtel NG |  | Akinboyewa Akinola |  |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Frozen gas line was worked on
NOCINC0006469730 | External Reconciliation | Site Down | P3 | IHS_ILO_0001B | KW2353 | IBD | Ibadan | Kwara | 3 - Low | KW0439 | WEST |  | 2025-11-28 04:17 | Osarieme Charles | 2025-11-28 04:09 | 2025-11-28 06:54 | 9884 | 2025-11-28 04:09 | 2025-11-28 06:54 | 2:45 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | Airtel NG, MTN NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Failed fuel pump was serviced
NOCINC0006445009 | External Reconciliation | Site Down | P4 | IHS_KWA_0977H | KW4709 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 02:18 | Praise Okezie | 2025-11-25 02:16 | 2025-11-25 04:59 | 9792 | 2025-11-25 02:16 | 2025-11-25 04:59 | 2:43 | Huawei | Site Asset Theft | Theft | Theft | Backup Batteries | 1 / 1 | MTN NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | 3Li-ion BUB, crank battery, DC cable and RMS were vandalised. DC cable was reconnected and placed on manual to restore site.
NOCINC0006456298 | External Reconciliation | Site Down | P2 | IHS_OND_0783A | T3423 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 09:38 | Mary Elaigwu | 2025-11-26 09:35 | 2025-11-26 12:14 | 9540 | 2025-11-26 09:35 | 2025-11-26 12:14 | 2:39 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gas Flow | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Faulty gas line was worked on
NOCINC0006436477 | External Reconciliation | Site Down | P4 | IHS_EDO_0849A | T3298 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 00:01 | Muhammed Hashirudeen | 2025-11-24 00:01 | 2025-11-24 02:39 | 9507 | 2025-11-24 00:01 | 2025-11-24 02:39 | 2:38 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG high temperature due to low coolant level, coolant was added (No diesel outage after validation)
NOCINC0006449256 | External Reconciliation | Site Down | P1 | IHS_EKI_0730A | T3499 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 14:49 | Yewande Adeagbo | 2025-11-25 14:49 | 2025-11-25 17:26 | 9450 | 2025-11-25 14:49 | 2025-11-25 17:26 | 2:38 | Biswal | Access Denial | Security | Security Concerns In Site Environs | Access Issue - Security | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 4 | Access security issue, access was granted. RES: Low engine oil, engine oil was added
NOCINC0006444717 | External Reconciliation | Site Down | P4 | IHS_KWA_1020B | KW6466 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 00:02 | Praise Okezie | 2025-11-24 23:59 | 2025-11-25 02:36 | 9441 | 2025-11-24 23:59 | 2025-11-25 02:36 | 2:37 | IPT | Fuel Outage (Probable) | Passive | Diesel | Fuel Line Issue | 1 / 1 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Blocked fuel line was flushed
NOCINC0006454914 | External Reconciliation | Site Down | P2 | IHS_OND_0783A | T3423 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 04:19 | Ademola Alabi | 2025-11-26 04:12 | 2025-11-26 06:49 | 9421 | 2025-11-26 04:12 | 2025-11-26 06:49 | 2:37 | Biswal | Access Denial | Security | Security Concerns In Site Environs | Access Issue - Security | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Access issue security due to site located in a high risk area. Access granted. RES: Start failure alarm was cleared
NOCINC0006437664 | External Reconciliation | Site Down | P4 | IHS_OSU_0913A | OS2609 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 04:13 | Mutmainnah Saba | 2025-11-24 04:08 | 2025-11-24 06:32 | 8643 | 2025-11-24 04:08 | 2025-11-24 06:44 | 2:36 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | Bayo Nathaniel |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start
NOCINC0006439335 | External Reconciliation | Site Down | P2 | IHS_WAR_0034B | DL0736 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 10:44 | Tracy Osarumwense | 2025-11-24 10:42 | 2025-11-24 13:17 | 9329 | 2025-11-24 10:42 | 2025-11-24 13:17 | 2:35 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty rectifier backplane was worked on | Faulty rectifier backplane was worked on. (No diesel outage after validation).
NOCINC0006436624 | External Reconciliation | Site Down | P1 | IHS_EDO_0979A | ED2145 | IBD | Asaba | Edo | 3 - Low | ED0499 | SOUTH SOUTH |  | 2025-11-24 00:34 | Muhammed Hashirudeen | 2025-11-24 00:34 | 2025-11-24 03:10 | 9329 | 2025-11-24 00:34 | 2025-11-24 03:10 | 2:35 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty radiator was replaced (No diesel outage after validation)
NOCINC0006461510 | External Reconciliation | Site Down | P2 | IHS_OSU_0929A | OS2725 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 00:03 | Victor Otugo | 2025-11-27 00:02 | 2025-11-27 02:37 | 9254 | 2025-11-27 00:02 | 2025-11-27 02:37 | 2:34 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Weak DG was primed to start
NOCINC0006454699 | External Reconciliation | Site Down | P3 | IHS_EDO_1245B | ED5509 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 02:11 | Ayomide Akindolie | 2025-11-26 02:09 | 2025-11-26 04:43 | 9242 | 2025-11-26 02:09 | 2025-11-26 04:43 | 2:34 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Pump | 1 / 1 | MTN NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Failed oil pump was worked on (No diesel outage after validation)
NOCINC0006465207 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-27 13:47 | Bukola Olabanji | 2025-11-27 13:45 | 2025-11-27 16:18 | 9181 | 2025-11-27 13:45 | 2025-11-27 16:18 | 2:33 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site I.D:-IHS_WAR_0747C Access Ref:-IHSREF/25112605474226012828 Company:- UZIBEN/GAIO SYSTEMS Purpose of visitation:- RMS REINSTALLATION DAY 1 RMS Engineer Name: NNADI EMMANUEL Phone Number:- 08033305048
NOCINC0006479011 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0997A | OY2854 | IBD | Ibadan | Oyo | 3 - Low | OY1101 | WEST |  | 2025-11-29 11:22 | Aishat Oyedeji | 2025-11-29 11:22 | 2025-11-29 13:55 | 9137 | 2025-11-29 11:22 | 2025-11-29 13:55 | 2:32 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Fan Belt | 2 / 2 | MTN NG, Airtel NG |  | Taiwo Abanikannda |  |  | Soye West | Ugwu Samuel Nnamdi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Cut fan belt was worked on | Cut fan belt was worked on
NOCINC0006437515 | External Reconciliation | Site Down | P2 | IHS_KWA_0902A | KW4577 | IBD | Ibadan | Kwara | 3 - Low | KW0457 | WEST |  | 2025-11-24 02:40 | Okusanya Joseph | 2025-11-24 02:38 | 2025-11-24 05:10 | 9105 | 2025-11-24 02:38 | 2025-11-24 05:10 | 2:32 | IPT | Fuel Outage (Probable) | Passive | Diesel | Fuel Line Issue | 2 / 2 | Airtel NG, MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | blocked fuel line was flushed
NOCINC0006448922 | External Reconciliation | Site Down | P4 | IHS_WAR_0776C | DL0650 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 14:04 | Oluwatobiloba Are | 2025-11-25 14:01 | 2025-11-25 16:32 | 9053 | 2025-11-25 14:01 | 2025-11-25 16:32 | 2:31 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 1 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Name: Joshua bulus Company: GAIOsystems Purpose: RMS REINSTALLATION Date :25/11/2025 Site Id:IHS_WAR_0776C IHSREF/25112416270706458415 SARID0009029020 | Name: Joshua bulus Company: GAIOsystems Purpose: RMS REINSTALLATION Date :25/11/2025 Site Id:IHS_WAR_0776C IHSREF/25112416270706458415 SARID0009029020
NOCINC0006466552 | External Reconciliation | Site Down | P1 | IHS_OSU_0782A | T3040 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 16:54 | Bosede Kutelu | 2025-11-27 16:44 | 2025-11-27 19:15 | 9093 | 2025-11-27 16:44 | 2025-11-27 19:15 | 2:31 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 1 / 1 | MTN NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 10 | Faulty fuel pump was worked on
NOCINC0006449008 | External Reconciliation | Site Down | P1 | IHS_OYO_0969A | T3006 | IBD | Ibadan | Oyo | 3 - Low | OY1057 | WEST |  | 2025-11-25 14:18 | Victor Otugo | 2025-11-25 14:18 | 2025-11-25 16:48 | 8986 | 2025-11-25 14:18 | 2025-11-25 16:48 | 2:30 | SPS | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | Airtel NG, MTN NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006456475 | External Reconciliation | Site Down | P4 | IHS_OYO_0985A | OY3547 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 10:09 | Ifechi Ugwueze | 2025-11-26 10:08 | 2025-11-26 12:36 | 8842 | 2025-11-26 10:08 | 2025-11-26 12:36 | 2:27 | SPS | Access Denial | Regulatory | State Or Federal Agency Related Issues | Access Issue - Regulatory Concerns | 1 / 1 | MTN NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Access issue due to court injunction on subject site due to unpaid rent, Access granted RES: Hybrid synchronization failure due to failed csu, csu was reset
NOCINC0006477735 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0820A | T3238 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 07:57 | Elizabeth Apata | 2025-11-29 07:51 | 2025-11-29 10:17 | 8743 | 2025-11-29 07:51 | 2025-11-29 10:17 | 2:26 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Sensor Switch | 1 / 1 | MTN NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Faulty oil switch was worked on to restore the site. (No diesel outage after validation). | Faulty oil switch was worked on to restore the site. (No diesel outage after validation).
NOCINC0006448181 | External Reconciliation | Site Down | P1 | IHS_DEL_1000A | DL0101 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 12:40 | Ezinne Ubachukwu | 2025-11-25 12:33 | 2025-11-25 14:53 | 8441 | 2025-11-25 12:28 | 2025-11-25 14:53 | 2:26 | Tyllium NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was serviced. (No diesel outage after validation) | Faulty injector pump was serviced. (No diesel outage after validation)
NOCINC0006482081 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1048A | OY2811 | IBD | Ibadan | Oyo | 3 - Low | - | - | Cascaded Incident from TTO6768862 - Cascade Removed From TTO6768862 | 2025-11-29 18:24 | Damilola Paseda | 2025-11-29 18:20 | 2025-11-29 20:45 | 8729 | 2025-11-29 18:20 | 2025-11-29 20:45 | 2:25 | Jaza Energy NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Salahudeen Damilola |  |  | Justin Okafor | Olaide Micheal |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | faulty injector pump was worked on
NOCINC0006461066 | External Reconciliation | Site Down | P4 | IHS_ANA_1185A | AN0665 | ASB | Asaba | Anambra | 3 - Low | AN1133 | SOUTH EAST |  | 2025-11-26 22:14 | Aderonke Olowojoba | 2025-11-26 22:12 | 2025-11-27 00:36 | 8628 | 2025-11-26 22:12 | 2025-11-27 00:36 | 2:24 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Ezimeruwe ANTHONY |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed charging alternator was swapped (No diesel outage after validation) | Failed charging alternator was swapped (No diesel outage after validation)
NOCINC0006477098 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1002A | DL0086 | ASB | Asaba | Delta | 3 - Low | - | - | OML Fault@2025-11-29 04:11:44@DL0086_Opposite God Divine Church | 2025-11-29 04:24 | System Administrator | 2025-11-29 04:15 | 2025-11-29 06:39 | 8622 | 2025-11-29 04:15 | 2025-11-29 06:39 | 2:24 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 1 | MTN NG |  | Monday Agha | Igwe Samuel | Igwe Samuel | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG under frequency, governor was adjusted to restore the site (No diesel outage after validation) | DG under frequency, governor was adjusted to restore the site (No diesel outage after validation)
NOCINC0006438084 | External Reconciliation | Site Down | P3 | IHS_EDO_0012B | ED5016 | IBD | Asaba | Edo | 3 - Low | ED0637 | SOUTH SOUTH |  | 2025-11-24 06:27 | Uthman Akinola | 2025-11-24 06:22 | 2025-11-24 08:42 | 8393 | 2025-11-24 06:22 | 2025-11-24 08:42 | 2:20 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Unbalanced | 2 / 2 | MTN NG, Airtel NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Unbalanced load due to faulty line breaker was worked on | Unbalanced load due to faulty line breaker was worked on
NOCINC0006456822 | External Reconciliation | Site Down | P4 | IHS_OND_0961A | OD2524 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 11:10 | Mary Elaigwu | 2025-11-26 11:10 | 2025-11-26 13:28 | 8296 | 2025-11-26 11:10 | 2025-11-26 13:28 | 2:18 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Atilola Mutiu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG battery, Site restored on BUB
NOCINC0006451273 | External Reconciliation | Site Down | P3 | IHS_EDO_1254B | ED5537 | IBD | Asaba | Edo | 3 - Low | ED0851 | SOUTH SOUTH |  | 2025-11-25 19:55 | Oluwatobiloba Are | 2025-11-25 19:55 | 2025-11-25 22:12 | 8227 | 2025-11-25 19:55 | 2025-11-25 22:12 | 2:17 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Alade Olufemi Olufem | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006473920 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0879H | T2907 | ASB | Asaba | Delta | 3 - Low | DL0635 | SOUTH SOUTH |  | 2025-11-28 16:54 | Bukola Olabanji | 2025-11-28 16:52 | 2025-11-28 19:06 | 8078 | 2025-11-28 16:52 | 2025-11-28 19:06 | 2:15 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier - Circuit Breaker | 1 / 2 | Airtel NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty DC circuit breaker was replaced (No diesel outage after validation) | Faulty DC circuit breaker was replaced (No diesel outage after validation)
NOCINC0006460633 | External Reconciliation | Site Down | P2 | IHS_OSU_0062B | OS4624 | IBD | Ibadan | Osun | 3 - Low | OS0627 | WEST | Cascaded Incident from TTO6744946 - Cascade Removed From TTO6744946 | 2025-11-26 21:01 | Victor Otugo | 2025-11-26 20:59 | 2025-11-26 23:13 | 8031 | 2025-11-26 20:59 | 2025-11-26 23:13 | 2:14 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Failed charging alternator was excited
NOCINC0006466392 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH | Huawei 3G SiteDown@2025-11-27 16:17:24@UDL1078 | 2025-11-27 16:32 | System Administrator | 2025-11-27 16:25 | 2025-11-27 18:39 | 7990 | 2025-11-27 16:25 | 2025-11-27 18:39 | 2:13 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected passive, Awaiting update from FSE
NOCINC0006472305 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0747A | T0161 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 12:53 | Azeezat Badmus | 2025-11-28 12:50 | 2025-11-28 15:01 | 7857 | 2025-11-28 12:50 | 2025-11-28 15:01 | 2:11 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty rectifier cabinet was worked on (No diesel outage after validation)
NOCINC0006465499 | External Reconciliation | Site Down | P1 | IHS_OYO_1174H | OY2820 | IBD | Ibadan | Oyo | 3 - Low | OY0083 | WEST |  | 2025-11-27 14:24 | Mutmainnah Saba | 2025-11-27 14:21 | 2025-11-27 16:32 | 7846 | 2025-11-27 14:21 | 2025-11-27 16:32 | 2:11 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Top Gasket | 2 / 2 | MTN NG, Airtel NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty top gasket was worked on
NOCINC0006466165 | External Reconciliation | Site Down | P4 | IHS_DEL_1082A | DL0083 | ASB | Asaba | Delta | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-27 15:42:46@DL0083_Ivorogbor | 2025-11-27 15:56 | System Administrator | 2025-11-27 15:47 | 2025-11-27 17:58 | 7829 | 2025-11-27 15:47 | 2025-11-27 17:58 | 2:10 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006454635 | External Reconciliation | Site Down | P2 | IHS_DEL_1051A | DL0091 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 01:49 | Ayokunle Samuel | 2025-11-26 01:49 | 2025-11-26 03:59 | 7815 | 2025-11-26 01:49 | 2025-11-26 03:59 | 2:10 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention. | Site inter failed and cleared without any technical intervention.
NOCINC0006457116 | External Reconciliation | Site Down | P2 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 11:38 | Azeezat Badmus | 2025-11-26 11:37 | 2025-11-26 13:45 | 7709 | 2025-11-26 11:37 | 2025-11-26 13:45 | 2:08 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is powered from ED4860. (No diesel outage after validation)
NOCINC0006469381 | External Reconciliation | Site Down | P3 | IHS_OYO_0925A | T3872 | IBD | Ibadan | Oyo | 3 - Low | OY1270 | WEST |  | 2025-11-28 01:35 | Osarieme Charles | 2025-11-28 01:32 | 2025-11-28 03:40 | 7684 | 2025-11-28 01:32 | 2025-11-28 03:40 | 2:08 | IPT | Access Denial | Security | Security Concerns In Site Environs | Access Issue - Security | 2 / 2 | MTN NG, Airtel NG |  | Fatunwase Samuel |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Access Restriction Area, Due to security concern. Team were escorted to site by Psoc patrol. RCA : Refurbished DG deployed mixing oil with diesel.DG lift pump was worked on
NOCINC0006462407 | External Reconciliation | Site Down | P4 | IHS_EDO_0950A | ED2018 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 05:34 | Oluwatomisin Sogbesan | 2025-11-27 05:31 | 2025-11-27 07:39 | 7651 | 2025-11-27 05:31 | 2025-11-27 07:39 | 2:08 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was serviced (No diesel outage after validation)
NOCINC0006485960 | Internal Reconciliation | Site Down | P3 | IHS_IBA_0753E | OY6526 | IBD | Ibadan | Oyo | 3 - Low | OY1166 | WEST |  | 2025-11-30 10:39 | Aishat Oyedeji | 2025-11-30 10:35 | 2025-11-30 12:42 | 7596 | 2025-11-30 10:35 | 2025-11-30 12:42 | 2:07 | Biswal | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | suspected power issue, awaiting update from FSE
NOCINC0006443590 | External Reconciliation | Site Down | P1 | IHS_OYO_0969A | T3006 | IBD | Ibadan | Oyo | 3 - Low | OY1057 | WEST |  | 2025-11-24 20:20 | Damilola Paseda | 2025-11-24 20:18 | 2025-11-24 22:24 | 7508 | 2025-11-24 20:18 | 2025-11-24 22:24 | 2:05 | SPS | Fuel Outage (Probable) | Passive | Diesel | Diesel Top-Up | 2 / 2 | MTN NG, Airtel NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Low diesel level, diesel was topped up | Low diesel level, diesel was topped up
NOCINC0006463711 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-27 10:30 | Bukola Olabanji | 2025-11-27 10:28 | 2025-11-27 12:31 | 7401 | 2025-11-27 10:28 | 2025-11-27 12:31 | 2:03 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site I.D:-IHS_WAR_0747C Access Ref:-IHSREF/25112605474226012828 Company:- UZIBEN/GAIO SYSTEMS Purpose of visitation:- RMS REINSTALLATION DAY 1 RMS Engineer Name: NNADI EMMANUEL Phone Number:- 08033305048
NOCINC0006485176 | Internal Reconciliation | Site Down | P4 | IHS_OND_0048B | OD2585 | IBD | Ibadan | Edo | 3 - Low | - | - |  | 2025-11-30 07:58 | Abisoye Olaleye | 2025-11-30 07:57 | 2025-11-30 10:00 | 7340 | 2025-11-30 07:57 | 2025-11-30 10:00 | 2:02 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG Was Primed To Start
NOCINC0006469522 | External Reconciliation | Site Down | P3 | IHS_OYO_1005A | OY2845 | IBD | Ibadan | Oyo | 3 - Low | OY1148 | WEST |  | 2025-11-28 02:42 | Marvellous Emecheta | 2025-11-28 02:40 | 2025-11-28 04:42 | 7335 | 2025-11-28 02:40 | 2025-11-28 04:42 | 2:02 | Inhouse | Access Denial | Security | Security Concerns In Site Environs | Access Issue - Security | 2 / 2 | MTN NG, Airtel NG |  | Oluwaseun Alaba |  |  | Paul Akpomie | Oluwaseun Alaba |  | Luke Eke | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Access issue- security, site located in high risk area. Site was visited by dawn RES: faulty radiator was worked on
NOCINC0006487421 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0791A | T0184 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 14:10 | Ezinne Ubachukwu | 2025-11-30 14:06 | 2025-11-30 16:08 | 7320 | 2025-11-30 14:06 | 2025-11-30 16:08 | 2:02 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 1 | MTN NG |  | Idowu Dare |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty manual lift pump was worked on. (No diesel outage after validation) | Faulty manual lift pump was worked on. (No diesel outage after validation)
NOCINC0006490002 | Resolved | Site Down | P2 | IHS_EDO_0828A | T3295 | IBD | Asaba | Edo | 3 - Low | ED0747 | SOUTH SOUTH |  | 2025-11-30 22:00 | Quadri Ogundare | 2025-11-30 21:58 | 2025-12-01 00:04 | 7560 | 2025-11-30 21:58 | 2025-12-01 | 2:02 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | AZUBUIKE EMEH | Shagba Terkula | Emeh Azubike | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 9 | Failed charging Alternator was excited (No diesel outage after validation) | Failed charging Alternator was excited (No diesel outage after validation)
NOCINC0006451746 | External Reconciliation | Site Down | P4 | IHS_OYO_1085K | OY4080 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 20:41 | Aishat Oyedeji | 2025-11-25 20:40 | 2025-11-25 22:41 | 7270 | 2025-11-25 20:40 | 2025-11-25 22:41 | 2:01 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Bayo Nathaniel |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting passive update from Fse.
NOCINC0006484895 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0796A | T2635 | ASB | Asaba | Delta | 3 - Low | DL0985 | SOUTH SOUTH | 4G Site Down@2025-11-30 06:24:27@DL0985_L | 2025-11-30 06:43 | System Administrator | 2025-11-30 06:24 | 2025-11-30 08:40 | 8149 | 2025-11-30 06:39 | 2025-11-30 08:40 | 2:01 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator Carbon Brush Faulty | 3 / 3 | Airtel NG, MTN NG, Smile |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Failed Charging alternator was replaced (No diesel outage after validation) | Failed Charging alternator was replaced (No diesel outage after validation)
NOCINC0006437611 | External Reconciliation | Site Down | P1 | IHS_DEL_1176A | DL0497 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 03:49 | Bukola Olabanji | 2025-11-24 03:41 | 2025-11-24 05:41 | 7174 | 2025-11-24 03:41 | 2025-11-24 05:41 | 2:00 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Faulty fuel lift pump was worked on (no diesel outage after validation).
NOCINC0006489533 | Internal Reconciliation | Site Down | P2 | IHS_OND_0061B | OD4825 | IBD | Ibadan | Ondo | 3 - Low | ON0777 | WEST |  | 2025-11-30 20:23 | Yewande Adeagbo | 2025-11-30 20:21 | 2025-11-30 22:20 | 7141 | 2025-11-30 20:21 | 2025-11-30 22:20 | 1:59 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Phase Controller | 2 / 2 | MTN NG, Airtel NG |  | Sanusi Idowu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Rectifier phase control was worked on
NOCINC0006442423 | External Reconciliation | Site Down | P2 | IHS_WAR_0928B | DL3323 | ASB | Asaba | Delta | 3 - Low | DL0890 | SOUTH SOUTH |  | 2025-11-24 17:12 | Ezinne Ubachukwu | 2025-11-24 17:08 | 2025-11-24 19:06 | 7101 | 2025-11-24 17:08 | 2025-11-24 19:06 | 1:58 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty AVR was worked on. (No diesel outage after validation) | Faulty AVR was worked on. (No diesel outage after validation)
NOCINC0006484353 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0930A | OS2608 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 03:16 | Okusanya Joseph | 2025-11-30 03:15 | 2025-11-30 05:14 | 7098 | 2025-11-30 03:15 | 2025-11-30 05:14 | 1:58 | IPT | Site Asset Theft | Theft | Theft | Backup Batteries | 1 / 1 | MTN NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Theft incident on site with backup batteries and cable were stolen. Stolen cables were replaced
NOCINC0006451671 | External Reconciliation | Site Down | P2 | IHS_OND_0024B | OD4717 | IBD | Ibadan | Ondo | 3 - Low | ON0813 | WEST |  | 2025-11-25 20:31 | Testimony Akinyemi | 2025-11-25 20:30 | 2025-11-25 22:28 | 7058 | 2025-11-25 20:30 | 2025-11-25 22:28 | 1:58 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | MTN NG |  | John Kunamon |  |  | Ibrahim Akinpelu | John Kunamon |  | Fagbemi Solomon | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006486825 | Internal Reconciliation | Site Down | P1 | IHS_OYO_1057A | OY2867 | IBD | Ibadan | Oyo | 3 - Low | OY0976 | WEST |  | 2025-11-30 12:44 | Aishat Oyedeji | 2025-11-30 12:43 | 2025-11-30 14:40 | 7047 | 2025-11-30 12:43 | 2025-11-30 14:40 | 1:57 | Biswal | Fuel Outage | Passive | Gas | Gas Outage | 2 / 2 | MTN NG, Airtel NG |  | Lukman Mohammed |  | Iyiola Azeez | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Gas outage, Gas was supplied
NOCINC0006436540 | External Reconciliation | Site Down | P2 | IHS_KWA_0787A | T3166 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 00:16 | Okusanya Joseph | 2025-11-24 00:13 | 2025-11-24 02:10 | 7023 | 2025-11-24 00:13 | 2025-11-24 02:10 | 1:57 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 5 | Failed charging alternator was excited.
NOCINC0006438515 | External Reconciliation | Site Down | P3 | IHS_BEN_0002B | ED4852 | IBD | Asaba | Edo | 3 - Low | ED0873 | SOUTH SOUTH |  | 2025-11-24 08:32 | Evelyn Emagurehor | 2025-11-24 08:30 | 2025-11-24 10:27 | 7017 | 2025-11-24 08:30 | 2025-11-24 10:27 | 1:57 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 2 / 2 | MTN NG, Airtel NG |  | SIMON SUNDAY | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty water pump was replaced to restore the site. (No diesel outage after validation). | Faulty water pump was replaced to restore the site. (No diesel outage after validation).
NOCINC0006466134 | External Reconciliation | Site Down | P3 | IHS_SAP_0007B | DL0491 | ASB | Asaba | Delta | 3 - Low | DL0913 | SOUTH SOUTH |  | 2025-11-27 15:49 | Mary Odefemi | 2025-11-27 15:49 | 2025-11-27 17:46 | 6991 | 2025-11-27 15:49 | 2025-11-27 17:46 | 1:57 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | Airtel NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Burnt load breaker was replaced (No diesel outage after validation)
NOCINC0006469530 | External Reconciliation | Site Down | P3 | IHS_ANA_1465C | AN4026 | ASB | Asaba | Anambra | 3 - Low | AN0847 | SOUTH EAST |  | 2025-11-28 02:47 | Oluwatoyin Fagite | 2025-11-28 02:40 | 2025-11-28 04:36 | 6969 | 2025-11-28 02:40 | 2025-11-28 04:36 | 1:56 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fan Belt | 2 / 2 | MTN NG, Airtel NG |  | Ugochuku Agbamuche | Ugo Agamuche | Ugo Agamuche | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Cut fan belt was replaced (No diesel outage after validation) | Cut fan belt was replaced (No diesel outage after validation)
NOCINC0006437990 | External Reconciliation | Site Down | P3 | IHS_OYO_1388B | - | - | Ibadan | Oyo | 3 - Low | OY1335 | WEST |  | 2025-11-24 05:57 | Mutmainnah Saba | 2025-11-24 05:48 | 2025-11-24 07:44 | 6950 | 2025-11-24 05:48 | 2025-11-24 07:44 | 1:56 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | Airtel NG |  | Taiwo Abanikannda |  |  | Soye West | Ugwu Samuel Nnamdi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006461280 | External Reconciliation | Site Down |  | IHS_OYO_1445B | - | - | Ibadan | Oyo | 3 - Low | OY1535 | WEST |  | 2025-11-26 23:12 | Victor Otugo | 2025-11-26 23:11 | 2025-11-27 01:06 | 6907 | 2025-11-26 23:11 | 2025-11-27 01:06 | 1:55 | Energy Vision Nigeria | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, Smile |  | Adewole Olumuyiwa |  |  | Oladotun Ogunleye | Banje Oluwaseun |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on.
NOCINC0006489933 | Resolved | Site Down | P4 | IHS_DEL_1009A | DL0046 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 21:44 | Solomon Bankole | 2025-11-30 21:43 | 2025-11-30 23:38 | 6900 | 2025-11-30 21:43 | 2025-11-30 23:38 | 1:55 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG under frequency, governor was adjusted ( No diesel outage after validation) | DG under frequency, governor was adjusted ( No diesel outage after validation)
NOCINC0006462947 | External Reconciliation | Site Down | P1 | IHS_WAR_0031B | DL0588 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 07:52 | Tracy Osarumwense | 2025-11-27 07:52 | 2025-11-27 09:47 | 6893 | 2025-11-27 07:52 | 2025-11-27 09:47 | 1:55 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 1 | MTN NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty governor was worked on (no diesel outage after validation).
NOCINC0006456112 | External Reconciliation | Site Down | P3 | IHS_EDO_1245B | ED5509 | IBD | Asaba | Edo | 3 - Low | - | - | NodeB Unavailable@2025-11-26 08:47:47@UED5509 | 2025-11-26 09:01 | System Administrator | 2025-11-26 08:50 | 2025-11-26 10:45 | 6884 | 2025-11-26 08:50 | 2025-11-26 10:45 | 1:55 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Suspected passive, Awaiting update from FSE
NOCINC0006469576 | External Reconciliation | Site Down | P3 | IHS_OSU_0704E | OS4659 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 03:04 | Ifechi Ugwueze | 2025-11-28 03:03 | 2025-11-28 04:54 | 6675 | 2025-11-28 03:03 | 2025-11-28 04:54 | 1:51 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on
NOCINC0006464272 | External Reconciliation | Site Down | P2 | IHS_OSU_0826A | T3626 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 11:39 | Titus Tosin | 2025-11-27 11:39 | 2025-11-27 13:30 | 6656 | 2025-11-27 11:39 | 2025-11-27 13:30 | 1:51 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Suspected passive issue at site awaiting RCA from FSE
NOCINC0006439554 | External Reconciliation | Site Down | P2 | IHS_OND_0894A | OD2408 | IBD | Ibadan | Ondo | 3 - Low | ON0706 | WEST |  | 2025-11-24 11:32 | Ihuoma Opurum | 2025-11-24 11:25 | 2025-11-24 13:16 | 6640 | 2025-11-24 11:25 | 2025-11-24 13:16 | 1:51 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006467013 | External Reconciliation | Site Down | P2 | IHS_OSU_0739E | OS4702 | IBD | Ibadan | Osun | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-27 18:00:11@OS4702_IHS | 2025-11-27 18:15 | System Administrator | 2025-11-27 18:04 | 2025-11-27 19:55 | 6633 | 2025-11-27 18:04 | 2025-11-27 19:55 | 1:51 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Interface Module Faulty | 1 / 2 | MTN NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty DG module was worked on
NOCINC0006466562 | External Reconciliation | Site Down | P3 | IHS_OND_0026B | OD2577 | IBD | Ibadan | Ondo | 3 - Low | ON0770 | WEST |  | 2025-11-27 16:57 | Iyesioluwa Ola | 2025-11-27 16:54 | 2025-11-27 18:44 | 6600 | 2025-11-27 16:54 | 2025-11-27 18:44 | 1:50 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed Charging Alternator Was Excited
NOCINC0006445566 | External Reconciliation | Site Down | P2 | IHS_DEL_0868A | T2749 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 06:31 | Quadri Ogundare | 2025-11-25 06:28 | 2025-11-25 08:18 | 6586 | 2025-11-25 06:28 | 2025-11-25 08:18 | 1:50 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Lifting Pump Faulty | 1 / 1 | MTN NG |  | HENRY OMELE |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty lift pump was worked on | Faulty lift pump was worked on. (No diesel outage after validation).
NOCINC0006480255 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1093A | DL0703 | ASB | Asaba | Delta | 3 - Low | DL1190 | SOUTH SOUTH |  | 2025-11-29 13:51 | Quadri Ogundare | 2025-11-29 13:50 | 2025-11-29 15:34 | 6222 | 2025-11-29 13:50 | 2025-11-29 15:40 | 1:50 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low oil pressure, oil was topped (No diesel outage after validation) | Low oil pressure, oil was topped (No diesel outage after validation)
NOCINC0006459119 | External Reconciliation | Site Down | P1 | IHS_IBA_0074B | OY4200 | IBD | Ibadan | Oyo | 3 - Low | OY1031 | WEST |  | 2025-11-26 16:41 | Bosede Kutelu | 2025-11-26 16:32 | 2025-11-26 18:21 | 6559 | 2025-11-26 16:32 | 2025-11-26 18:21 | 1:49 | SPS | Fuel Outage (Probable) | Passive | Diesel | Diesel Top-Up | 1 / 1 | Airtel NG |  | SUNDAY MOSES |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Low diesel pressure, diesel was topped
NOCINC0006439224 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST |  | 2025-11-24 10:26 | Aderonke Olowojoba | 2025-11-24 10:01 | 2025-11-24 11:50 | 6548 | 2025-11-24 10:01 | 2025-11-24 11:50 | 1:49 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation) | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006489589 | Internal Reconciliation | Site Down | P3 | IHS_IBA_0705E | OY3696 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 20:35 | Damilola Paseda | 2025-11-30 20:33 | 2025-11-30 22:22 | 6537 | 2025-11-30 20:33 | 2025-11-30 22:22 | 1:49 | SPS | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Smile |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty Fuel Pump was Worked On | Faulty Fuel Pump was Worked On
NOCINC0006452896 | External Reconciliation | Site Down | P1 | IHS_DEL_1189A | DL0746 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 00:15 | Ayokunle Samuel | 2025-11-26 00:10 | 2025-11-26 01:58 | 6527 | 2025-11-26 00:10 | 2025-11-26 01:58 | 1:49 | Tyllium NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was serviced to restore site (No diesel outage after validation) | Faulty injector pump was serviced to restore site (No diesel outage after validation)
NOCINC0006469424 | External Reconciliation | Site Down | P4 | IHS_OND_0975A | OD4795 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 01:50 | Mary Elaigwu | 2025-11-28 01:49 | 2025-11-28 03:38 | 6526 | 2025-11-28 01:49 | 2025-11-28 03:38 | 1:49 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | MTN NG |  | Habeed Yunus |  |  | Soye West | Ugwu Samuel Nnamdi |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty DG AVR was worked on
NOCINC0006467367 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0829A | T2689 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 19:17 | Femi Olanipekun | 2025-11-27 19:17 | 2025-11-27 21:05 | 6476 | 2025-11-27 19:17 | 2025-11-27 21:05 | 1:48 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 1 / 1 | MTN NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty kick starter was worked on (no diesel outage after validation)
NOCINC0006461536 | External Reconciliation | Site Down | P3 | IHS_ANA_0966A | T4830 | ASB | Asaba | Anambra | 3 - Low | AN0833 | SOUTH EAST |  | 2025-11-27 00:09 | Ezinne Ubachukwu | 2025-11-27 00:07 | 2025-11-27 01:54 | 6459 | 2025-11-27 00:07 | 2025-11-27 01:54 | 1:48 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Amadi Fabian | Tijani Haruna | Tijani Haruna | Henry Wanogho | Ifeanyi Chukusa |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG Loss Compression, weak DG was primed to start.(No diesel outage after validation) | DG Loss Compression, weak DG was primed to start.(No diesel outage after validation)
NOCINC0006438104 | External Reconciliation | Site Down | P4 | IHS_OSU_0977K | OS4314 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 06:33 | Okusanya Joseph | 2025-11-24 06:32 | 2025-11-24 08:20 | 6436 | 2025-11-24 06:32 | 2025-11-24 08:20 | 1:47 | SPS | Fuel Outage (Probable) | Passive | Diesel | Fuel Line Issue | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Blocked fuel line was flushed
NOCINC0006469247 | External Reconciliation | Site Down | P4 | IHS_EDO_1340B | - | - | Asaba | Edo | 3 - Low | ED0945 | SOUTH SOUTH |  | 2025-11-28 01:06 | Emmanuel Faleti | 2025-11-28 01:02 | 2025-11-28 02:48 | 6398 | 2025-11-28 01:02 | 2025-11-28 02:48 | 1:47 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | Airtel NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid to Gen synchronization failure due to weak ACDG - Generator Battery. RES: An external battery was used to power the Gen manually to restore power to the site. (No diesel outage after validation) | Hybrid to Gen synchronization failure due to weak ACDG - Generator Battery. RES: An external battery was used to power the Gen manually to restore power to the site. (No diesel outage after validation)
NOCINC0006444606 | External Reconciliation | Site Down | P1 | IHS_EDO_0797A | T3262 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 23:31 | Azeezat Badmus | 2025-11-24 23:30 | 2025-11-25 01:16 | 6369 | 2025-11-24 23:30 | 2025-11-25 01:16 | 1:46 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Control Panel | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Faulty DG module was worked on (No diesel outage after validation)
NOCINC0006472241 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1133A | DL0683 | ASB | Asaba | Delta | 3 - Low | DL1153 | SOUTH SOUTH |  | 2025-11-28 12:42 | Abundance Otunola | 2025-11-28 12:42 | 2025-11-28 14:28 | 6368 | 2025-11-28 12:42 | 2025-11-28 14:28 | 1:46 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG high temperature, Coolant was added(no diesel outage after validation)
NOCINC0006468102 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 21:37 | Emmanuel Faleti | 2025-11-27 21:37 | 2025-11-27 23:22 | 6328 | 2025-11-27 21:37 | 2025-11-27 23:22 | 1:45 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty rectifier module was worked on. (No diesel outage after validation) | Faulty rectifier module was worked on. (No diesel outage after validation)
NOCINC0006448669 | External Reconciliation | Site Down | P3 | IHS_ANA_1101A | AN0331 | ASB | Asaba | Anambra | 3 - Low | AN0655 | SOUTH EAST |  | 2025-11-25 13:42 | Aderonke Olowojoba | 2025-11-25 13:34 | 2025-11-25 15:19 | 6319 | 2025-11-25 13:34 | 2025-11-25 15:19 | 1:45 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 2 | Airtel NG |  | Moses Kenechukwu | Kenneth Ogbodo | Kenneth Ogbodo | Fady Safwat | Aliyu Garuba |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation) | Low DG frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006489884 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0824A | T2660 | ASB | Asaba | Delta | 3 - Low | DL0839 | SOUTH SOUTH |  | 2025-11-30 21:36 | Solomon Bankole | 2025-11-30 21:35 | 2025-11-30 23:20 | 6272 | 2025-11-30 21:35 | 2025-11-30 23:20 | 1:45 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Burnt AVR was replaced ( No diesel outage after validation) | Burnt AVR was replaced ( No diesel outage after validation)
NOCINC0006477171 | Internal Reconciliation | Site Down | P3 | IHS_AGB_0005B | DL0430 | ASB | Asaba | Delta | 3 - Low | DL0522 | SOUTH SOUTH |  | 2025-11-29 05:04 | Femi Olanipekun | 2025-11-29 05:01 | 2025-11-29 06:45 | 6265 | 2025-11-29 05:01 | 2025-11-29 06:45 | 1:44 | Tyllium NGA | Site Asset Theft | Theft | Theft | DC Cable Stolen | 1 / 2 | MTN NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Team confirmed stolen DC cable at site, DC cable was replaced to power the site (No diesel outage after validation) | Team confirmed stolen DC cable at site, DC cable was replaced to power the site (No diesel outage after validation)
NOCINC0006468778 | External Reconciliation | Site Down | P4 | IHS_EDO_1246B | ED5521 | IBD | Asaba | Edo | 3 - Low | ED1124 | SOUTH SOUTH |  | 2025-11-28 00:13 | Oluwatobiloba Are | 2025-11-28 00:12 | 2025-11-28 01:56 | 6232 | 2025-11-28 00:12 | 2025-11-28 01:56 | 1:44 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Unbalanced load due to insurfficient rectifier module, module was added (no diesel outage after validation).
NOCINC0006445055 | External Reconciliation | Site Down | P3 | IHS_ANA_0992A | T4192 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 02:40 | Solomon Bankole | 2025-11-25 02:40 | 2025-11-25 04:23 | 6197 | 2025-11-25 02:40 | 2025-11-25 04:23 | 1:43 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 1 / 1 | MTN NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty Radiator was replaced ( No diesel outage after validation) | Faulty Radiator was replaced ( No diesel outage after validation)
NOCINC0006454829 | External Reconciliation | Site Down | P1 | IHS_OND_0029B | OD4751 | IBD | Ibadan | Ondo | 3 - Low | ON0530 | WEST | Cascaded Incident from TTO6738517 - Cascade Removed From TTO6738517 | 2025-11-26 03:22 | Testimony Akinyemi | 2025-11-26 03:15 | 2025-11-26 04:58 | 6180 | 2025-11-26 03:15 | 2025-11-26 04:58 | 1:43 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Module | 2 / 2 | Airtel NG, MTN NG |  | Usman Hammed |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Hybrid synchronization failure due to failed hybrid module, DG powered manually
NOCINC0006452902 | External Reconciliation | Site Down | P2 | IHS_ANA_0989A | T4169 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 00:17 | Ayokunle Samuel | 2025-11-26 00:12 | 2025-11-26 01:55 | 6177 | 2025-11-26 00:12 | 2025-11-26 01:55 | 1:43 | Tyllium NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Air Intake | 1 / 1 | MTN NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 4 | Airlock in fuel line was cleared. (No diesel outage after validation) | Airlock in fuel line was cleared. (No diesel outage after validation)
NOCINC0006462049 | External Reconciliation | Site Down | P2 | IHS_OSU_0929A | OS2725 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 02:52 | Victor Otugo | 2025-11-27 02:51 | 2025-11-27 04:34 | 6156 | 2025-11-27 02:51 | 2025-11-27 04:34 | 1:43 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Weak DG was primed to start
NOCINC0006452100 | External Reconciliation | Site Down | P3 | IHS_OSU_1043B | OS4746 | IBD | Ibadan | Osun | 3 - Low | - | - | CSL Fault@2025-11-25 21:30:33@OS4746_2G | 2025-11-25 21:43 | System Administrator | 2025-11-25 21:31 | 2025-11-25 23:13 | 6131 | 2025-11-25 21:31 | 2025-11-25 23:12 | 1:42 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Low Oil Pressure | 1 / 1 | MTN NG |  | Odufu Friday |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Low oil pressure, oil was topped
NOCINC0006466152 | External Reconciliation | Site Down | P3 | IHS_OYO_0940A | T3628 | IBD | Ibadan | Osun | 3 - Low | OS0731 | WEST |  | 2025-11-27 15:53 | Oluwatomisin Ogunleye | 2025-11-27 15:53 | 2025-11-27 17:32 | 5968 | 2025-11-27 15:51 | 2025-11-27 17:32 | 1:41 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Zechariah Akinbulejo | Opeyemi Ajibola | Opeyemi Ajibola | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start.
NOCINC0006436487 | External Reconciliation | Site Down | P1 | IHS_OSU_0806A | T3021 | IBD | Ibadan | Osun | 3 - Low | OS0647 | WEST |  | 2025-11-24 00:03 | Okusanya Joseph | 2025-11-24 00:01 | 2025-11-24 00:07 | 323 | 2025-11-24 00:01 | 2025-11-24 01:43 | 1:41 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 3 | Faulty charging alternator was swapped
NOCINC0006436566 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 00:20 | Bukola Olabanji | 2025-11-24 00:17 | 2025-11-24 01:58 | 6060 | 2025-11-24 00:17 | 2025-11-24 01:58 | 1:41 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Suspected passive, awaiting update
NOCINC0006450372 | External Reconciliation | Site Down | P2 | IHS_OYO_1207H | - | - | Ibadan | Oyo | 3 - Low | OY1537 | WEST |  | 2025-11-25 17:03 | Victor Otugo | 2025-11-25 17:03 | 2025-11-25 18:44 | 6037 | 2025-11-25 17:03 | 2025-11-25 18:44 | 1:41 | Biswal | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 2 / 2 | Airtel NG, Smile |  | Enoch Fidelis |  |  | Abiola Adegbiji | Habeeb Adepoju |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | GG loss compression, Site restored on stop gap GG
NOCINC0006462762 | External Reconciliation | Site Down | P2 | IHS_EKI_0757A | T3470 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-27 07:09 | Oluwadara Bankole | 2025-11-27 07:03 | 2025-11-27 08:44 | 6036 | 2025-11-27 07:03 | 2025-11-27 08:44 | 1:41 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Yohanna Sabo |  |  | Ibrahim Akinpelu | Yohanna Sabo |  | Collins Edike | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Failed charging alternator was excited
NOCINC0006442183 | External Reconciliation | Site Down | P2 | IHS_EDO_0976A | ED2148 | IBD | Asaba | Edo | 3 - Low | ED0659 | SOUTH SOUTH |  | 2025-11-24 16:46 | Oluwatomisin Sogbesan | 2025-11-24 16:42 | 2025-11-24 18:22 | 6030 | 2025-11-24 16:42 | 2025-11-24 18:22 | 1:40 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Hammed Abubakar |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty injector pump was serviced (No diesel outage after validation) | Faulty injector pump was serviced (No diesel outage after validation)
NOCINC0006439532 | External Reconciliation | Site Down | P3 | IHS_EDO_0963A | ED3347 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 11:29 | Evelyn Emagurehor | 2025-11-24 11:22 | 2025-11-24 13:02 | 6010 | 2025-11-24 11:22 | 2025-11-24 13:02 | 1:40 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Radiator Leakage | 1 / 1 | MTN NG |  | Mike Imomoh | Mike Imomoh | Mike Imomoh | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | High engine temperature due to radiator leakage. Radiator was worked on pending replacement (No diesel outage after validation) | High engine temperature due to radiator leakage. Radiator was worked on pending replacement
NOCINC0006459634 | External Reconciliation | Site Down | P1 | IHS_KWA_0763A | T3496 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-26 18:16 | Titus Tosin | 2025-11-26 18:15 | 2025-11-26 19:55 | 6006 | 2025-11-26 18:15 | 2025-11-26 19:55 | 1:40 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Afolabi Ganiyyu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Failed charging alternator was excited
NOCINC0006476842 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1169H | ED2065 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 03:06 | Elizabeth Apata | 2025-11-29 03:03 | 2025-11-29 04:43 | 5973 | 2025-11-29 03:03 | 2025-11-29 04:43 | 1:40 | Huawei | Site Intrusion | Intrusion On Site | Intrusion On Site | Intrusion - Vandalism/Sabotage | 1 / 1 | MTN NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Intrusion on site, Attempted theft at site
NOCINC0006448622 | External Reconciliation | Site Down | P4 | IHS_ILO_0057C | KW4672 | IBD | Ibadan | Kwara | 3 - Low | KW0470 | WEST | Huawei 2G SiteDown@2025-11-25 13:17:48@KW4672_Nnpc Road Gaa-Akanbi | 2025-11-25 13:35 | System Administrator | 2025-11-25 13:23 | 2025-11-25 15:00 | 5873 | 2025-11-25 13:23 | 2025-11-25 15:00 | 1:38 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | David Oyebamiji |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | faulty injector pump was worked on
NOCINC0006472261 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0721E | OS2696 | IBD | Ibadan | Osun | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-28 12:27:48@ | 2025-11-28 12:45 | System Administrator | 2025-11-28 12:38 | 2025-11-28 14:16 | 5861 | 2025-11-28 12:38 | 2025-11-28 14:16 | 1:38 | IPT | Fuel Outage (Probable) | Passive | Diesel | Diesel Top-Up | 1 / 1 | MTN NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Low diesel level, diesel was topped up | Low diesel level, diesel was topped up
NOCINC0006484475 | Internal Reconciliation | Site Down | P2 | IHS_OND_0943A | OD2463 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 04:13 | Abisoye Olaleye | 2025-11-30 04:10 | 2025-11-30 05:47 | 5837 | 2025-11-30 04:10 | 2025-11-30 05:47 | 1:37 | IPT | Fuel Outage (Probable) | Passive | DCDG Gen | DCDG - Injector Pump | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 4 | Faulty Injector Nozzles Was Serviced
NOCINC0006461872 | External Reconciliation | Site Down | P1 | IHS_DEL_0984A | DL0006 | ASB | Asaba | Delta | 3 - Low | DL1272 | SOUTH SOUTH |  | 2025-11-27 01:12 | Ezinne Ubachukwu | 2025-11-27 01:12 | 2025-11-27 02:49 | 5809 | 2025-11-27 01:12 | 2025-11-27 02:49 | 1:37 | Tyllium NGA | Fuel Outage (Probable) | Passive | Diesel | Tank Sealing Issue - Water In The Fuel | 2 / 2 | Airtel NG, MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Water Ingress, Water was separated from Diesel. | Water Ingress, Water was separated from Diesel. (No diesel outage after validation). (No diesel outage after validation).
NOCINC0006456207 | External Reconciliation | Site Down | P2 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 09:24 | Azeezat Badmus | 2025-11-26 09:21 | 2025-11-26 10:58 | 5806 | 2025-11-26 09:21 | 2025-11-26 10:58 | 1:37 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is powered from ED4860. (No diesel outage after validation)
NOCINC0006474169 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0939A | T2447 | ASB | Asaba | Delta | 3 - Low | DL1077 | SOUTH SOUTH |  | 2025-11-28 17:31 | Bukola Olabanji | 2025-11-28 17:28 | 2025-11-28 19:05 | 5803 | 2025-11-28 17:28 | 2025-11-28 19:05 | 1:37 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Insufficient rectifier module, module was added | Insufficient rectifier module, module was added
NOCINC0006475335 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0774A | T0090 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 20:33 | Bosede Kutelu | 2025-11-28 20:28 | 2025-11-28 22:05 | 5803 | 2025-11-28 20:28 | 2025-11-28 22:05 | 1:37 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 3 | MTN NG, Smile |  | BASHIR ABDULRASAQ | Yusuf Gyang |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Low Voltage AVR was adjusted
NOCINC0006483388 | Internal Reconciliation | Site Down | P3 | IHS_OND_0040B | OD4827 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 22:07 | Abisoye Olaleye | 2025-11-29 22:06 | 2025-11-29 23:43 | 5801 | 2025-11-29 22:06 | 2025-11-29 23:43 | 1:37 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Fan Belt | 1 / 1 | MTN NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Cut Fanbelt Was Replaced
NOCINC0006468589 | External Reconciliation | Site Down | P2 | IHS_OND_0838A | T3930 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 23:15 | Mary Elaigwu | 2025-11-27 23:14 | 2025-11-28 00:50 | 5733 | 2025-11-27 23:14 | 2025-11-28 00:50 | 1:36 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Fan Belt Issue | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 3 | Cut fan belt was replaced
NOCINC0006457576 | External Reconciliation | Site Down | P1 | IHS_OYO_1008A | OY2827 | IBD | Ibadan | Oyo | 3 - Low | OY1664 | WEST |  | 2025-11-26 12:44 | Bosede Kutelu | 2025-11-26 12:38 | 2025-11-26 14:12 | 5692 | 2025-11-26 12:38 | 2025-11-26 14:12 | 1:35 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | Airtel NG |  | SUNDAY MOSES |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Suspected passive issue on site, awaiting RCA from FSE
NOCINC0006438467 | External Reconciliation | Site Down | P3 | IHS_KWA_0703E | KW4741 | IBD | Ibadan | Kwara | 3 - Low | KW0393 | WEST | NE3SWS AGENT NOT RESPONDING TO REQUESTS@2025-11-24 08:02:41@MRBTS-940393 | 2025-11-24 08:24 | System Administrator | 2025-11-24 08:03 | 2025-11-24 09:37 | 5631 | 2025-11-24 08:03 | 2025-11-24 09:37 | 1:34 | IPT | Fuel Outage (Probable) | Passive | DCDG Gen | DCDG - Fuel Pump | 1 / 2 | Airtel NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty fuel pump was replaced
NOCINC0006481526 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0704E | ED2050 | IBD | Asaba | Edo | 3 - Low | ED0482 | SOUTH SOUTH |  | 2025-11-29 16:53 | Azeezat Badmus | 2025-11-29 16:51 | 2025-11-29 18:24 | 5624 | 2025-11-29 16:51 | 2025-11-29 18:24 | 1:34 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | Airtel NG |  | EKPU SUNDAY |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Tripped Load breaker was replaced. (No diesel outage after validation)
NOCINC0006462242 | External Reconciliation | Site Down | P1 | IHS_DEL_1020A | DL0113 | ASB | Asaba | Delta | 3 - Low | DL0742 | SOUTH SOUTH |  | 2025-11-27 04:32 | Tracy Osarumwense | 2025-11-27 04:27 | 2025-11-27 06:01 | 5597 | 2025-11-27 04:27 | 2025-11-27 06:01 | 1:33 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Filter | 2 / 2 | MTN NG, Airtel NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Clogged Fuel Filter was replaced. | Clogged Fuel Filter was replaced. (No diesel outage after validation).
NOCINC0006480506 | Internal Reconciliation | Site Down | P4 | IHS_OND_0874A | T3936 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 14:27 | Testimony Akinyemi | 2025-11-29 14:27 | 2025-11-29 16:00 | 5580 | 2025-11-29 14:27 | 2025-11-29 16:00 | 1:33 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG Primed To Start
NOCINC0006462793 | External Reconciliation | Site Down | P4 | IHS_EDO_0920A | T3354 | IBD | Asaba | Kogi | 3 - Low | - | - |  | 2025-11-27 07:14 | Oluwatomisin Sogbesan | 2025-11-27 07:11 | 2025-11-27 08:44 | 5578 | 2025-11-27 07:11 | 2025-11-27 08:44 | 1:33 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Adekoya Adetunji |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected passive fault, awaiting update from FSE
NOCINC0006458490 | External Reconciliation | Site Down | P1 | IHS_ANA_1013A | T4866 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 15:04 | Akachukwu Ugwu | 2025-11-26 15:01 | 2025-11-26 16:34 | 5564 | 2025-11-26 15:01 | 2025-11-26 16:34 | 1:33 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Pump | 1 / 1 | MTN NG |  | Adams Uthman | Adams Uthman | Adams Uthman | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | faulty oil pump was worked on (No diesel outage after validation)
NOCINC0006464230 | External Reconciliation | Site Down | P1 | IHS_WAR_0071C | DL0939 | ASB | Asaba | Delta | 3 - Low | DL0688 | SOUTH SOUTH |  | 2025-11-27 11:34 | Bukola Olabanji | 2025-11-27 11:33 | 2025-11-27 13:06 | 5555 | 2025-11-27 11:33 | 2025-11-27 13:06 | 1:33 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Main Alternator | 2 / 2 | Airtel NG, MTN NG |  | Kevwe Oshoture |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty main alternator was worked on (No diesel outage after validation)
NOCINC0006445358 | External Reconciliation | Site Down | P3 | IHS_OSU_0919A | OS3637 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 05:07 | Praise Okezie | 2025-11-25 05:04 | 2025-11-25 06:36 | 5531 | 2025-11-25 05:04 | 2025-11-25 06:36 | 1:32 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 2 | MTN NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid Synchronization failure due to weak DG battery, external battery was used to power site.
NOCINC0006473211 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0747A | T0161 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 15:14 | Azeezat Badmus | 2025-11-28 15:14 | 2025-11-28 16:46 | 5526 | 2025-11-28 15:14 | 2025-11-28 16:46 | 1:32 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty Rectifier cabinet was worked on (No diesel outage after validation)
NOCINC0006484201 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0988C | OS4729 | IBD | Ibadan | Osun | 3 - Low | OS0941 | WEST |  | 2025-11-30 02:14 | Okusanya Joseph | 2025-11-30 02:14 | 2025-11-30 03:46 | 5499 | 2025-11-30 02:14 | 2025-11-30 03:46 | 1:32 | Energy Vision Nigeria | Site Asset Theft | Theft | Theft | Backup Batteries | 2 / 2 | MTN NG, Airtel NG |  | Osas Sunday |  |  | Oladotun Ogunleye | Osas Sunday |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Cables / Backup batteries theft .DG powered manually to restore the site.
NOCINC0006463283 | External Reconciliation | Site Down | P2 | IHS_EKI_0757A | T3470 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-27 09:14 | Kandervil Uwah | 2025-11-27 09:13 | 2025-11-27 10:44 | 5478 | 2025-11-27 09:13 | 2025-11-27 10:44 | 1:31 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Yohanna Sabo |  |  | Ibrahim Akinpelu | Yohanna Sabo |  | Collins Edike | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Failed charging alternator was worked on
NOCINC0006484536 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0057B | ED5096 | IBD | Asaba | Edo | 3 - Low | ED0664 | SOUTH SOUTH |  | 2025-11-30 04:38 | Muhammed Hashirudeen | 2025-11-30 04:38 | 2025-11-30 06:09 | 5468 | 2025-11-30 04:38 | 2025-11-30 06:09 | 1:31 | Huawei | Site Asset Theft | Theft | Theft | DC Cable Stolen | 2 / 2 | Airtel NG, MTN NG |  | Ismail Adeyinka |  |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DC cable theft. Cable was reterminated to restore site (No diesel outage after validation)
NOCINC0006484316 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1142A | DL0762 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 03:02 | Uthman Akinola | 2025-11-30 02:57 | 2025-11-30 04:28 | 5460 | 2025-11-30 02:57 | 2025-11-30 04:28 | 1:31 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | faulty DG Rectifier module was reset(no diesel outage after validation)
NOCINC0006457796 | External Reconciliation | Site Down | P1 | IHS_WAR_0071C | DL0939 | ASB | Asaba | Delta | 3 - Low | DL0688 | SOUTH SOUTH |  | 2025-11-26 13:16 | Mary Odefemi | 2025-11-26 13:12 | 2025-11-26 14:00 | 2868 | 2025-11-26 12:31 | 2025-11-26 14:00 | 1:29 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Kevwe Oshoture |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled (No diesel outage after validation)
NOCINC0006455209 | External Reconciliation | Site Down | P2 | IHS_WAR_0707E | T2676 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 06:00 | Ayomide Akindolie | 2025-11-26 06:00 | 2025-11-26 07:29 | 5324 | 2025-11-26 06:00 | 2025-11-26 07:29 | 1:29 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Top Gasket | 1 / 1 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 2 | Burnt top gasket was replaced (No diesel outage after validation)
NOCINC0006476437 | Internal Reconciliation | Site Down | P4 | IHS_DEL_0928A | T2927 | ASB | Asaba | Delta | 3 - Low | DL1189 | SOUTH SOUTH |  | 2025-11-29 | Mary Odefemi | 2025-11-28 23:56 | 2025-11-29 01:24 | 5303 | 2025-11-28 23:56 | 2025-11-29 01:24 | 1:28 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | HENRY OMELE |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | High DG temperature, coolant was added (No diesel outage after validation)
NOCINC0006464438 | External Reconciliation | Site Down | P2 | IHS_OSU_1025H | OS2687 | IBD | Ibadan | Osun | 3 - Low | OS0778 | WEST |  | 2025-11-27 12:08 | Mutmainnah Saba | 2025-11-27 12:06 | 2025-11-27 13:34 | 5299 | 2025-11-27 12:06 | 2025-11-27 13:34 | 1:28 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | MTN NG, Airtel NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Flat DG battery, external battery was used to power the site
NOCINC0006489703 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0017B | OS2679 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 21:02 | Valentine Adinnu | 2025-11-30 21:01 | 2025-11-30 22:29 | 5293 | 2025-11-30 21:01 | 2025-11-30 22:29 | 1:28 | Energy Vision Nigeria | Site Asset Theft | Theft | Theft | DC Cable Stolen | 2 / 2 | MTN NG, Airtel NG |  | Joshua Peter |  |  | Oladotun Ogunleye | Osas Sunday |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Stolen DC cable was replaced | Stolen DC cable was replaced
NOCINC0006485278 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1033A | ED4944 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 08:26 | Ayomide Akindolie | 2025-11-30 08:20 | 2025-11-30 09:49 | 5292 | 2025-11-30 08:20 | 2025-11-30 09:49 | 1:28 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | AZUBUIKE EMEH | Shagba Terkula | Emeh Azubike | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected Passive Issue, Awaiting Update from FSE. | Suspected Passive Issue, Awaiting Update from FSE.
NOCINC0006470085 | External Reconciliation | Site Down | P2 | IHS_OSU_0820A | T3606 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 06:19 | Marvellous Emecheta | 2025-11-28 06:18 | 2025-11-28 07:45 | 5268 | 2025-11-28 06:18 | 2025-11-28 07:45 | 1:28 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Panel Board | 1 / 1 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 3 | Faulty DCDG Trion module was worked on
NOCINC0006451986 | External Reconciliation | Site Down | P4 | IHS_OYO_1353B | OY4327 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 21:16 | Aishat Oyedeji | 2025-11-25 21:16 | 2025-11-25 22:43 | 5252 | 2025-11-25 21:16 | 2025-11-25 22:43 | 1:28 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Taiwo Abanikannda |  |  | Soye West | Ugwu Samuel Nnamdi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting passive update from Fse. | Suspected passive issue, awaiting passive update from Fse.
NOCINC0006450064 | External Reconciliation | Site Down | P1 | IHS_BEN_0023V | ED5366 | IBD | Asaba | Edo | 3 - Low | ED0420 | SOUTH SOUTH |  | 2025-11-25 16:35 | Oluwatobiloba Are | 2025-11-25 16:27 | 2025-11-25 17:54 | 5213 | 2025-11-25 16:27 | 2025-11-25 17:54 | 1:27 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 3 | MTN NG, Airtel NG |  | KAZEEM AJIBOYE |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006457809 | External Reconciliation | Site Down | P3 | IHS_WAR_0963C | DL4026 | ASB | Asaba | Delta | 3 - Low | DL0975 | SOUTH SOUTH |  | 2025-11-26 13:19 | Mary Odefemi | 2025-11-26 13:15 | 2025-11-26 14:42 | 5210 | 2025-11-26 13:15 | 2025-11-26 14:42 | 1:27 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 4 | Faulty radiator was worked (No diesel outage after validation)
NOCINC0006476225 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1118A | DL0580 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 22:47 | Mary Odefemi | 2025-11-28 22:42 | 2025-11-29 00:08 | 5158 | 2025-11-28 22:42 | 2025-11-29 00:08 | 1:26 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Main Alternator | 1 / 1 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty main alternator was replaced (No diesel outage after validation)
NOCINC0006481432 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1175A | DL0676 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 16:36 | Quadri Ogundare | 2025-11-29 16:30 | 2025-11-29 17:56 | 5155 | 2025-11-29 16:30 | 2025-11-29 17:56 | 1:26 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | Airtel NG, MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Weak DG battery, external battery was used to power site (No diesel outage after validation)
NOCINC0006471297 | Internal Reconciliation | Site Down | P2 | IHS_ONT_0014V | - | - | Asaba | Anambra | 3 - Low | AN0468 | SOUTH EAST |  | 2025-11-28 10:21 | Abundance Otunola | 2025-11-28 10:19 | 2025-11-28 11:45 | 5144 | 2025-11-28 10:19 | 2025-11-28 11:45 | 1:26 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, Smile |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty Injector pump was serviced.
NOCINC0006482974 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0957A | OS2651 | IBD | Ibadan | Osun | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-29 20:52:25@OS2651_Ajagba Olaoluwa LGA | 2025-11-29 21:09 | System Administrator | 2025-11-29 20:56 | 2025-11-29 22:22 | 5140 | 2025-11-29 20:56 | 2025-11-29 22:22 | 1:26 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Emeh Henry |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start
NOCINC0006472052 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0883A | T2770 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 12:09 | Uthman Akinola | 2025-11-28 12:07 | 2025-11-28 13:32 | 5131 | 2025-11-28 12:07 | 2025-11-28 13:32 | 1:26 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier - Circuit Breaker | 1 / 1 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed rectifier circuit breaker was enabled(no diesel outage after validation)
NOCINC0006442807 | External Reconciliation | Site Down | P2 | IHS_OND_0061B | OD4825 | IBD | Ibadan | Ondo | 3 - Low | ON0777 | WEST |  | 2025-11-24 18:10 | Ihuoma Opurum | 2025-11-24 18:08 | 2025-11-24 19:33 | 5100 | 2025-11-24 18:08 | 2025-11-24 19:33 | 1:25 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | Airtel NG, MTN NG |  | Sanusi Idowu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Failed rectifier controller was worked on
NOCINC0006480623 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0019B | DL0427 | ASB | Asaba | Delta | 3 - Low | DL1270 | SOUTH SOUTH |  | 2025-11-29 14:42 | Ayomide Akindolie | 2025-11-29 14:42 | 2025-11-29 16:07 | 5092 | 2025-11-29 14:42 | 2025-11-29 16:07 | 1:25 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on (No diesel outage after validation)
NOCINC0006456400 | External Reconciliation | Site Down | P1 | IHS_DEL_0862A | T2756 | ASB | Asaba | Delta | 3 - Low | DL0241 | SOUTH SOUTH |  | 2025-11-26 09:57 | Mary Odefemi | 2025-11-26 09:53 | 2025-11-26 11:18 | 5088 | 2025-11-26 09:53 | 2025-11-26 11:18 | 1:25 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | MTN NG |  | Kenneth Oboniye |  |  | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 8 | IHSREF/25112516130647936737 SARID0009045602 for IHS_DEL_0862A PURPOSE: RMS Maintenance BY Emmanuel from UZIBEN.
NOCINC0006449629 | External Reconciliation | Site Down | P2 | IHS_OYO_0790A | T3004 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 15:41 | Tunji Adejumo | 2025-11-25 15:22 | 2025-11-25 16:45 | 4995 | 2025-11-25 15:22 | 2025-11-25 16:45 | 1:23 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 3 | Spectranet |  | Olaitan Olajide | Habeeb Adepoju |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | low bus voltage alarm was cleared from the control module.
NOCINC0006474054 | Internal Reconciliation | Site Down | P1 | IHS_OND_0775A | T3404 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 17:13 | Testimony Akinyemi | 2025-11-28 17:13 | 2025-11-28 18:36 | 4991 | 2025-11-28 17:13 | 2025-11-28 18:36 | 1:23 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 2 / 2 | MTN NG, Airtel NG |  | Mercy Oni |  | Ojadua Olusegun | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | faulty water pump was replaced
NOCINC0006446612 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-25 09:34 | Emmanuel Faleti | 2025-11-25 09:33 | 2025-11-25 10:56 | 4986 | 2025-11-25 09:33 | 2025-11-25 10:56 | 1:23 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty Radiator was worked on to restore power on site (No diesel outage after validation) | Faulty Radiator was worked on to restore power on site (No diesel outage after validation)
NOCINC0006436473 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST |  | 2025-11-23 23:57 | Gbemisola Adedeji | 2025-11-23 23:53 | 2025-11-24 01:23 | 5410 | 2025-11-24 | 2025-11-24 01:23 | 1:23 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation). | Weak DG was primed to start (No diesel outage after validation).
NOCINC0006455465 | External Reconciliation | Site Down | P1 | IHS_WAR_0019B | DL0427 | ASB | Asaba | Delta | 3 - Low | DL1270 | SOUTH SOUTH |  | 2025-11-26 06:58 | Ayomide Akindolie | 2025-11-26 06:56 | 2025-11-26 08:19 | 4961 | 2025-11-26 06:56 | 2025-11-26 08:19 | 1:23 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on (No diesel outage after validation)
NOCINC0006478840 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0718E | - | - | Asaba | Edo | 3 - Low | ED0748 | SOUTH SOUTH |  | 2025-11-29 10:59 | Azeezat Badmus | 2025-11-29 10:59 | 2025-11-29 12:22 | 4951 | 2025-11-29 10:59 | 2025-11-29 12:22 | 1:23 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | Airtel NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | faulty charging alternator was worked on (No diesel outage after validation)
NOCINC0006484070 | Internal Reconciliation | Site Down | P2 | IHS_OND_0894A | OD2408 | IBD | Ibadan | Ondo | 3 - Low | ON0706 | WEST |  | 2025-11-30 01:25 | Abisoye Olaleye | 2025-11-30 01:23 | 2025-11-30 02:46 | 4932 | 2025-11-30 01:23 | 2025-11-30 02:46 | 1:22 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 2 / 2 | MTN NG, Airtel NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty solenoid coil was bypassed pending replacement
NOCINC0006463256 | External Reconciliation | Site Down | P3 | IHS_OSU_0073B | OS4386 | IBD | Ibadan | Osun | 3 - Low | OS0712 | WEST |  | 2025-11-27 09:08 | Titus Tosin | 2025-11-27 09:05 | 2025-11-27 10:28 | 4932 | 2025-11-27 09:05 | 2025-11-27 10:28 | 1:22 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on
NOCINC0006463142 | External Reconciliation | Site Down | P1 | IHS_DEL_0929A | T2950 | ASB | Asaba | Delta | 3 - Low | DL0580 | SOUTH SOUTH |  | 2025-11-27 08:43 | Femi Olanipekun | 2025-11-27 08:41 | 2025-11-27 09:56 | 4451 | 2025-11-27 08:33 | 2025-11-27 09:56 | 1:22 | Tyllium NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty injector pump was worked on (No diesel outage after validation) | Faulty injector pump was worked on (No diesel outage after validation)
NOCINC0006448103 | External Reconciliation | Site Down | P4 | IHS_EKI_0851A | EK2263 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-25 12:31 | Tunji Adejumo | 2025-11-25 12:30 | 2025-11-25 13:52 | 4930 | 2025-11-25 12:30 | 2025-11-25 13:52 | 1:22 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | failed charging alternator was excited
NOCINC0006465591 | External Reconciliation | Site Down | P3 | IHS_OND_0058B | OD4813 | IBD | Ibadan | Ondo | 3 - Low | ON0686 | WEST |  | 2025-11-27 14:39 | Iyesioluwa Ola | 2025-11-27 14:39 | 2025-11-27 16:01 | 4918 | 2025-11-27 14:39 | 2025-11-27 16:01 | 1:22 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 2 / 2 | MTN NG, Airtel NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty Lift Pump was worked on
NOCINC0006455263 | External Reconciliation | Site Down | P1 | IHS_KWA_0759A | T3136 | IBD | Ibadan | Kwara | 3 - Low | - | - | gNodeB Out of Service@2025-11-26 05:57:37@N3136 | 2025-11-26 06:11 | System Administrator | 2025-11-26 05:58 | 2025-11-26 07:19 | 4879 | 2025-11-26 05:58 | 2025-11-26 07:19 | 1:21 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 1 / 1 | MTN NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | faulty fuel pump was worked on
NOCINC0006475122 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0939A | OS2708 | IBD | Ibadan | Kwara | 3 - Low | OS0817 | WEST |  | 2025-11-28 19:56 | Maureen Uchehorke | 2025-11-28 19:56 | 2025-11-28 21:17 | 4877 | 2025-11-28 19:56 | 2025-11-28 21:17 | 1:21 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | MTN NG |  | Enorch Dauda |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting RCA from FSE
NOCINC0006437695 | External Reconciliation | Site Down | P4 | IHS_OND_0858A | T3836 | IBD | Ibadan | Ondo | 3 - Low | - | - | CSL Fault@2025-11-24 04:10:22@T3836_Adebayo streetOre | 2025-11-24 04:23 | System Administrator | 2025-11-24 04:10 | 2025-11-24 05:32 | 4877 | 2025-11-24 04:10 | 2025-11-24 05:32 | 1:21 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Oluwaseun Awolope |  |  | Ibrahim Akinpelu | Oluwaseun Awolope |  | John Momoh | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen SMU,SMU was reset.
NOCINC0006459336 | External Reconciliation | Site Down | P2 | IHS_OSU_0959A | OS4283 | IBD | Ibadan | Osun | 3 - Low | OS0763 | WEST |  | 2025-11-26 17:19 | Marvellous Emecheta | 2025-11-26 17:17 | 2025-11-26 18:38 | 4875 | 2025-11-26 17:17 | 2025-11-26 18:38 | 1:21 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Control Panel | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Faulty control module was worked on
NOCINC0006470573 | External Reconciliation | Site Down | P2 | IHS_OSU_0948A | OS2623 | IBD | Ibadan | Osun | 3 - Low | OS0682 | WEST |  | 2025-11-28 08:33 | Oluwatomisin Ogunleye | 2025-11-28 08:31 | 2025-11-28 09:52 | 4863 | 2025-11-28 08:31 | 2025-11-28 09:52 | 1:21 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on | Faulty injector pump was worked on
NOCINC0006477701 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0727C | DL0990 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 07:48 | Mary Odefemi | 2025-11-29 07:45 | 2025-11-29 09:06 | 4842 | 2025-11-29 07:45 | 2025-11-29 09:06 | 1:21 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on (No diesel outage after validation) | Faulty injector pump was worked on (No diesel outage after validation)
NOCINC0006488033 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0945C | KW6396 | IBD | Ibadan | Kwara | 3 - Low | KW0487 | WEST | 4G ZTE Sitedown@2025-11-30 15:29:46@KW0487(40487) | 2025-11-30 15:46 | System Administrator | 2025-11-30 15:30 | 2025-11-30 16:50 | 4840 | 2025-11-30 15:30 | 2025-11-30 16:50 | 1:21 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | Airtel NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting update from FSE
NOCINC0006489550 | Internal Reconciliation | Site Down | P3 | IHS_OZO_0001C | DL0884 | ASB | Asaba | Delta | 3 - Low | DL0715 | SOUTH SOUTH |  | 2025-11-30 20:30 | Solomon Bankole | 2025-11-30 20:14 | 2025-11-30 21:35 | 4837 | 2025-11-30 20:14 | 2025-11-30 21:35 | 1:21 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Low DG frequency, Governor was adjusted ( No diesel outage after validation) | Low DG frequency, Governor was adjusted ( No diesel outage after validation)
NOCINC0006470469 | External Reconciliation | Site Down | P2 | IHS_OND_0777A | T3405 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 08:08 | Mary Elaigwu | 2025-11-28 08:06 | 2025-11-28 09:26 | 4801 | 2025-11-28 08:06 | 2025-11-28 09:26 | 1:20 | Biswal | Equipment Repair | Passive | DCGG DB | DCGG - Faulty Expansion Board | 1 / 1 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | DG expansion board was reset
NOCINC0006465806 | External Reconciliation | Site Down | P4 | IHS_DEL_1142A | DL0762 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 15:12 | Uthman Akinola | 2025-11-27 15:12 | 2025-11-27 16:31 | 4732 | 2025-11-27 15:11 | 2025-11-27 16:31 | 1:20 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG under frequency, governor was adjusted(no diesel outage after validation)
NOCINC0006466254 | External Reconciliation | Site Down | P1 | IHS_EKI_0890B | EK6327 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-27 16:08 | Kandervil Uwah | 2025-11-27 16:06 | 2025-11-27 17:27 | 4823 | 2025-11-27 16:07 | 2025-11-27 17:27 | 1:19 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | failed charging alternator was excited
NOCINC0006441523 | External Reconciliation | Site Down | P1 | IHS_DEL_1151A | DL0675 | ASB | Asaba | Delta | 3 - Low | DL0761 | SOUTH SOUTH |  | 2025-11-24 15:39 | Ayomide Akindolie | 2025-11-24 15:39 | 2025-11-24 16:59 | 4767 | 2025-11-24 15:39 | 2025-11-24 16:59 | 1:19 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fan Belt | 2 / 2 | MTN NG, Airtel NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Loose Fan Belt Pulley was re-tightened (No diesel outage after validation). | Loose Fan Belt Pulley was re-tightened (No diesel outage after validation).
NOCINC0006443437 | External Reconciliation | Site Down | P2 | IHS_OSU_0959A | OS4283 | IBD | Ibadan | Osun | 3 - Low | OS0763 | WEST |  | 2025-11-24 19:54 | Hardy Oko | 2025-11-24 19:52 | 2025-11-24 21:11 | 4739 | 2025-11-24 19:52 | 2025-11-24 21:11 | 1:19 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Control Panel | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty DG module was worked on | Faulty DG module was worked on
NOCINC0006470047 | External Reconciliation | Site Down | P1 | IHS_KWA_0912A | KW4643 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 06:08 | Marvellous Emecheta | 2025-11-28 06:03 | 2025-11-28 07:21 | 4714 | 2025-11-28 06:03 | 2025-11-28 07:21 | 1:19 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Charging Alternator | 1 / 1 | MTN NG |  | Enorch Dauda |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 5 | Failed charging alternator was excited
NOCINC0006455760 | External Reconciliation | Site Down | P2 | IHS_KWA_0741A | T3117 | IBD | Ibadan | Kwara | 3 - Low | KW0516 | WEST | 4G ZTE Sitedown@2025-11-26 07:37:04@KW0516(40516) | 2025-11-26 07:49 | System Administrator | 2025-11-26 07:37 | 2025-11-26 08:56 | 4711 | 2025-11-26 07:37 | 2025-11-26 08:56 | 1:19 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | faulty charging alternator was worked on
NOCINC0006451004 | External Reconciliation | Site Down | P1 | IHS_ANA_1166A | AN0765 | ASB | Asaba | Enugu | 3 - Low | AN0894 | SOUTH EAST |  | 2025-11-25 19:01 | Oluwatoyin Fagite | 2025-11-25 18:56 | 2025-11-25 20:15 | 4708 | 2025-11-25 18:56 | 2025-11-25 20:15 | 1:18 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Oladele Segun | David Ndubuisi | David Ndubuisi | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Failed charging alternator was excited. (No diesel outage after validation) | Failed charging alternator was excited. (No diesel outage after validation)
NOCINC0006441378 | External Reconciliation | Site Down | P2 | IHS_EDO_0976A | ED2148 | IBD | Asaba | Edo | 3 - Low | ED0659 | SOUTH SOUTH |  | 2025-11-24 15:17 | Oluwatomisin Sogbesan | 2025-11-24 15:15 | 2025-11-24 16:33 | 4689 | 2025-11-24 15:15 | 2025-11-24 16:33 | 1:18 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Fip Solenoid Cable Faulty | 2 / 2 | MTN NG, Airtel NG |  | Hammed Abubakar |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty solenoid switch cable was worked on (No diesel outage after validation) | Faulty solenoid switch cable was worked on (No diesel outage after validation)
NOCINC0006484829 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 06:20 | Uthman Akinola | 2025-11-30 06:05 | 2025-11-30 07:41 | 5731 | 2025-11-30 06:23 | 2025-11-30 07:41 | 1:18 | Tyllium NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty injector pump was worked on. (No diesel outage after validation) | Faulty injector pump was worked on. (No diesel outage after validation)
NOCINC0006485259 | Internal Reconciliation | Site Down | P2 | IHS_ANA_0847A | T4031 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 08:23 | Uthman Akinola | 2025-11-30 08:22 | 2025-11-30 09:40 | 4676 | 2025-11-30 08:22 | 2025-11-30 09:40 | 1:18 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Clogged Radiator | 1 / 1 | MTN NG |  | Kingsley Obele | Kingsley Obele | Kingsley Obele | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | High engine temperature due to clogged radiator, radiator was flushed and coolant was added(No diesel outage after validation) | High engine temperature due to clogged radiator, radiator was flushed and coolant was added(No diesel outage after validation)
NOCINC0006464410 | External Reconciliation | Site Down | P4 | IHS_EDO_1101C | ED6122 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 12:02 | Bukola Olabanji | 2025-11-27 12:02 | 2025-11-27 13:20 | 4669 | 2025-11-27 12:02 | 2025-11-27 13:20 | 1:18 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Insufficient Rectifier module, module was added (no diesel outage after validation).
NOCINC0006458207 | External Reconciliation | Site Down | P1 | IHS_EDO_0998A | ED4856 | IBD | Asaba | Edo | 3 - Low | ED0968 | SOUTH SOUTH |  | 2025-11-26 14:22 | Azeezat Badmus | 2025-11-26 14:21 | 2025-11-26 15:38 | 4667 | 2025-11-26 14:21 | 2025-11-26 15:38 | 1:18 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Generator servicing was completed at site (No diesel outage after validation) | Generator servicing was completed at site (No diesel outage after validation)
NOCINC0006450183 | External Reconciliation | Site Down | P1 | IHS_WAR_0907H | DL0003 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 16:48 | Ezinne Ubachukwu | 2025-11-25 16:45 | 2025-11-25 18:02 | 4657 | 2025-11-25 16:45 | 2025-11-25 18:02 | 1:18 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 1 / 1 | MTN NG |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Blocked radiator was flushed (No diesel outage after validation) | Blocked radiator was flushed (No diesel outage after validation)
NOCINC0006473910 | Internal Reconciliation | Site Down | P2 | IHS_OND_0870A | T3870 | IBD | Ibadan | Ondo | 3 - Low | - | - | Cascaded Incident from TTO6759678 - Cascade Removed From TTO6759678 | 2025-11-28 16:53 | Testimony Akinyemi | 2025-11-28 16:49 | 2025-11-28 18:06 | 4648 | 2025-11-28 16:49 | 2025-11-28 18:06 | 1:17 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Mercy Oni |  | Ojadua Olusegun | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | hybrid synchronization failure due to frozen csu orion, csu was reset
NOCINC0006466980 | External Reconciliation | Site Down | P2 | IHS_KWA_0902A | KW4577 | IBD | Ibadan | Kwara | 3 - Low | KW0457 | WEST |  | 2025-11-27 18:08 | Titus Tosin | 2025-11-27 18:06 | 2025-11-27 19:23 | 4647 | 2025-11-27 18:06 | 2025-11-27 19:23 | 1:17 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Air Intake | 2 / 2 | MTN NG, Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Fuel line airlock was flushed
NOCINC0006438439 | External Reconciliation | Site Down | P2 | IHS_OND_1000A | OD4809 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-24 08:15 | Abisoye Olaleye | 2025-11-24 08:11 | 2025-11-24 09:28 | 4642 | 2025-11-24 08:11 | 2025-11-24 09:28 | 1:17 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Benjamin Onwu |  |  | Ibrahim Akinpelu | Benjamin Onwu |  | Victor Adeoye | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Hybrid synchronization failure due to frozen SMU was reset.
NOCINC0006457041 | External Reconciliation | Site Down | P3 | IHS_EDO_1245B | ED5509 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 11:30 | Mary Odefemi | 2025-11-26 11:27 | 2025-11-26 12:26 | 3548 | 2025-11-26 11:09 | 2025-11-26 12:26 | 1:17 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Suspected passive, Awaiting update from FSE | Suspected passive fault
NOCINC0006458168 | External Reconciliation | Site Down | P4 | IHS_EDO_1239B | ED5540 | IBD | Asaba | Edo | 3 - Low | ED1106 | South South | Site Abis control link broken@2025-11-26 14:00:28@ED1106 | 2025-11-26 14:19 | System Administrator | 2025-11-26 14:00 | 2025-11-26 15:17 | 4614 | 2025-11-26 14:00 | 2025-11-26 15:17 | 1:17 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Kazeem Ajiboye |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty charging alternator was worked on. (No diesel outage after validation) | Faulty charging alternator was worked on. (No diesel outage after validation)
NOCINC0006475180 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0825A | T3979 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 20:05 | Titus Tosin | 2025-11-28 20:02 | 2025-11-28 21:19 | 4601 | 2025-11-28 20:02 | 2025-11-28 21:19 | 1:17 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 5 | Faulty injector pump was worked on
NOCINC0006445401 | External Reconciliation | Site Down | P3 | IHS_OYO_1378B | - | - | Ibadan | Oyo | 3 - Low | OY1094 | WEST |  | 2025-11-25 05:27 | Damilola Paseda | 2025-11-25 05:26 | 2025-11-25 06:43 | 4578 | 2025-11-25 05:26 | 2025-11-25 06:43 | 1:16 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | Airtel NG |  | Taiwo Abanikannda |  |  | Soye West | Ugwu Samuel Nnamdi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid Synchronization failure due to flat DG battery, external battery was used to power site. | Hybrid Synchronization failure due to flat DG battery, external battery was used to power site.
NOCINC0006470079 | External Reconciliation | Site Down | P3 | IHS_LFG_0001B | KW4585 | IBD | Ibadan | Kwara | 3 - Low | KW0412 | WEST |  | 2025-11-28 06:17 | Marvellous Emecheta | 2025-11-28 06:13 | 2025-11-28 07:29 | 4577 | 2025-11-28 06:13 | 2025-11-28 07:29 | 1:16 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Lifting Pump Faulty | 2 / 2 | MTN NG, Airtel NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | faulty fuel pump was worked on
NOCINC0006455912 | External Reconciliation | Site Down | P3 | IHS_OSU_0731E | OS4656 | IBD | Ibadan | Osun | 3 - Low | OS0646 | WEST |  | 2025-11-26 08:20 | Marvellous Emecheta | 2025-11-26 08:19 | 2025-11-26 09:35 | 4576 | 2025-11-26 08:19 | 2025-11-26 09:35 | 1:16 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Radiator Leakage | 2 / 2 | MTN NG, Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | faulty Radiator was worked on
NOCINC0006477508 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0967A | ED2046 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 06:58 | Elizabeth Apata | 2025-11-29 06:58 | 2025-11-29 08:14 | 4574 | 2025-11-29 06:58 | 2025-11-29 08:14 | 1:16 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on .(No diesel outage after validation).
NOCINC0006484073 | Internal Reconciliation | Site Down | P4 | IHS_ONT_0083B | AN0905 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-30 01:13:38@AN0905_Adazi Nnukwu | 2025-11-30 01:26 | System Administrator | 2025-11-30 01:14 | 2025-11-30 02:30 | 4563 | 2025-11-30 01:14 | 2025-11-30 02:30 | 1:16 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Ezimeruwe ANTHONY |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Tripped DG load breaker was enabled (No diesel outage after validation). | Tripped DG load breaker was enabled (No diesel outage after validation).
NOCINC0006454724 | External Reconciliation | Site Down | P4 | IHS_OSU_0732E | OS4698 | IBD | Ibadan | Osun | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-26 02:09:00@OS4698_IHS | 2025-11-26 02:25 | System Administrator | 2025-11-26 02:13 | 2025-11-26 03:29 | 4558 | 2025-11-26 02:13 | 2025-11-26 03:29 | 1:16 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 2 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset
NOCINC0006456060 | External Reconciliation | Site Down | P1 | IHS_DEL_1176A | DL0497 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 08:52 | Mary Odefemi | 2025-11-26 08:49 | 2025-11-26 10:04 | 4497 | 2025-11-26 08:48 | 2025-11-26 10:04 | 1:16 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Unbalanced | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Phase loss due to unbalanced load was resolved and DG was powered
NOCINC0006467180 | External Reconciliation | Site Down | P3 | IHS_DEL_1149A | DL0635 | ASB | Asaba | Delta | 3 - Low | DL0723 | SOUTH SOUTH |  | 2025-11-27 18:45 | Mary Odefemi | 2025-11-27 18:44 | 2025-11-27 20:00 | 4548 | 2025-11-27 18:44 | 2025-11-27 20:00 | 1:16 | BJ Bison NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure, DG was powered manually (no diesel outage after validation).
NOCINC0006470361 | External Reconciliation | Site Down | P4 | IHS_ANA_1179A | AN0694 | ASB | Asaba | Anambra | 3 - Low | AN1114 | SOUTH EAST |  | 2025-11-28 07:46 | Oluwatoyin Fagite | 2025-11-28 07:42 | 2025-11-28 08:58 | 4540 | 2025-11-28 07:42 | 2025-11-28 08:58 | 1:16 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Femi Balogun | Femi Balogun | Femi Balogun | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed charging alternator was excited(No diesel outage after validation) | Failed charging alternator was excited(No diesel outage after validation)
NOCINC0006461080 | External Reconciliation | Site Down | P2 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 22:17 | Oluwatomisin Sogbesan | 2025-11-26 22:17 | 2025-11-26 23:32 | 4539 | 2025-11-26 22:17 | 2025-11-26 23:32 | 1:16 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Team confirmed site is affected by ed4860 | Team confirmed site is affected by ed4860
NOCINC0006455562 | External Reconciliation | Site Down | P2 | IHS_OND_1074H | OD6009 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 07:04 | Ihuoma Opurum | 2025-11-26 07:04 | 2025-11-26 08:19 | 4517 | 2025-11-26 07:04 | 2025-11-26 08:19 | 1:15 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 2 / 2 | MTN NG, Airtel NG |  | Habeed Yunus |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | faulty tempearture sensor switch was worked on
NOCINC0006440960 | External Reconciliation | Site Down | P2 | IHS_IBA_0014V | OY4050 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 14:35 | Aishat Oyedeji | 2025-11-24 14:32 | 2025-11-24 15:47 | 4512 | 2025-11-24 14:32 | 2025-11-24 15:47 | 1:15 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | BASHIR ABDULRASAQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Suspected passive issue awaiting RCA from FSE
NOCINC0006448557 | External Reconciliation | Site Down | P3 | IHS_ANA_1219A | AN0603 | ASB | Asaba | Anambra | 3 - Low | AN0959 | SOUTH EAST |  | 2025-11-25 13:30 | Aderonke Olowojoba | 2025-11-25 13:26 | 2025-11-25 14:41 | 4504 | 2025-11-25 13:26 | 2025-11-25 14:41 | 1:15 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty radiator was worked on (No diesel outage after validation | Faulty radiator was worked on (No diesel outage after validation
NOCINC0006477032 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0787A | T3012 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 04:13 | Bosede Kutelu | 2025-11-29 04:11 | 2025-11-29 05:26 | 4496 | 2025-11-29 04:11 | 2025-11-29 05:26 | 1:15 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Smile |  | ADEMOLA ADELEKE |  | Olumide Adebayo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed Charging Alternator was excited
NOCINC0006477138 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0804A | T3777 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 04:46 | Ihuoma Opurum | 2025-11-29 04:37 | 2025-11-29 05:52 | 4490 | 2025-11-29 04:37 | 2025-11-29 05:52 | 1:15 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG undervoltage alarm was cleared and DG was powered manually.
NOCINC0006466862 | External Reconciliation | Site Down | P4 | IHS_EDO_1045C | ED6119 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 17:48 | Elizabeth Apata | 2025-11-27 17:47 | 2025-11-27 19:01 | 4484 | 2025-11-27 17:47 | 2025-11-27 19:01 | 1:15 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Kazeem Ajiboye |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | hook injector pump was serviced (No diesel outage after validation)
NOCINC0006448990 | External Reconciliation | Site Down | P3 | IHS_EDO_0987A | ED2044 | IBD | Asaba | Edo | 3 - Low | ED0551 | SOUTH SOUTH |  | 2025-11-25 14:14 | Oluwatomisin Sogbesan | 2025-11-25 14:11 | 2025-11-25 15:24 | 4398 | 2025-11-25 14:10 | 2025-11-25 15:24 | 1:15 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006466704 | External Reconciliation | Site Down | P4 | IHS_EDO_1240B | ED5542 | IBD | Asaba | Edo | 3 - Low | ED1126 | SOUTH SOUTH |  | 2025-11-27 17:22 | Bukola Olabanji | 2025-11-27 17:21 | 2025-11-27 18:36 | 4472 | 2025-11-27 17:21 | 2025-11-27 18:36 | 1:15 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Jude Audu | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on (no diesel outage after validation).
NOCINC0006483361 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1460C | AN4025 | ASB | Asaba | Anambra | 3 - Low | AN0983 | SOUTH EAST |  | 2025-11-29 22:04 | Gbemisola Adedeji | 2025-11-29 22:02 | 2025-11-29 23:16 | 4468 | 2025-11-29 22:02 | 2025-11-29 23:16 | 1:14 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 2 / 2 | MTN NG, Airtel NG |  | Ugochuku Agbamuche | Ugo Agamuche | Ugo Agamuche | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty lift pump was worked on (No diesel outage after validation) | Faulty lift pump was worked on (No diesel outage after validation)
NOCINC0006448924 | External Reconciliation | Site Down | P1 | IHS_UMU_0001B | AN0093 | ASB | Asaba | Anambra | 3 - Low | AN0453 | SOUTH EAST |  | 2025-11-25 14:04 | Oluwatoyin Fagite | 2025-11-25 14:03 | 2025-11-25 15:17 | 4452 | 2025-11-25 14:03 | 2025-11-25 15:17 | 1:14 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Aneke Christian | Habib Muhammed | Habib Muhammed | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty rectifier module was replaced (No diesel outage after validation) | Faulty rectifier module was replaced (No diesel outage after validation)
NOCINC0006463629 | External Reconciliation | Site Down | P3 | IHS_EDO_0831A | T3280 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 10:15 | Muhammed Hashirudeen | 2025-11-27 10:12 | 2025-11-27 11:26 | 4429 | 2025-11-27 10:12 | 2025-11-27 11:26 | 1:14 | Huawei | Fuel Outage (Probable) | Passive | Diesel | Tank Sealing Issue - Water In The Fuel | 1 / 1 | MTN NG |  | Christopher Aiyenale |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Water ingress; water was separated from diesel (No diesel outage after validation)
NOCINC0006449430 | External Reconciliation | Site Down | P3 | IHS_EDO_1337B | ED2262 | - | Asaba | Edo | 3 - Low | ED0853 | SOUTH SOUTH |  | 2025-11-25 15:11 | Emmanuel Faleti | 2025-11-25 15:11 | 2025-11-25 16:25 | 4419 | 2025-11-25 15:11 | 2025-11-25 16:25 | 1:14 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Asukwo Effiong |  |  | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited. (No diesel outage after validation) | Failed charging alternator was excited. (No diesel outage after validation)
NOCINC0006437213 | External Reconciliation | Site Down | P1 | IHS_OSU_0770A | T0300 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 01:18 | Osarieme Charles | 2025-11-24 01:11 | 2025-11-24 02:24 | 4408 | 2025-11-24 01:11 | 2025-11-24 02:24 | 1:13 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 1 | MTN NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 4 | DG-Grid synchronisation failure due to unstable grid supply, Dg powered manually
NOCINC0006445221 | External Reconciliation | Site Down | P3 | IHS_EDO_1043C | ED6117 | IBD | Asaba | Edo | 3 - Low | - | - | CSL Fault@2025-11-25 03:35:04@ED6117_ COUNTRY HOME | 2025-11-25 03:57 | System Administrator | 2025-11-25 03:35 | 2025-11-25 04:48 | 4378 | 2025-11-25 03:35 | 2025-11-25 04:48 | 1:13 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 1 / 1 | MTN NG |  | Kazeem Ajiboye |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Faulty fuel pump was worked on (No diesel outage after validation)
NOCINC0006452302 | External Reconciliation | Site Down | P1 | IHS_OYO_1197H | - | - | Ibadan | Oyo | 3 - Low | OY1033 | WEST |  | 2025-11-25 22:33 | Aishat Oyedeji | 2025-11-25 22:25 | 2025-11-25 23:38 | 4377 | 2025-11-25 22:25 | 2025-11-25 23:38 | 1:13 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty Avr was worked on
NOCINC0006445866 | External Reconciliation | Site Down | P1 | IHS_ANA_1103A | AN0332 | ASB | Asaba | Anambra | 3 - Low | - | - | Cascaded Incident from TTO6728776 - Cascade Removed From TTO6728776 | 2025-11-25 07:58 | Kehinde Akinbowale | 2025-11-25 07:52 | 2025-11-25 09:05 | 4351 | 2025-11-25 07:52 | 2025-11-25 09:05 | 1:13 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Augustine Okoro | Ademola Adekunle | Ademola Adekunle | Henry Wanogho | Ifeanyi Chukusa |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Low DG frequency, governor was adjusted (No diesel outage after validation) | Low DG frequency, governor was adjusted (No diesel outage after validation)
NOCINC0006490053 | Resolved | Site Down | P3 | IHS_EDO_0874A | ED3970 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 22:07 | Azeezat Badmus | 2025-11-30 22:06 | 2025-11-30 23:19 | 4347 | 2025-11-30 22:06 | 2025-11-30 23:19 | 1:12 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Weak DG was primed to start(No diesel outage after validation)
NOCINC0006461645 | External Reconciliation | Site Down | P2 | IHS_OKP_0004B | AN0326 | ASB | Asaba | Anambra | 3 - Low | AN0404 | SOUTH EAST |  | 2025-11-27 00:21 | Aderonke Olowojoba | 2025-11-27 00:18 | 2025-11-27 01:30 | 4342 | 2025-11-27 00:18 | 2025-11-27 01:30 | 1:12 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006466551 | External Reconciliation | Site Down | P4 | IHS_IBA_0086B | OY4185 | IBD | Ibadan | Oyo | 3 - Low | - | - | CSL Fault@2025-11-27 16:41:57@OY4185_Aba Eko Rd Moniya | 2025-11-27 16:54 | System Administrator | 2025-11-27 16:42 | 2025-11-27 17:56 | 4442 | 2025-11-27 16:44 | 2025-11-27 17:56 | 1:12 | SPS | Equipment Repair | Passive | Infrastructure | Armoured Cable | 1 / 1 | MTN NG |  | Oremade Yusuf |  | Iyiola Azeez | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DC cable was reterminated
NOCINC0006482440 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1473B | AN3657 | ASB | Asaba | Anambra | 3 - Low | AN0878 | SOUTH EAST |  | 2025-11-29 19:22 | Abundance Otunola | 2025-11-29 19:17 | 2025-11-29 20:30 | 4335 | 2025-11-29 19:17 | 2025-11-29 20:30 | 1:12 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | NNADOZIE CASMIR |  |  | Erik Nwodo | Nwigbo Chijioke |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | High DG temperature alarm was cleared, coolant was added (No diesel outage after validation) | High DG temperature alarm was cleared, coolant was added (No diesel outage after validation)
NOCINC0006478204 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0801A | T0092 | IBD | Ibadan | Oyo | 3 - Low | OY1694 | WEST |  | 2025-11-29 09:29 | Damilola Paseda | 2025-11-29 09:28 | 2025-11-29 10:40 | 4311 | 2025-11-29 09:28 | 2025-11-29 10:40 | 1:12 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Control Panel | 2 / 2 | MTN NG, Airtel NG |  | Lukman Mohammed | Isah Ahmed |  | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 3 | GG high load alarm was cleared from the control panel | GG high load alarm was cleared from the control panel
NOCINC0006487733 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0938A | ED3287 | IBD | Asaba | Edo | 3 - Low | ED0643 | SOUTH SOUTH |  | 2025-11-30 15:01 | Evelyn Emagurehor | 2025-11-30 15:01 | 2025-11-30 16:12 | 4302 | 2025-11-30 15:01 | 2025-11-30 16:12 | 1:12 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Failed Charging Alternator was excited . (No diesel outage after validation). | Failed Charging Alternator was excited . (No diesel outage after validation).
NOCINC0006469917 | External Reconciliation | Site Down | P1 | IHS_ANA_0809A | T4053 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-28 05:29:40@T4053_Peoples Club KM1 OWERRI ROAD | 2025-11-28 05:42 | System Administrator | 2025-11-28 05:30 | 2025-11-28 06:41 | 4297 | 2025-11-28 05:30 | 2025-11-28 06:41 | 1:12 | Tyllium NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Air Intake | 1 / 1 | MTN NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Airlock in fuel line was cleared | Airlock in fuel line was cleared
NOCINC0006474843 | Internal Reconciliation | Site Down | P1 | IHS_OYO_1006A | OY3535 | IBD | Ibadan | Oyo | 3 - Low | OY0732 | WEST |  | 2025-11-28 19:11 | Damilola Paseda | 2025-11-28 19:10 | 2025-11-28 20:18 | 4092 | 2025-11-28 19:10 | 2025-11-28 20:21 | 1:12 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Interface Module Faulty | 2 / 2 | MTN NG, Airtel NG |  | SUNDAY MOSES |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Faulty DG module was worked on | Faulty DG module was worked on
NOCINC0006451260 | External Reconciliation | Site Down | P3 | IHS_OND_0812A | T3941 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-25 19:54 | Mary Elaigwu | 2025-11-25 19:53 | 2025-11-25 21:04 | 4287 | 2025-11-25 19:53 | 2025-11-25 21:04 | 1:11 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Daniel Akinfenwa |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Start failure due to dead crank battery. Alarm was cleared.
NOCINC0006485103 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1449B | AN3476 | ASB | Asaba | Anambra | 3 - Low | AN0744 | SOUTH EAST |  | 2025-11-30 07:33 | Gbemisola Adedeji | 2025-11-30 07:29 | 2025-11-30 08:41 | 4286 | 2025-11-30 07:29 | 2025-11-30 08:41 | 1:11 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on. (No diesel outage after validation) | Faulty injector pump was worked on. (No diesel outage after validation)
NOCINC0006467081 | External Reconciliation | Site Down | P2 | IHS_EDO_1028A | ED4923 | IBD | Asaba | Edo | 3 - Low | ED1071 | South South |  | 2025-11-27 18:29 | Muhammed Hashirudeen | 2025-11-27 18:29 | 2025-11-27 19:40 | 4277 | 2025-11-27 18:29 | 2025-11-27 19:40 | 1:11 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 3 | MTN NG, Smile |  | EKPU SUNDAY |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Burnt rectifier load contactor was replaced (No diesel outage after validation) | Burnt rectifier load contactor was replaced (No diesel outage after validation)
NOCINC0006442831 | External Reconciliation | Site Down | P3 | IHS_OSU_0944A | OS2636 | IBD | Ibadan | Osun | 3 - Low | OS0655 | WEST |  | 2025-11-24 18:15 | Azeezat Adekunle | 2025-11-24 18:13 | 2025-11-24 19:24 | 4275 | 2025-11-24 18:13 | 2025-11-24 19:24 | 1:11 | IPT | Equipment Repair | Passive | ACDG Gen | Gen Temp High | 2 / 2 | MTN NG, Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG high temperature, water and coolant was added
NOCINC0006467956 | External Reconciliation | Site Down | P3 | IHS_OSU_0944A | OS2636 | IBD | Ibadan | Osun | 3 - Low | OS0655 | WEST |  | 2025-11-27 21:09 | Osarieme Charles | 2025-11-27 20:58 | 2025-11-27 22:09 | 4266 | 2025-11-27 20:58 | 2025-11-27 22:09 | 1:11 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Low frequency, Governor was adjusted
NOCINC0006447697 | External Reconciliation | Site Down | P1 | IHS_ANA_1231A | AN0649 | ASB | Asaba | Anambra | 3 - Low | AN0664 | SOUTH EAST |  | 2025-11-25 11:38 | Oluwatoyin Fagite | 2025-11-25 11:35 | 2025-11-25 12:46 | 4265 | 2025-11-25 11:35 | 2025-11-25 12:46 | 1:11 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Oladele Segun | David Ndubuisi | David Ndubuisi | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty AVR was replaced (No diesel outage after validation) | Faulty AVR was replaced (No diesel outage after validation)
NOCINC0006475393 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1364B | OY1004 | IBD | Ibadan | Oyo | 3 - Low | OY1596 | WEST |  | 2025-11-28 20:41 | Bosede Kutelu | 2025-11-28 20:39 | 2025-11-28 21:50 | 4257 | 2025-11-28 20:39 | 2025-11-28 21:50 | 1:11 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Over Voltage | 2 / 2 | MTN NG, Airtel NG |  | BANKOLE SODIQ |  | Filani Oluwatobi | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG over voltage alarm was cleared, DG was powered manually
NOCINC0006476864 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1198B | DL4061 | ASB | Asaba | Delta | 3 - Low | DL0878 | SOUTH SOUTH |  | 2025-11-29 03:21 | Elizabeth Apata | 2025-11-29 03:20 | 2025-11-29 04:31 | 4235 | 2025-11-29 03:20 | 2025-11-29 04:31 | 1:11 | Tyllium NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Adedeji Olusegun |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG failed to start alarm was cleared DG was powered manually. (No diesel outage after validation) | DG failed to start alarm, alarm was cleared DG was powered manually. (No diesel outage after validation)
NOCINC0006443140 | External Reconciliation | Site Down | P2 | IHS_BEN_0723E | ED5140 | IBD | Asaba | Edo | 3 - Low | ED0609 | SOUTH SOUTH |  | 2025-11-24 19:02 | Evelyn Emagurehor | 2025-11-24 19:00 | 2025-11-24 20:11 | 4226 | 2025-11-24 19:00 | 2025-11-24 20:11 | 1:10 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | EKPU SUNDAY |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed Charging Alternator was excited (No diesel outage after validation) | Failed Charging Alternator was excited (No diesel outage after validation)
NOCINC0006439322 | External Reconciliation | Site Down | P4 | IHS_KWA_0811A | T3193 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 10:42 | Precious Attah | 2025-11-24 10:41 | 2025-11-24 11:51 | 4224 | 2025-11-24 10:41 | 2025-11-24 11:51 | 1:10 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Failed rectifier module was replaced
NOCINC0006484529 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1347B | OY1076 | IBD | Ibadan | Oyo | 3 - Low | OY1228 | WEST |  | 2025-11-30 04:36 | Mutmainnah Saba | 2025-11-30 04:32 | 2025-11-30 05:43 | 4217 | 2025-11-30 04:32 | 2025-11-30 05:43 | 1:10 | SPS | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  | Olumide Adebayo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | freeze rectifier CSU was worked on
NOCINC0006470325 | External Reconciliation | Site Down | P2 | IHS_ILO_0065C | KW4737 | IBD | Ibadan | Kwara | 3 - Low | KW0486 | WEST |  | 2025-11-28 07:40 | Osarieme Charles | 2025-11-28 07:34 | 2025-11-28 08:44 | 4214 | 2025-11-28 07:34 | 2025-11-28 08:44 | 1:10 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | DG undervoltage alarm, AVR was adjusted
NOCINC0006437533 | External Reconciliation | Site Down | P4 | IHS_KWA_0764A | T3137 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 02:48 | Okusanya Joseph | 2025-11-24 02:48 | 2025-11-24 03:58 | 4205 | 2025-11-24 02:48 | 2025-11-24 03:58 | 1:10 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Filter | 1 / 1 | MTN NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Airlock in fuel filter was bleeded out
NOCINC0006437355 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST |  | 2025-11-24 01:36 | Gbemisola Adedeji | 2025-11-24 01:32 | 2025-11-24 02:42 | 4198 | 2025-11-24 01:32 | 2025-11-24 02:42 | 1:10 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation). | Weak DG was primed to start (No diesel outage after validation).
NOCINC0006476697 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0989A | OY2802 | IBD | Ibadan | Oyo | 3 - Low | OY0956 | WEST |  | 2025-11-29 01:49 | Bosede Kutelu | 2025-11-29 01:47 | 2025-11-29 02:56 | 4182 | 2025-11-29 01:47 | 2025-11-29 02:56 | 1:10 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Over Frequency | 2 / 2 | Airtel NG, MTN NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG Over Frequency was adjusted
NOCINC0006438303 | External Reconciliation | Site Down | P3 | IHS_ANA_1483B | - | - | Asaba | Anambra | 3 - Low | AN0791 | SOUTH EAST |  | 2025-11-24 07:37 | Gbemisola Adedeji | 2025-11-24 07:32 | 2025-11-24 08:42 | 4179 | 2025-11-24 07:32 | 2025-11-24 08:42 | 1:10 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | Airtel NG |  | Ugwuja Chinonso |  |  | Erik Nwodo | Nwigbo Chijioke |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty DG Injector Pump was worked on to restore power to the site. (No diesel outage after validation) | Faulty DG Injector Pump was worked on to restore power to the site. (No diesel outage after validation)
NOCINC0006465464 | External Reconciliation | Site Down | P3 | IHS_OSU_0073B | OS4386 | IBD | Ibadan | Osun | 3 - Low | OS0712 | WEST |  | 2025-11-27 14:21 | Okusanya Joseph | 2025-11-27 14:20 | 2025-11-27 15:29 | 4170 | 2025-11-27 14:20 | 2025-11-27 15:29 | 1:10 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | faulty fuel pump was worked on
NOCINC0006477994 | Internal Reconciliation | Site Down | P4 | IHS_OND_0798A | T3435 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 08:49 | Testimony Akinyemi | 2025-11-29 08:48 | 2025-11-29 09:57 | 4165 | 2025-11-29 08:48 | 2025-11-29 09:57 | 1:09 | IPT | Equipment Repair | Passive | Control Panel | Relay | 1 / 1 | MTN NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty Relay was Replaced
NOCINC0006459042 | External Reconciliation | Site Down | P1 | IHS_BEN_0006B | ED5101 | IBD | Asaba | Edo | 3 - Low | ED0385 | SOUTH SOUTH |  | 2025-11-26 16:25 | Emmanuel Faleti | 2025-11-26 16:24 | 2025-11-26 17:33 | 4163 | 2025-11-26 16:24 | 2025-11-26 17:33 | 1:09 | Huawei | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | Airtel NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Team confirmed passive snag clearance was done at site with IHSREF/25112517401994231896
NOCINC0006489673 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1329B | OY1043 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 20:52 | Damilola Paseda | 2025-11-30 20:31 | 2025-11-30 21:41 | 4159 | 2025-11-30 20:31 | 2025-11-30 21:41 | 1:09 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty load breaker was replaced | Faulty load breaker was replaced
NOCINC0006484047 | Internal Reconciliation | Site Down | P1 | IHS_OSU_0870A | T3671 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 01:10 | Okusanya Joseph | 2025-11-30 01:09 | 2025-11-30 02:17 | 4106 | 2025-11-30 01:09 | 2025-11-30 02:17 | 1:08 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 1 / 1 | MTN NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Grid to DG synchronization failure due to incomplete phase from Grid. DG was powered manually
NOCINC0006473651 | Internal Reconciliation | Site Down | P3 | IHS_EDO_1032A | ED4943 | IBD | Asaba | Edo | 3 - Low | ED0808 | SOUTH SOUTH |  | 2025-11-28 16:18 | Bukola Olabanji | 2025-11-28 16:17 | 2025-11-28 17:26 | 4096 | 2025-11-28 16:17 | 2025-11-28 17:26 | 1:08 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | AZUBUIKE EMEH | Shagba Terkula | Emeh Azubike | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed Charging Alternator was Excited (No diesel outage after validation) | Failed Charging Alternator was Excited (No diesel outage after validation)
NOCINC0006484557 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0852A | T2715 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-30 04:35:26@T2715_Old Warri Road Ekiugbo | 2025-11-30 04:48 | System Administrator | 2025-11-30 04:35 | 2025-11-30 05:44 | 4096 | 2025-11-30 04:35 | 2025-11-30 05:44 | 1:08 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | HENRY OMELE |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | DG high temperature, Coolant top up was done
NOCINC0006485657 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0800A | T3057 | IBD | Ibadan | Oyo | 3 - Low | OY1106 | WEST |  | 2025-11-30 09:37 | Victor Otugo | 2025-11-30 09:36 | 2025-11-30 10:44 | 4092 | 2025-11-30 09:36 | 2025-11-30 10:44 | 1:08 | Biswal | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 6 | PPM was carried out site with IHSREF/25110413472536457057
NOCINC0006474498 | Internal Reconciliation | Site Down | P1 | IHS_OSU_0967A | OS4261 | IBD | Ibadan | Osun | 3 - Low | OS0966 | WEST |  | 2025-11-28 18:17 | Valentine Adinnu | 2025-11-28 18:10 | 2025-11-28 19:18 | 4091 | 2025-11-28 18:10 | 2025-11-28 19:18 | 1:08 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 2 / 2 | MTN NG, Airtel NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty lift pump was worked on | Faulty lift pump was worked on
NOCINC0006464589 | External Reconciliation | Site Down | P3 | IHS_EKI_0923B | EK4552 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-27 12:19 | Abisoye Olaleye | 2025-11-27 12:18 | 2025-11-27 13:26 | 4089 | 2025-11-27 12:18 | 2025-11-27 13:26 | 1:08 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Weak crank battery, external battery was used to start the GG
NOCINC0006440046 | External Reconciliation | Site Down | P1 | IHS_EDO_0891A | T3363 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 12:58 | Oluwatomisin Sogbesan | 2025-11-24 12:53 | 2025-11-24 14:01 | 4084 | 2025-11-24 12:53 | 2025-11-24 14:01 | 1:08 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed rectifier module was reset (No diesel outage after validation) | Failed rectifier module was reset
NOCINC0006461951 | External Reconciliation | Site Down | P1 | IHS_ANA_0790A | T4023 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 01:58 | Aderonke Olowojoba | 2025-11-27 01:54 | 2025-11-27 03:02 | 4080 | 2025-11-27 01:54 | 2025-11-27 03:02 | 1:08 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Over Speed | 1 / 1 | MTN NG |  | Appeal John |  |  | Erik Nwodo | Nwigbo Chijioke |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Engine over speed alarm was cleared (No diesel outage after validation)
NOCINC0006448458 | External Reconciliation | Site Down | P3 | IHS_EDO_0978A | ED2153 | IBD | Asaba | Edo | 3 - Low | ED0709 | SOUTH SOUTH |  | 2025-11-25 13:16 | Oluwatomisin Sogbesan | 2025-11-25 13:14 | 2025-11-25 14:22 | 4077 | 2025-11-25 13:14 | 2025-11-25 14:22 | 1:08 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 2 / 2 | MTN NG, Airtel NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 2 | Faulty temperature sensor switch was replaced(No diesel outage after validation) | Faulty temperature sensor switch was replaced(No diesel outage after validation)
NOCINC0006462974 | External Reconciliation | Site Down | P3 | IHS_DEL_1133A | DL0683 | ASB | Asaba | Delta | 3 - Low | DL1153 | SOUTH SOUTH |  | 2025-11-27 08:01 | Ezinne Ubachukwu | 2025-11-27 08:01 | 2025-11-27 09:09 | 4071 | 2025-11-27 08:01 | 2025-11-27 09:09 | 1:08 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Failed Charging Alternator was replaced(no diesel outage after validation)
NOCINC0006466014 | External Reconciliation | Site Down | P3 | IHS_DEL_1178A | DL0565 | ASB | Asaba | Delta | 3 - Low | DL1251 | SOUTH SOUTH |  | 2025-11-27 15:34 | Bukola Olabanji | 2025-11-27 15:32 | 2025-11-27 16:39 | 4049 | 2025-11-27 15:32 | 2025-11-27 16:39 | 1:07 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 2 / 2 | MTN NG, Airtel NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | RMS snag clearance was completed at site with ref (IHSREF/25112617540662791672 SARID0009062961)
NOCINC0006461708 | External Reconciliation | Site Down | P3 | IHS_ANA_1061A | AN4165 | ASB | Asaba | Anambra | 3 - Low | AN0863 | SOUTH EAST | CSL Fault@2025-11-27 00:25:35@AN4165_Ogboji Road Ekwulobia Aguluchuk | 2025-11-27 00:38 | System Administrator | 2025-11-27 00:26 | 2025-11-27 01:33 | 4044 | 2025-11-27 00:26 | 2025-11-27 01:33 | 1:07 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Harrison Igbinedion | Harrison Igbinedion | Harrison Igbinedion | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation) | Low DG frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006458231 | External Reconciliation | Site Down | P2 | IHS_OYO_1198H | OY2864 | IBD | Ibadan | Oyo | 3 - Low | OY0998 | WEST |  | 2025-11-26 14:25 | Ifechi Ugwueze | 2025-11-26 14:23 | 2025-11-26 15:31 | 4027 | 2025-11-26 14:23 | 2025-11-26 15:31 | 1:07 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Taiwo Abanikannda | Yusuf Gyang |  | Soye West | Ugwu Samuel Nnamdi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Low DG frequency, frequency was adjusted
NOCINC0006469924 | External Reconciliation | Site Down | P4 | IHS_DEL_0997A | DL0010 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 05:47 | Patrick Okoro | 2025-11-28 05:46 | 2025-11-28 06:53 | 4022 | 2025-11-28 05:46 | 2025-11-28 06:53 | 1:07 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed AVR was worked on | Failed AVR was worked on
NOCINC0006464472 | External Reconciliation | Site Down | P1 | IHS_OND_1003A | OD4702 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 12:11 | Iyesioluwa Ola | 2025-11-27 12:09 | 2025-11-27 13:16 | 4015 | 2025-11-27 12:09 | 2025-11-27 13:16 | 1:07 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Relay Faulty | 1 / 2 | MTN NG |  | Adetutu Adedipupo |  |  | Soye West | Goddey Nwokedigbo Peter |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty DG Relay Was Replaced
NOCINC0006445579 | External Reconciliation | Site Down | P3 | IHS_OYO_1038A | OY2974 | IBD | Ibadan | Oyo | 3 - Low | OY1112 | WEST |  | 2025-11-25 06:38 | Damilola Paseda | 2025-11-25 06:37 | 2025-11-25 07:44 | 4010 | 2025-11-25 06:37 | 2025-11-25 07:44 | 1:07 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Throttle Motor | 2 / 2 | MTN NG, Airtel NG |  | Azeez Salami |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Faulty throttle mixer was worked on
NOCINC0006444434 | External Reconciliation | Site Down | P4 | IHS_DEL_1212B | DL4085 | ASB | Asaba | Delta | 3 - Low | DL1034 | SOUTH SOUTH |  | 2025-11-24 22:41 | Quadri Ogundare | 2025-11-24 22:39 | 2025-11-24 23:46 | 3999 | 2025-11-24 22:39 | 2025-11-24 23:46 | 1:07 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Emergency Stop | 2 / 2 | MTN NG, Airtel NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Emergency stop alarm was cleared, DG powered manually | Emergency stop alarm was cleared, DG powered manually
NOCINC0006455014 | External Reconciliation | Site Down | P1 | IHS_ANA_0790A | T4023 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 05:01 | Abundance Otunola | 2025-11-26 04:54 | 2025-11-26 06:00 | 3998 | 2025-11-26 04:54 | 2025-11-26 06:00 | 1:07 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Sensor Switch | 1 / 1 | MTN NG |  | Appeal John |  |  | Erik Nwodo | Nwigbo Chijioke |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty oil switch was worked on. (No diesel outage after validation) | Faulty oil switch was worked on. (No diesel outage after validation)
NOCINC0006460758 | External Reconciliation | Site Down | P1 | IHS_BEN_0747E | ED6149 | IBD | Asaba | Edo | 3 - Low | ED0502 | SOUTH SOUTH |  | 2025-11-26 21:22 | Oluwatomisin Sogbesan | 2025-11-26 21:15 | 2025-11-26 22:21 | 3991 | 2025-11-26 21:15 | 2025-11-26 22:21 | 1:07 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | MTN NG |  | Ismail Adeyinka |  |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty load breaker was replaced (No diesel outage after validation)
NOCINC0006442065 | External Reconciliation | Site Down | P4 | IHS_EDO_1169H | ED2065 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 16:37 | Evelyn Emagurehor | 2025-11-24 16:35 | 2025-11-24 17:42 | 3977 | 2025-11-24 16:35 | 2025-11-24 17:42 | 1:06 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hooked injuector pump was worked on to restore power on site (No diesel outage after validation) | Hooked injuector pump was worked on to restore power on site (No diesel outage after validation)
NOCINC0006467742 | External Reconciliation | Site Down | P2 | IHS_KWA_0760A | T3127 | IBD | Ibadan | Kwara | 3 - Low | KW0651 | WEST | CSL Fault@2025-11-27 20:17:40@T3127_OrolodoArea | 2025-11-27 20:30 | System Administrator | 2025-11-27 20:18 | 2025-11-27 21:24 | 3973 | 2025-11-27 20:18 | 2025-11-27 21:24 | 1:06 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 2 | MTN NG |  | Enorch Dauda |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 5 | faulty hand primer was worked on
NOCINC0006451887 | External Reconciliation | Site Down | P2 | IHS_OSU_0908A | T3600 | IBD | Ibadan | Osun | 3 - Low | - | - | CSL Fault@2025-11-25 20:49:08@T3600_IfetedoAyesan | 2025-11-25 21:01 | System Administrator | 2025-11-25 20:49 | 2025-11-25 21:55 | 3961 | 2025-11-25 20:49 | 2025-11-25 21:55 | 1:06 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Olatunde Babatunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | faulty injector pump was worked on
NOCINC0006449475 | External Reconciliation | Site Down | P3 | IHS_OYO_1414B | - | - | Ibadan | Oyo | 3 - Low | OY1366 | WEST |  | 2025-11-25 15:18 | Precious Attah | 2025-11-25 15:10 | 2025-11-25 16:16 | 3960 | 2025-11-25 15:10 | 2025-11-25 16:16 | 1:06 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 1 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty lift pump was worked on
NOCINC0006470083 | External Reconciliation | Site Down | P4 | IHS_OSU_0976K | OY4078 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 06:18 | Ifechi Ugwueze | 2025-11-28 06:13 | 2025-11-28 07:19 | 3956 | 2025-11-28 06:13 | 2025-11-28 07:19 | 1:06 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Emergency Stop | 1 / 1 | MTN NG |  | Bayo Nathaniel |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Emergency stop alarm was cleared
NOCINC0006448727 | External Reconciliation | Site Down | P4 | IHS_DEL_1196B | DL4059 | ASB | Asaba | Delta | 3 - Low | DL1139 | SOUTH SOUTH |  | 2025-11-25 13:46 | Ezinne Ubachukwu | 2025-11-25 13:43 | 2025-11-25 14:49 | 3952 | 2025-11-25 13:43 | 2025-11-25 14:49 | 1:06 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 3 / 3 | MTN NG, Airtel NG, Smile |  | Gabriel Akhamiogu |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | High DG temperature, coolant was added (No diesel outage after validation) | High DG temperature, coolant was added (No diesel outage after validation)
NOCINC0006450835 | External Reconciliation | Site Down | P1 | IHS_OYO_1008A | OY2827 | IBD | Ibadan | Oyo | 3 - Low | OY1664 | WEST |  | 2025-11-25 18:33 | Mutmainnah Saba | 2025-11-25 18:32 | 2025-11-25 19:38 | 3950 | 2025-11-25 18:32 | 2025-11-25 19:38 | 1:06 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | SUNDAY MOSES |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Tripped Load Breaker Was Enabled
NOCINC0006487942 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1358B | OY1036 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 15:30 | Aishat Oyedeji | 2025-11-30 15:25 | 2025-11-30 16:30 | 3942 | 2025-11-30 15:25 | 2025-11-30 16:30 | 1:06 | SPS | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006485205 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0896A | T3828 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 08:05 | Osarieme Charles | 2025-11-30 08:03 | 2025-11-30 09:08 | 3931 | 2025-11-30 08:03 | 2025-11-30 09:08 | 1:06 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Burnt Load breaker was replaced
NOCINC0006483765 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1038A | AN0004 | ASB | Asaba | Anambra | 3 - Low | - | - | Cascaded Incident from TTO6770748 - Cascade Removed From TTO6770748 | 2025-11-29 23:25 | Uthman Akinola | 2025-11-29 23:23 | 2025-11-30 00:28 | 3924 | 2025-11-29 23:23 | 2025-11-30 00:28 | 1:05 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Obinna Clinton |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 2 | dg high temperature, coolant was added (no diesel outage after validation)
NOCINC0006461900 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-27 01:26 | Aderonke Olowojoba | 2025-11-27 01:21 | 2025-11-27 01:34 | 804 | 2025-11-27 00:29 | 2025-11-27 01:34 | 1:05 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation) | Low DG frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006462354 | External Reconciliation | Site Down | P4 | IHS_OSU_0026B | OS4289 | IBD | Ibadan | Osun | 3 - Low | OS0601 | WEST |  | 2025-11-27 05:16 | Precious Attah | 2025-11-27 05:10 | 2025-11-27 06:15 | 3918 | 2025-11-27 05:10 | 2025-11-27 06:15 | 1:05 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Flat DG battery. External generator battery was used to power site.
NOCINC0006484465 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0913A | OS2609 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 04:07 | Mutmainnah Saba | 2025-11-30 04:03 | 2025-11-30 05:09 | 3916 | 2025-11-30 04:03 | 2025-11-30 05:09 | 1:05 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | Bayo Nathaniel |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start
NOCINC0006483247 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1236B | ED5525 | IBD | Asaba | Edo | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-29 21:29:21@ | 2025-11-29 21:45 | System Administrator | 2025-11-29 21:30 | 2025-11-29 22:35 | 3914 | 2025-11-29 21:30 | 2025-11-29 22:35 | 1:05 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty Rectifier module was replaced
NOCINC0006484045 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1400H | AN0419 | ASB | Asaba | Anambra | 3 - Low | AN1085 | SOUTH EAST | 4G Site Down@2025-11-30 00:51:16@AN1085_L | 2025-11-30 01:10 | System Administrator | 2025-11-30 00:51 | 2025-11-30 01:56 | 3914 | 2025-11-30 00:51 | 2025-11-30 01:56 | 1:05 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | Airtel NG, MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low DG frequency, governor was adjusted (No diesel outage after validation). | Low DG frequency, governor was adjusted (No diesel outage after validation).
NOCINC0006466154 | External Reconciliation | Site Down | P3 | IHS_OSU_0865A | T3680 | IBD | Ibadan | Osun | 3 - Low | OS0949 | WEST | Huawei 3G SiteDown@2025-11-27 15:35:59@U3680 | 2025-11-27 15:53 | System Administrator | 2025-11-27 15:47 | 2025-11-27 16:52 | 3912 | 2025-11-27 15:47 | 2025-11-27 16:52 | 1:05 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006461253 | External Reconciliation | Site Down | P4 | IHS_OND_0998A | OD4708 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 23:01 | Yewande Adeagbo | 2025-11-26 23:01 | 2025-11-27 00:06 | 3901 | 2025-11-26 23:01 | 2025-11-27 00:06 | 1:05 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start
NOCINC0006445121 | External Reconciliation | Site Down | P4 | IHS_OSU_0873A | T3665 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 03:02 | Valentine Adinnu | 2025-11-25 02:53 | 2025-11-25 03:58 | 3870 | 2025-11-25 02:53 | 2025-11-25 03:58 | 1:04 | IPT | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 1 / 1 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to incomplete phase from Grid. DG was powered manually | Grid to DG synchronization failure due to incomplete phase from Grid. DG was powered manually
NOCINC0006480028 | Internal Reconciliation | Site Down | P1 | IHS_OND_0829A | T3950 | IBD | Ibadan | Ondo | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-29 13:08:41@T3950_AkinwunmiPlotA | 2025-11-29 13:24 | System Administrator | 2025-11-29 13:15 | 2025-11-29 14:19 | 3867 | 2025-11-29 13:15 | 2025-11-29 14:19 | 1:04 | IPT | Equipment Repair | Passive | Rectifier | Rectifier - Phase Controller | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty Rectifier Backplane Worked On
NOCINC0006470499 | External Reconciliation | Site Down | P3 | IHS_KWA_0885A | KW2318 | IBD | Ibadan | Kwara | 3 - Low | KW0525 | WEST |  | 2025-11-28 08:16 | Okusanya Joseph | 2025-11-28 08:15 | 2025-11-28 09:19 | 3860 | 2025-11-28 08:15 | 2025-11-28 09:19 | 1:04 | IPT | Fuel Outage (Probable) | Passive | Diesel | Fuel Line Issue | 2 / 2 | MTN NG, Airtel NG |  | Olapade Babatunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Blocked fuel line was flushed
NOCINC0006457394 | External Reconciliation | Site Down | P2 | IHS_EKI_0777A | T3717 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-26 12:20 | Tunji Adejumo | 2025-11-26 12:19 | 2025-11-26 13:24 | 3852 | 2025-11-26 12:19 | 2025-11-26 13:24 | 1:04 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Over Voltage | 1 / 1 | MTN NG |  | Yohanna Sabo |  |  | Ibrahim Akinpelu | Yohanna Sabo |  | Collins Edike | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | DG over voltage alarm cleared
NOCINC0006452357 | External Reconciliation | Site Down | P3 | IHS_EKI_0005B | EK2239 | IBD | Ibadan | Ekiti | 3 - Low | EK0430 | WEST |  | 2025-11-25 22:46 | Ihuoma Opurum | 2025-11-25 22:46 | 2025-11-25 23:50 | 3845 | 2025-11-25 22:46 | 2025-11-25 23:50 | 1:04 | Huawei | Fuel Outage (Probable) | Passive | Diesel | Fuel Line Issue | 2 / 2 | MTN NG, Airtel NG |  | Oluwafemi Oluwasegun |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Fuel leakage due to burst fuel hose. Hose was replaced.
NOCINC0006478374 | Internal Reconciliation | Site Down | P3 | IHS_OYO_0841A | T3071 | IBD | Ibadan | Oyo | 3 - Low | - | - | gNodeB Out of Service@2025-11-29 09:36:20@N3071 | 2025-11-29 09:50 | System Administrator | 2025-11-29 09:36 | 2025-11-29 10:40 | 3845 | 2025-11-29 09:36 | 2025-11-29 10:40 | 1:04 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting update from FSE
NOCINC0006468114 | External Reconciliation | Site Down | P3 | IHS_ANA_1182A | AN0734 | ASB | Asaba | Anambra | 3 - Low | AN0860 | SOUTH EAST |  | 2025-11-27 21:41 | Oluwatoyin Fagite | 2025-11-27 21:39 | 2025-11-27 22:43 | 3844 | 2025-11-27 21:39 | 2025-11-27 22:43 | 1:04 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator Leakage | 2 / 2 | Airtel NG, MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Radiator hose leakage was worked on (No diesel outage after validation) | Radiator hose leakage was worked on (No diesel outage after validation)
NOCINC0006478332 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-29 09:45 | Quadri Ogundare | 2025-11-29 09:44 | 2025-11-29 10:48 | 3838 | 2025-11-29 09:44 | 2025-11-29 10:48 | 1:04 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006454955 | External Reconciliation | Site Down | P4 | IHS_ONT_0083B | AN0905 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-26 04:37:45@AN0905_Adazi Nnukwu | 2025-11-26 04:50 | System Administrator | 2025-11-26 04:38 | 2025-11-26 05:42 | 3829 | 2025-11-26 04:38 | 2025-11-26 05:42 | 1:04 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Ezimeruwe ANTHONY |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Tripped Load Breaker was enabled. (No diesel outage after validation) | Tripped Load Breaker was enabled. (No diesel outage after validation)
NOCINC0006476248 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1090A | AN0336 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 22:52 | Akachukwu Ugwu | 2025-11-28 22:44 | 2025-11-28 23:48 | 3827 | 2025-11-28 22:44 | 2025-11-28 23:48 | 1:04 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting update from FSE
NOCINC0006465576 | External Reconciliation | Site Down | P4 | IHS_OYO_1329B | OY1043 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 14:37 | Mutmainnah Saba | 2025-11-27 14:34 | 2025-11-27 15:38 | 3827 | 2025-11-27 14:34 | 2025-11-27 15:38 | 1:04 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to lost of communication, DG was powered manually
NOCINC0006437239 | External Reconciliation | Site Down | P1 | IHS_WAR_0031B | DL0588 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 01:20 | Bukola Olabanji | 2025-11-24 01:20 | 2025-11-24 02:24 | 3824 | 2025-11-24 01:20 | 2025-11-24 02:24 | 1:04 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Failed charging alternator was excited (no diesel outage after validation).
NOCINC0006467014 | External Reconciliation | Site Down | P2 | IHS_WAR_0042B | DL0624 | ASB | Asaba | Delta | 3 - Low | DL0809 | SOUTH SOUTH |  | 2025-11-27 18:15 | Bukola Olabanji | 2025-11-27 18:12 | 2025-11-27 19:16 | 3818 | 2025-11-27 18:12 | 2025-11-27 19:16 | 1:04 | BJ Bison NGA | Equipment Repair | Passive | Control Panel | ATS Relay Faulty | 2 / 2 | MTN NG, Airtel NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty ATS relay was replaced (No diesel outage after validation)
NOCINC0006473061 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1444B | - | - | Ibadan | Oyo | 3 - Low | OY1564 | WEST |  | 2025-11-28 14:53 | Oluwatomisin Ogunleye | 2025-11-28 14:46 | 2025-11-28 15:50 | 3816 | 2025-11-28 14:46 | 2025-11-28 15:50 | 1:04 | Inhouse | Equipment Repair | Passive | Hybrid | Site Down - Low Voltage | 1 / 1 | Airtel NG |  | Effiong Asukwo |  |  |  | Effiong Asukwo |  | Victor Olanrewaju | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen SMU, SMU was reset | Hybrid synchronization failure due to frozen SMU, SMU was reset
NOCINC0006462924 | External Reconciliation | Site Down | P1 | IHS_OSU_0927A | OS2702 | IBD | Ibadan | Osun | 3 - Low | OS0733 | WEST | Cascaded Incident from TTO6747457 - Cascade Removed From TTO6747457 | 2025-11-27 07:45 | Hardy Oko | 2025-11-27 07:39 | 2025-11-27 08:43 | 3810 | 2025-11-27 07:39 | 2025-11-27 08:43 | 1:04 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Zechariah Akinbulejo | Opeyemi Ajibola | Opeyemi Ajibola | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 3 | faulty load breaker was replaced
NOCINC0006439638 | External Reconciliation | Site Down | P1 | IHS_IBA_0099C | OY4157 | IBD | Ibadan | Oyo | 3 - Low | OY1034 | WEST |  | 2025-11-24 11:50 | Victor Otugo | 2025-11-24 11:49 | 2025-11-24 12:52 | 3800 | 2025-11-24 11:49 | 2025-11-24 12:52 | 1:03 | SPS | Fuel Outage | Passive | Diesel | Diesel Outage | 2 / 2 | MTN NG, Airtel NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Diesel outage, diesel was added. | Diesel outage, diesel was added.
NOCINC0006468463 | External Reconciliation | Site Down | P1 | IHS_OYO_0879A | T3545 | IBD | Ibadan | Oyo | 3 - Low | OY0996 | WEST | Cascaded Incident from TTO6753670 - Cascade Removed From TTO6753670 | 2025-11-27 22:37 | Ifechi Ugwueze | 2025-11-27 22:33 | 2025-11-27 23:36 | 3797 | 2025-11-27 22:33 | 2025-11-27 23:36 | 1:03 | SPS | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Grid-DG synchronization failure due to unstable grid supply issue. DG was powered manually.
NOCINC0006460580 | External Reconciliation | Site Down | P2 | IHS_EDO_1112C | ED6199 | IBD | Asaba | Edo | 3 - Low | ED0995 | SOUTH SOUTH |  | 2025-11-26 20:53 | Tracy Osarumwense | 2025-11-26 20:53 | 2025-11-26 21:56 | 3790 | 2025-11-26 20:53 | 2025-11-26 21:56 | 1:03 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Failed Fuel Pump was replaced. | Failed Fuel Pump was replaced. (No diesel outage after validation).
NOCINC0006452306 | External Reconciliation | Site Down | P3 | IHS_EKI_0804A | T3777 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-25 22:35 | Testimony Akinyemi | 2025-11-25 22:30 | 2025-11-25 23:34 | 3840 | 2025-11-25 22:31 | 2025-11-25 23:34 | 1:03 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Over Voltage | 1 / 1 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify | 1 | DG over voltage alarm was cleared
NOCINC0006489136 | Internal Reconciliation | Site Down | P1 | IHS_WAR_0869H | DL0348 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 18:51 | Tracy Osarumwense | 2025-11-30 18:49 | 2025-11-30 19:52 | 3779 | 2025-11-30 18:49 | 2025-11-30 19:52 | 1:03 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006437561 | External Reconciliation | Site Down | P2 | IHS_EDO_0913A | T3350 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 03:09 | Muhammed Hashirudeen | 2025-11-24 03:06 | 2025-11-24 04:09 | 3777 | 2025-11-24 03:06 | 2025-11-24 04:09 | 1:03 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006479890 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0704E | OS4659 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-29 13:07 | Damilola Paseda | 2025-11-29 13:02 | 2025-11-29 14:05 | 3776 | 2025-11-29 13:02 | 2025-11-29 14:05 | 1:03 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on | Faulty ATS contactor was worked on
NOCINC0006443097 | External Reconciliation | Site Down | P3 | IHS_ILO_0027B | KW4596 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 18:54 | Precious Attah | 2025-11-24 18:52 | 2025-11-24 19:55 | 3776 | 2025-11-24 18:52 | 2025-11-24 19:55 | 1:03 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Loose DG battery terminal was tightened.
NOCINC0006445509 | External Reconciliation | Site Down | P3 | IHS_EDO_1321B | - | - | Asaba | Edo | 3 - Low | ED0833 | SOUTH SOUTH |  | 2025-11-25 06:09 | Azeezat Badmus | 2025-11-25 06:08 | 2025-11-25 07:11 | 3770 | 2025-11-25 06:08 | 2025-11-25 07:11 | 1:03 | MPI NGA | Equipment Repair | Passive | Infrastructure | Armoured Cable | 1 / 1 | Airtel NG |  | Asukwo Effiong | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Burnt DC cable was replaced (No diesel outage after validation)
NOCINC0006470370 | External Reconciliation | Site Down | P1 | IHS_ANA_1072A | AN0304 | ASB | Asaba | Anambra | 3 - Low | AN0717 | SOUTH EAST |  | 2025-11-28 07:48 | Oluwatoyin Fagite | 2025-11-28 07:45 | 2025-11-28 08:47 | 3764 | 2025-11-28 07:45 | 2025-11-28 08:47 | 1:03 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Failed charging alternator was excited(No diesel outage after validation) | Failed charging alternator was excited(No diesel outage after validation)
NOCINC0006476406 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0017B | DL0487 | ASB | Asaba | Delta | 3 - Low | DL0618 | SOUTH SOUTH |  | 2025-11-28 23:44 | Mary Odefemi | 2025-11-28 23:43 | 2025-11-29 00:46 | 3763 | 2025-11-28 23:43 | 2025-11-29 00:46 | 1:03 | BJ Bison NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Emuesiri� Sunday |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure, DG was powered manually
NOCINC0006454819 | External Reconciliation | Site Down | P2 | IHS_OSU_0898A | T3798 | IBD | Ibadan | Osun | 3 - Low | OS0672 | WEST |  | 2025-11-26 03:19 | Osarieme Charles | 2025-11-26 03:16 | 2025-11-26 04:19 | 3756 | 2025-11-26 03:16 | 2025-11-26 04:19 | 1:03 | IPT | Equipment Repair | Passive | Hybrid | Hybrid Module | 1 / 2 | MTN NG |  | Odufu Friday |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Hybrid synchronisation failure due to weak BUB, site was powered manually
NOCINC0006455112 | External Reconciliation | Site Down | P4 | IHS_DEL_1142A | DL0762 | ASB | Asaba | Delta | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-26 05:22:33@DL0762_Jephers Plot Uruabe Quaters | 2025-11-26 05:35 | System Administrator | 2025-11-26 05:30 | 2025-11-26 06:33 | 3750 | 2025-11-26 05:30 | 2025-11-26 06:33 | 1:03 | Tyllium NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on. (No diesel outage after validation) | Faulty injector pump was worked on. (No diesel outage after validation)
NOCINC0006451148 | External Reconciliation | Site Down | P3 | IHS_ANA_1005A | T4856 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 19:21 | Patrick Okoro | 2025-11-25 19:21 | 2025-11-25 20:20 | 3570 | 2025-11-25 19:18 | 2025-11-25 20:20 | 1:03 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Over Frequency | 1 / 1 | MTN NG |  | Emmanuel Emmanuel | Henry Ubawuchi | Henry Ubawuchi | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | DG over frequency, governor was adjusted. (No diesel outage after validation) | DG over frequency, governor was adjusted. (No diesel outage after validation)
NOCINC0006444109 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-24 21:44 | Quadri Ogundare | 2025-11-24 21:42 | 2025-11-24 22:44 | 3748 | 2025-11-24 21:42 | 2025-11-24 22:44 | 1:02 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low gen frequency, governor was adjusted (No diesel outage after validation) | Low gen frequency, governor was adjusted (No diesel outage after validation)
NOCINC0006465979 | External Reconciliation | Site Down | P2 | IHS_OSU_0990C | OS4351 | IBD | Ibadan | Osun | 3 - Low | OS0774 | WEST | Cascaded Incident from TTO6750853 - Cascade Removed From TTO6750853 | 2025-11-27 15:31 | Sheriff Salami | 2025-11-27 15:27 | 2025-11-27 16:30 | 3744 | 2025-11-27 15:27 | 2025-11-27 16:30 | 1:02 | IPT | Fuel Outage (Probable) | Passive | DCDG Gen | DCDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Zechariah Akinbulejo | Opeyemi Ajibola | Opeyemi Ajibola | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | faulty injector pump was worked on
NOCINC0006476840 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0781A | T0104 | IBD | Ibadan | Oyo | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-29 02:48:59@ | 2025-11-29 03:06 | System Administrator | 2025-11-29 02:54 | 2025-11-29 03:57 | 3738 | 2025-11-29 02:54 | 2025-11-29 03:57 | 1:02 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Samuel Olaobaju | Yusuf Gyang |  | Abiola Adegbiji | Habeeb Adepoju |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Weak crank battery was temporarily replaced
NOCINC0006476885 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1309B | OY4472 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 03:31 | Bosede Kutelu | 2025-11-29 03:28 | 2025-11-29 03:58 | 1830 | 2025-11-29 02:54 | 2025-11-29 03:57 | 1:02 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG Under Voltage was Cleared and AVR was Adjusted.
NOCINC0006465863 | External Reconciliation | Site Down | P2 | IHS_KWA_0814A | T3178 | IBD | Ibadan | Kwara | 3 - Low | KW0454 | WEST |  | 2025-11-27 15:19 | Titus Tosin | 2025-11-27 15:19 | 2025-11-27 16:21 | 3737 | 2025-11-27 15:19 | 2025-11-27 16:21 | 1:02 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 2 / 2 | Airtel NG, MTN NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | faulty lift pump was worked on
NOCINC0006448009 | External Reconciliation | Site Down | P3 | IHS_ANA_1122A | AN0659 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 12:18 | Oluwatoyin Fagite | 2025-11-25 12:15 | 2025-11-25 13:17 | 3731 | 2025-11-25 12:15 | 2025-11-25 13:17 | 1:02 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 1 / 1 | MTN NG |  | Ukanwa Reginald | Ukanwa Karachi | Ukanwa Karachi | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | faulty rectifier cabinet was replaced (No diesel outage after validation) | faulty rectifier cabinet was replaced (No diesel outage after validation)
NOCINC0006475142 | Internal Reconciliation | Site Down | P3 | IHS_OND_0020B | OD2555 | IBD | Ibadan | Ondo | 3 - Low | ON0519 | WEST |  | 2025-11-28 19:59 | Testimony Akinyemi | 2025-11-28 19:57 | 2025-11-28 20:59 | 3716 | 2025-11-28 19:57 | 2025-11-28 20:59 | 1:02 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Low oil pressure Alarm was cleared
NOCINC0006461148 | External Reconciliation | Site Down | P3 | IHS_OND_1044B | OD6249 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 22:36 | Oluwadara Bankole | 2025-11-26 22:33 | 2025-11-26 23:34 | 3710 | 2025-11-26 22:33 | 2025-11-26 23:34 | 1:02 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Injection Pump Calibration | 1 / 1 | MTN NG |  | Obuseh Williams |  |  | Ibrahim Akinpelu | Obuseh Williams |  | Lukman Amusat | Ibrahim Yekini | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty injection pump was serviced. | Faulty injection pump was serviced.
NOCINC0006442850 | External Reconciliation | Site Down | P3 | IHS_OYO_1017A | OY2801 | IBD | Ibadan | Oyo | 3 - Low | OY1142 | WEST |  | 2025-11-24 18:16 | Aishat Oyedeji | 2025-11-24 18:16 | 2025-11-24 19:17 | 3708 | 2025-11-24 18:16 | 2025-11-24 19:17 | 1:02 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Aramide Kazeem |  | Aramide Kazeem | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty AVR was swapped | Faulty AVR was swapped
NOCINC0006460291 | External Reconciliation | Site Down | P3 | IHS_OYO_0940A | T3628 | IBD | Ibadan | Osun | 3 - Low | OS0731 | WEST |  | 2025-11-26 20:10 | Sheriff Salami | 2025-11-26 20:07 | 2025-11-26 21:09 | 3708 | 2025-11-26 20:07 | 2025-11-26 21:09 | 1:02 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Zechariah Akinbulejo | Opeyemi Ajibola | Opeyemi Ajibola | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | failed charging alternator was excited
NOCINC0006444559 | External Reconciliation | Site Down | P1 | IHS_OYO_1037A | OY2967 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 23:18 | Damilola Paseda | 2025-11-24 23:18 | 2025-11-25 00:19 | 3696 | 2025-11-24 23:18 | 2025-11-25 00:19 | 1:02 | SPS | Equipment Repair | Passive | Infrastructure | Armoured Cable | 1 / 3 | MTN NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 3 | Burnt Amoured Cable was re-terminated | Burnt Amoured Cable was re-terminated
NOCINC0006474170 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0042B | OS4285 | IBD | Ibadan | Osun | 3 - Low | OS0738 | WEST |  | 2025-11-28 17:32 | Okusanya Joseph | 2025-11-28 17:31 | 2025-11-28 18:07 | 2205 | 2025-11-28 17:31 | 2025-11-28 18:32 | 1:02 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Control Panel | 2 / 2 | Airtel NG, MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty DG control panel was worked on
NOCINC0006469823 | External Reconciliation | Site Down | P4 | IHS_OYO_1292B | OY6454 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 05:15 | Marvellous Emecheta | 2025-11-28 05:11 | 2025-11-28 06:13 | 3695 | 2025-11-28 05:11 | 2025-11-28 06:13 | 1:02 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Fan Belt Issue | 1 / 1 | MTN NG |  | Lukman Mohammed | Habeeb Adepoju |  | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | slacked fan belt was adjusted
NOCINC0006452007 | External Reconciliation | Site Down | P4 | IHS_OYO_1058A | OY2762 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 21:23 | Aishat Oyedeji | 2025-11-25 21:20 | 2025-11-25 22:21 | 3679 | 2025-11-25 21:20 | 2025-11-25 22:21 | 1:01 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Emeh Henry |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | failed charging alternator was excited
NOCINC0006462106 | External Reconciliation | Site Down | P1 | IHS_OYO_0032B | OY4293 | IBD | Ibadan | Oyo | 3 - Low | OY1022 | WEST |  | 2025-11-27 03:27 | Victor Otugo | 2025-11-27 03:26 | 2025-11-27 04:27 | 3675 | 2025-11-27 03:26 | 2025-11-27 04:27 | 1:01 | SPS | Equipment Repair | Passive | Hybrid | E-Site Comm Failure | 2 / 2 | MTN NG, Airtel NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Hybrid synchronization failure due to loss of communication, DG was powered manually
NOCINC0006485181 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1447B | - | - | Ibadan | Oyo | 3 - Low | OY1565 | WEST |  | 2025-11-30 07:59 | Mutmainnah Saba | 2025-11-30 07:57 | 2025-11-30 08:58 | 3663 | 2025-11-30 07:57 | 2025-11-30 08:58 | 1:01 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 1 / 1 | Airtel NG |  | Mohammed Soliu |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Low Oil Pressure Alarm was Cleared
NOCINC0006463932 | External Reconciliation | Site Down | P4 | IHS_OSU_0875A | OS3995 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 11:04 | Okusanya Joseph | 2025-11-27 11:04 | 2025-11-27 12:05 | 3663 | 2025-11-27 11:04 | 2025-11-27 12:05 | 1:01 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 1 / 1 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty thermostat was worked on
NOCINC0006460331 | External Reconciliation | Site Down | P2 | IHS_OSU_0929A | OS2725 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 20:20 | Victor Otugo | 2025-11-26 20:13 | 2025-11-26 21:14 | 3657 | 2025-11-26 20:13 | 2025-11-26 21:14 | 1:01 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | DG lost compression, engine was swapped
NOCINC0006443429 | External Reconciliation | Site Down | P1 | IHS_OSU_0027B | OS4293 | IBD | Ibadan | Osun | 3 - Low | OS0640 | WEST |  | 2025-11-24 19:52 | Azeezat Adekunle | 2025-11-24 19:50 | 2025-11-24 20:50 | 3630 | 2025-11-24 19:50 | 2025-11-24 20:50 | 1:01 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 2 / 2 | Airtel NG, MTN NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty KICK-STARTER was worked on
NOCINC0006469724 | External Reconciliation | Site Down | P3 | IHS_EDO_0718E | - | - | Asaba | Edo | 3 - Low | ED0748 | SOUTH SOUTH |  | 2025-11-28 04:15 | Emmanuel Faleti | 2025-11-28 04:14 | 2025-11-28 05:14 | 3624 | 2025-11-28 04:14 | 2025-11-28 05:14 | 1:00 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | Airtel NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start. (No diesel outage after validation) | Weak DG was primed to start. (No diesel outage after validation)
NOCINC0006454718 | External Reconciliation | Site Down | P2 | IHS_DEL_1106A | DL0750 | ASB | Asaba | Delta | 3 - Low | DL0758 | SOUTH SOUTH |  | 2025-11-26 02:22 | Ayomide Akindolie | 2025-11-26 02:20 | 2025-11-26 03:20 | 3620 | 2025-11-26 02:20 | 2025-11-26 03:20 | 1:00 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | HENRY OMELE | Henry Ikede | Henry Ikede | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006476808 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1336B | OY1044 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 02:45 | Bosede Kutelu | 2025-11-29 02:44 | 2025-11-29 03:44 | 3619 | 2025-11-29 02:44 | 2025-11-29 03:44 | 1:00 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG high temperature due to low coolant level. Radiator was flushed and coolant was added.
NOCINC0006462937 | External Reconciliation | Site Down | P3 | IHS_OND_0994A | OD4828 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 07:48 | Yewande Adeagbo | 2025-11-27 07:47 | 2025-11-27 08:47 | 3619 | 2025-11-27 07:47 | 2025-11-27 08:47 | 1:00 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Oluwaseun Awolope |  |  | Ibrahim Akinpelu | Oluwaseun Awolope |  | John Momoh | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen smu, frozen SMU was reset
NOCINC0006489591 | Internal Reconciliation | Site Down | P3 | IHS_EDO_1010A | ED4907 | IBD | Asaba | Edo | 3 - Low | ED1131 | South South |  | 2025-11-30 20:36 | Azeezat Badmus | 2025-11-30 20:36 | 2025-11-30 21:18 | 2535 | 2025-11-30 20:18 | 2025-11-30 21:18 | 1:00 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Module | 2 / 2 | Airtel NG, MTN NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 4 | Hybrid synchronization failure due to Failed to start alarm was cleared and DG powered manually (No diesel outage after validation)
NOCINC0006458077 | External Reconciliation | Site Down | P1 | IHS_SAP_0008B | DL0851 | ASB | Asaba | Delta | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-26 13:48:37@DL0851_2 | 2025-11-26 14:05 | System Administrator | 2025-11-26 13:52 | 2025-11-26 14:52 | 3614 | 2025-11-26 13:52 | 2025-11-26 14:52 | 1:00 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG Under Frequency, Governor was adjusted. | DG Under Frequency, Governor was adjusted. (No diesel outage after validation).
NOCINC0006477809 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1051A | DL0091 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 08:16 | Ayokunle Samuel | 2025-11-29 08:16 | 2025-11-29 09:16 | 3597 | 2025-11-29 08:16 | 2025-11-29 09:16 | 1:00 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Failed rectifier module was reset. (No diesel outage after validation) | Failed rectifier module was reset. (No diesel outage after validation)
NOCINC0006456832 | External Reconciliation | Site Down | P2 | IHS_IBA_0014V | OY4050 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 11:13 | Ifechi Ugwueze | 2025-11-26 11:12 | 2025-11-26 12:12 | 3597 | 2025-11-26 11:12 | 2025-11-26 12:12 | 1:00 | SPS | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | BASHIR ABDULRASAQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on
NOCINC0006484157 | Internal Reconciliation | Site Down | P1 | IHS_OSU_0790A | T3038 | IBD | Ibadan | Osun | 3 - Low | OS0657 | WEST |  | 2025-11-30 02:04 | Osarieme Charles | 2025-11-30 01:56 | 2025-11-30 02:55 | 3596 | 2025-11-30 01:56 | 2025-11-30 02:55 | 1:00 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Fuse | 1 / 2 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 7 | Cut F2 fuse was replaced
NOCINC0006462663 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-27 06:43 | Aderonke Olowojoba | 2025-11-27 06:37 | 2025-11-27 07:37 | 3592 | 2025-11-27 06:37 | 2025-11-27 07:37 | 1:00 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | failed charging alternator was excited (No diesel outage after validations) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006461608 | External Reconciliation | Site Down | P4 | IHS_ANA_1229A | AN0565 | ASB | Asaba | Anambra | 3 - Low | - | - | NodeB Unavailable@2025-11-26 23:56:58@UAN0565 | 2025-11-27 00:12 | System Administrator | 2025-11-27 00:06 | 2025-11-27 00:17 | 641 | 2025-11-27 00:06 | 2025-11-27 01:06 | 1:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006443795 | External Reconciliation | Site Down | P2 | IHS_OYO_0850A | T3536 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 20:56 | Damilola Paseda | 2025-11-24 20:54 | 2025-11-24 21:54 | 3578 | 2025-11-24 20:54 | 2025-11-24 21:54 | 1:00 | IPT | Fuel Outage (Probable) | Passive | Diesel | Diesel Top-Up | 1 / 1 | MTN NG |  | Olalekan Saheed | Adewale Adejumo | Adewale Adejumo | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Low diesel level, diesel was topped up | Low diesel level, diesel was topped up
NOCINC0006474365 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0877A | T3661 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 17:59 | Valentine Adinnu | 2025-11-28 17:56 | 2025-11-28 18:56 | 3565 | 2025-11-28 17:56 | 2025-11-28 18:56 | 0:59 | IPT | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on | Faulty ATS contactor was worked on
NOCINC0006453935 | External Reconciliation | Site Down | P4 | IHS_DEL_1142A | DL0762 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 00:54 | Ayokunle Samuel | 2025-11-26 00:54 | 2025-11-26 01:53 | 3504 | 2025-11-26 00:53 | 2025-11-26 01:53 | 0:59 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed charging alternator was worked on. (No diesel outage after validation) | Failed charging alternator was worked on. (No diesel outage after validation)
NOCINC0006466969 | External Reconciliation | Site Down | P1 | IHS_ANA_1220A | AN0567 | ASB | Asaba | Anambra | 3 - Low | AN0594 | SOUTH EAST |  | 2025-11-27 18:06 | Akachukwu Ugwu | 2025-11-27 18:03 | 2025-11-27 19:03 | 3561 | 2025-11-27 18:03 | 2025-11-27 19:03 | 0:59 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Ugochuku Agbamuche | Ugo Agamuche | Ugo Agamuche | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on (No diesel outage after validation) | Faulty injector pump was worked on (No diesel outage after validation)
NOCINC0006469637 | External Reconciliation | Site Down | P3 | IHS_IBA_0728E | OY2930 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 03:40 | Tunji Adejumo | 2025-11-28 03:27 | 2025-11-28 04:21 | 3261 | 2025-11-28 03:27 | 2025-11-28 04:26 | 0:59 | SPS | Grid Supply | Passive | Grid | National Grid - Low Current Supply | 1 / 1 | Smile |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid low supply, DG was powered manually
NOCINC0006477287 | Internal Reconciliation | Site Down | P4 | IHS_DEL_0942A | T2916 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 05:54 | Femi Olanipekun | 2025-11-29 05:54 | 2025-11-29 06:53 | 3560 | 2025-11-29 05:54 | 2025-11-29 06:53 | 0:59 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG under frequency, Governor was adjusted. (No diesel outage after validation). | DG under frequency, Governor was adjusted. (No diesel outage after validation).
NOCINC0006471687 | Internal Reconciliation | Site Down | P2 | IHS_IBA_0003B | OY4356 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 11:18 | Zainab Bello | 2025-11-28 11:01 | 2025-11-28 12:00 | 3559 | 2025-11-28 11:01 | 2025-11-28 12:00 | 0:59 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Emergency Stop | 1 / 1 | INQ |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Emergency Stop Alarm was cleared
NOCINC0006482645 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0973A | T3358 | IBD | Asaba | Edo | 3 - Low | ED0496 | SOUTH SOUTH |  | 2025-11-29 20:08 | Evelyn Emagurehor | 2025-11-29 20:07 | 2025-11-29 21:06 | 3559 | 2025-11-29 20:07 | 2025-11-29 21:06 | 0:59 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Sensor Switch | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty oil switch was replaced (No diesel outage after validation)
NOCINC0006462992 | External Reconciliation | Site Down | P1 | IHS_OSU_0027B | OS4293 | IBD | Ibadan | Osun | 3 - Low | OS0640 | WEST |  | 2025-11-27 08:05 | Precious Attah | 2025-11-27 08:03 | 2025-11-27 09:02 | 3559 | 2025-11-27 08:03 | 2025-11-27 09:02 | 0:59 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 2 / 2 | Airtel NG, MTN NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty KICK-STARTER was worked on
NOCINC0006456644 | External Reconciliation | Site Down | P2 | IHS_ILO_0065C | KW4737 | IBD | Ibadan | Kwara | 3 - Low | KW0486 | WEST |  | 2025-11-26 10:38 | Titus Tosin | 2025-11-26 10:38 | 2025-11-26 11:37 | 3554 | 2025-11-26 10:38 | 2025-11-26 11:37 | 0:59 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Fan Belt | 2 / 2 | MTN NG, Airtel NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Cut fan belt was replaced
NOCINC0006468420 | External Reconciliation | Site Down | P1 | IHS_OSU_0781A | T3091 | IBD | Ibadan | Osun | 3 - Low | OS0661 | WEST | Huawei 2G SiteDown@2025-11-27 22:16:34@T3091_SaratVenturesLtd | 2025-11-27 22:31 | System Administrator | 2025-11-27 22:20 | 2025-11-27 23:19 | 3554 | 2025-11-27 22:20 | 2025-11-27 23:19 | 0:59 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006445175 | External Reconciliation | Site Down | P3 | IHS_WAR_0053B | DL0581 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 03:27 | Quadri Ogundare | 2025-11-25 03:25 | 2025-11-25 04:24 | 3550 | 2025-11-25 03:25 | 2025-11-25 04:24 | 0:59 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 2 | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006463818 | External Reconciliation | Site Down | P4 | IHS_WAR_0951B | DL3357 | ASB | Asaba | Delta | 3 - Low | DL1186 | SOUTH SOUTH | CSL Fault@2025-11-27 10:31:19@DL3357_DL3357_Ukwomugwa_Road | 2025-11-27 10:44 | System Administrator | 2025-11-27 10:35 | 2025-11-27 11:34 | 3548 | 2025-11-27 10:35 | 2025-11-27 11:34 | 0:59 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start
NOCINC0006481241 | Internal Reconciliation | Site Down | P3 | IHS_OND_0076C | OD4969 | IBD | Ibadan | Osun | 3 - Low | ON0668 | WEST |  | 2025-11-29 16:09 | Maureen Uchehorke | 2025-11-29 16:09 | 2025-11-29 17:07 | 3482 | 2025-11-29 16:08 | 2025-11-29 17:07 | 0:59 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 2 / 2 | Airtel NG, MTN NG |  | Olatunde Babatunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty temperature sensor switch was worked on
NOCINC0006451435 | External Reconciliation | Site Down | P4 | IHS_ANA_0810A | T4056 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 20:14 | Patrick Okoro | 2025-11-25 20:06 | 2025-11-25 21:05 | 3540 | 2025-11-25 20:06 | 2025-11-25 21:05 | 0:59 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Amadi Fabian | Tijani Haruna | Tijani Haruna | Henry Wanogho | Ifeanyi Chukusa |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector nozzle was serviced. (No diesel outage after validation) | Faulty injector nozzle was serviced. (No diesel outage after validation)
NOCINC0006445590 | External Reconciliation | Site Down | P4 | IHS_WAR_0727C | DL0990 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 06:42 | Quadri Ogundare | 2025-11-25 06:41 | 2025-11-25 07:40 | 3537 | 2025-11-25 06:41 | 2025-11-25 07:40 | 0:59 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on (No diesel outage after validation) | Faulty injector pump was worked on (No diesel outage after validation)
NOCINC0006476621 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0910H | EK4407 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 01:10 | Iyesioluwa Ola | 2025-11-29 01:07 | 2025-11-29 02:06 | 3536 | 2025-11-29 01:07 | 2025-11-29 02:06 | 0:59 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Ajao Oyekunle |  |  | Soye West | Ugwu Samuel Nnamdi |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | weak DG battery. external battery was used to power DG
NOCINC0006475243 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1141A | DL0630 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 20:16 | Mary Odefemi | 2025-11-28 20:11 | 2025-11-28 21:09 | 3534 | 2025-11-28 20:11 | 2025-11-28 21:09 | 0:59 | BJ Bison NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure, DG was powered manually
NOCINC0006488361 | Internal Reconciliation | Site Down | P4 | IHS_DEL_0997A | DL0010 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 16:38 | Ayokunle Samuel | 2025-11-30 16:31 | 2025-11-30 17:30 | 3532 | 2025-11-30 16:31 | 2025-11-30 17:30 | 0:59 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty AVR was excited. (No diesel outage after validation) | Faulty AVR was excited. (No diesel outage after validation)
NOCINC0006451127 | External Reconciliation | Site Down | P3 | IHS_OND_0039B | OD4837 | IBD | Ibadan | Ondo | 3 - Low | ON0692 | WEST |  | 2025-11-25 19:14 | Mary Elaigwu | 2025-11-25 19:12 | 2025-11-25 20:11 | 3530 | 2025-11-25 19:12 | 2025-11-25 20:11 | 0:59 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | Airtel NG, MTN NG |  | Olatunde Babatunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | faulty DG radiator was worked on
NOCINC0006458441 | External Reconciliation | Site Down | P3 | IHS_EDO_1317B | - | - | Asaba | Edo | 3 - Low | ED0844 | SOUTH SOUTH |  | 2025-11-26 14:59 | Emmanuel Faleti | 2025-11-26 14:58 | 2025-11-26 15:57 | 3527 | 2025-11-26 14:58 | 2025-11-26 15:57 | 0:59 | MPI NGA | Fuel Outage (Probable) | Passive | Diesel | Diesel Top-Up | 1 / 1 | Airtel NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Low diesel pressure, diesel was topped | Low diesel pressure, diesel was topped
NOCINC0006445005 | External Reconciliation | Site Down | P2 | IHS_ANA_1381H | - | - | Asaba | Anambra | 3 - Low | AN0429 | SOUTH EAST |  | 2025-11-25 02:15 | Solomon Bankole | 2025-11-25 02:14 | 2025-11-25 03:13 | 3526 | 2025-11-25 02:14 | 2025-11-25 03:13 | 0:59 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Air Intake | 2 / 2 | Airtel NG, Smile |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Air Lock in fuel line was cleared ( No diesel outage after validation) | Air Lock in fuel line was cleared ( No diesel outage after validation)
NOCINC0006489584 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1246B | ED5521 | IBD | Asaba | Edo | 3 - Low | ED1124 | SOUTH SOUTH |  | 2025-11-30 20:35 | Quadri Ogundare | 2025-11-30 20:23 | 2025-11-30 21:22 | 3524 | 2025-11-30 20:23 | 2025-11-30 21:22 | 0:59 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset (No diesel outage after validation) | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006443098 | External Reconciliation | Site Down | P4 | IHS_OYO_1011A | T3599 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 18:54 | Victor Otugo | 2025-11-24 18:52 | 2025-11-24 19:51 | 3524 | 2025-11-24 18:52 | 2025-11-24 19:51 | 0:59 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Azeez Salami |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Low voltage alarm was cleared from the control module | Low voltage alarm was cleared from the control module
NOCINC0006445004 | External Reconciliation | Site Down | P4 | IHS_OND_0956A | OD2520 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-25 02:14 | Maureen Uchehorke | 2025-11-25 02:11 | 2025-11-25 03:10 | 3522 | 2025-11-25 02:11 | 2025-11-25 03:10 | 0:59 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Oluwaseun Awolope |  |  | Ibrahim Akinpelu | Oluwaseun Awolope |  | John Momoh | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure, frozen smu was reset
NOCINC0006483355 | Internal Reconciliation | Site Down | P1 | IHS_WAR_0907H | DL0003 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-29 21:50:21@DL0003_Opposite Abraka MarketAsaba AS | 2025-11-29 22:03 | System Administrator | 2025-11-29 21:50 | 2025-11-29 22:53 | 3730 | 2025-11-29 21:54 | 2025-11-29 22:53 | 0:59 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty rectifier module was replaced (No diesel outage after validation) | Faulty rectifier module was replaced (No diesel outage after validation)
NOCINC0006473255 | Internal Reconciliation | Site Down | P3 | IHS_IBA_0009B | OY2916 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 15:22 | Damilola Paseda | 2025-11-28 15:21 | 2025-11-28 16:20 | 3517 | 2025-11-28 15:21 | 2025-11-28 16:20 | 0:59 | SPS | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 1 / 1 | MTN NG |  | SUNDAY MOSES |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty IPT rectifier Orion was bypassed | Faulty IPT rectifier Orion was bypassed
NOCINC0006469605 | External Reconciliation | Site Down | P1 | IHS_OSU_0801A | T3087 | IBD | Ibadan | Osun | 3 - Low | OS0765 | WEST |  | 2025-11-28 03:19 | Mary Elaigwu | 2025-11-28 03:18 | 2025-11-28 04:17 | 3514 | 2025-11-28 03:18 | 2025-11-28 04:17 | 0:59 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | MTN NG, Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 8 | National grid incomplete phase, DG powered manually
NOCINC0006461373 | External Reconciliation | Site Down | P2 | IHS_KWA_0893A | KW4593 | IBD | Ibadan | Kwara | 3 - Low | KW0434 | WEST |  | 2025-11-26 23:29 | Precious Attah | 2025-11-26 23:28 | 2025-11-27 00:27 | 3513 | 2025-11-26 23:28 | 2025-11-27 00:27 | 0:59 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty DG breaker was replaced
NOCINC0006444344 | External Reconciliation | Site Down | P2 | IHS_OYO_0774A | T0090 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 22:25 | Damilola Paseda | 2025-11-24 22:23 | 2025-11-24 23:22 | 3503 | 2025-11-24 22:23 | 2025-11-24 23:22 | 0:58 | SPS | Fuel Outage (Probable) | Passive | Diesel | Water Separator Blockage | 2 / 3 | MTN NG, Smile |  | BASHIR ABDULRASAQ | Yusuf Gyang |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Water ingress, water was separated from diesel | Water ingress, water was separated from diesel
NOCINC0006454779 | External Reconciliation | Site Down | P1 | IHS_DEL_0906A | T2725 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 03:01 | Ayokunle Samuel | 2025-11-26 03:01 | 2025-11-26 03:59 | 3486 | 2025-11-26 03:01 | 2025-11-26 03:59 | 0:58 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 12 | Failed charging alternator was worked on. (No diesel outage after validation). | Failed charging alternator was worked on. (No diesel outage after validation).
NOCINC0006450935 | External Reconciliation | Site Down | P1 | IHS_EDO_0935A | ED2001 | IBD | Asaba | Edo | 3 - Low | ED0656 | SOUTH SOUTH |  | 2025-11-25 18:51 | Oluwatomisin Sogbesan | 2025-11-25 18:48 | 2025-11-25 19:46 | 3479 | 2025-11-25 18:48 | 2025-11-25 19:46 | 0:58 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG high temperature due to faulty radiator was worked on (No diesel outage after validation) | DG high temperature due to faulty radiator was worked on
NOCINC0006445523 | External Reconciliation | Site Down | P4 | IHS_ILO_0708E | KW4718 | IBD | Ibadan | Kwara | 3 - Low | KW0688 | West |  | 2025-11-25 06:12 | Praise Okezie | 2025-11-25 06:10 | 2025-11-25 07:08 | 3474 | 2025-11-25 06:10 | 2025-11-25 07:08 | 0:58 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG under voltage alarm cleared
NOCINC0006453124 | External Reconciliation | Site Down | P4 | IHS_OSU_0888A | T3830 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 00:41 | Aishat Oyedeji | 2025-11-26 00:41 | 2025-11-26 01:39 | 3473 | 2025-11-26 00:41 | 2025-11-26 01:39 | 0:58 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Charging Alternator | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | failed charging alternator was excited
NOCINC0006440653 | External Reconciliation | Site Down | P1 | IHS_OYO_0908A | T3862 | IBD | Ibadan | Oyo | 3 - Low | OY0975 | WEST |  | 2025-11-24 13:52 | Hardy Oko | 2025-11-24 13:49 | 2025-11-24 14:47 | 3470 | 2025-11-24 13:49 | 2025-11-24 14:47 | 0:58 | Inhouse | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty injection pump was worked on.
NOCINC0006446201 | External Reconciliation | Site Down | P1 | IHS_EDO_0840A | T3291 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 09:06 | Emmanuel Faleti | 2025-11-25 09:05 | 2025-11-25 10:03 | 3468 | 2025-11-25 09:05 | 2025-11-25 10:03 | 0:58 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Failed charging alternator was excited pending replacement (No diesel outage after validation) | Failed charging alternator was excited pending replacement (No diesel outage after validation)
NOCINC0006449252 | External Reconciliation | Site Down | P4 | IHS_EDO_1169H | ED2065 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 14:48 | Emmanuel Faleti | 2025-11-25 14:47 | 2025-11-25 15:45 | 3466 | 2025-11-25 14:47 | 2025-11-25 15:45 | 0:58 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | High temperature due to low level in the ACDG – Radiator. Water and coolant added and Gen power to restore the site. (No diesel outage after validation) | High temperature due to low level in the ACDG – Radiator. Water and coolant added and Gen power to restore the site. (No diesel outage after validation)
NOCINC0006452510 | External Reconciliation | Site Down | P1 | IHS_KWA_0774A | T3128 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 22:55 | Ihuoma Opurum | 2025-11-25 22:54 | 2025-11-25 23:52 | 3466 | 2025-11-25 22:54 | 2025-11-25 23:52 | 0:58 | IPT | Grid Supply | Passive | Grid | National Grid - Low Current Supply | 1 / 1 | MTN NG |  | Enorch Dauda |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Grid-DG synchronization failure due to low current supply. DG was powered manually.
NOCINC0006443088 | External Reconciliation | Site Down | P1 | IHS_KWA_0759A | T3136 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 18:52 | Precious Attah | 2025-11-24 18:51 | 2025-11-24 19:49 | 3459 | 2025-11-24 18:51 | 2025-11-24 19:49 | 0:58 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Faulty injector pump was worked on
NOCINC0006449299 | External Reconciliation | Site Down | P4 | IHS_ANA_1332B | AN3183 | ASB | Asaba | Anambra | 3 - Low | AN1013 | SOUTH EAST |  | 2025-11-25 14:53 | Ezinne Ubachukwu | 2025-11-25 14:49 | 2025-11-25 15:47 | 3453 | 2025-11-25 14:49 | 2025-11-25 15:47 | 0:58 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | failed charging alternator was excited
NOCINC0006442682 | External Reconciliation | Site Down | P4 | IHS_WAR_0776C | DL0650 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 17:58 | Ayomide Akindolie | 2025-11-24 17:56 | 2025-11-24 18:53 | 3453 | 2025-11-24 17:56 | 2025-11-24 18:53 | 0:58 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 1 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Name: Joshua bulus Company: GAIOsystems Purpose: RMS REINSTALLATION Date :24/11/2025 Site Id:IHS_WAR_0776C IHSREF/25112316371215456233 SARID0009010799 | Name: Joshua bulus Company: GAIOsystems Purpose: RMS REINSTALLATION Date :24/11/2025 Site Id:IHS_WAR_0776C IHSREF/25112316371215456233 SARID0009010799
NOCINC0006462315 | External Reconciliation | Site Down | P1 | IHS_DEL_0811A | T2654 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 05:04 | Ezinne Ubachukwu | 2025-11-27 05:01 | 2025-11-27 05:58 | 3443 | 2025-11-27 05:01 | 2025-11-27 05:58 | 0:57 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 1 / 1 | MTN NG |  | Dare Oguyemi | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 9 | faulty water pump was worked (No diesel outage after validation) | faulty water pump was worked (No diesel outage after validation)
NOCINC0006438240 | External Reconciliation | Site Down | P3 | IHS_OSU_0110C | OS4664 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 07:20 | Okusanya Joseph | 2025-11-24 07:19 | 2025-11-24 08:16 | 3443 | 2025-11-24 07:19 | 2025-11-24 08:16 | 0:57 | IPT | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out
NOCINC0006455397 | External Reconciliation | Site Down | P1 | IHS_KWA_0815A | T3188 | IBD | Ibadan | Kwara | 3 - Low | KW0544 | WEST |  | 2025-11-26 06:52 | Ihuoma Opurum | 2025-11-26 06:51 | 2025-11-26 07:48 | 3439 | 2025-11-26 06:51 | 2025-11-26 07:48 | 0:57 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Enorch Dauda |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG loss compression. Weak DG was primed to start.
NOCINC0006462614 | External Reconciliation | Site Down | P3 | IHS_ANA_0955A | T4810 | ASB | Asaba | Anambra | 3 - Low | IM0871 | SOUTH EAST |  | 2025-11-27 06:26 | Aderonke Olowojoba | 2025-11-27 06:22 | 2025-11-27 07:19 | 3438 | 2025-11-27 06:22 | 2025-11-27 07:19 | 0:57 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Madu Modestus | Madu Modestus | Madu Modestus | Fady Safwat | Aliyu Garuba |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | DG High Temperature due to low Coolant level, Coolant was added. | DG High Temperature due to low Coolant level, Coolant was added. No diesel outage after validation).
NOCINC0006471214 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0082B | OS4410 | IBD | Ibadan | Osun | 3 - Low | OS0914 | WEST |  | 2025-11-28 10:12 | Oluwatomisin Ogunleye | 2025-11-28 10:11 | 2025-11-28 11:08 | 3429 | 2025-11-28 10:11 | 2025-11-28 11:08 | 0:57 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty lift pump was worked on
NOCINC0006485562 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0726E | ED6177 | IBD | Asaba | Edo | 3 - Low | ED0473 | SOUTH SOUTH |  | 2025-11-30 09:20 | Evelyn Emagurehor | 2025-11-30 09:20 | 2025-11-30 10:17 | 3422 | 2025-11-30 09:20 | 2025-11-30 10:17 | 0:57 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 3 / 3 | Airtel NG, MTN NG, Smile |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Hybrid to Gen synchronization failure due to bursted ACDG - Generator Battery. An external battery was used to power the Gen manually to restore power to the site. (No diesel outage after validation). | Hybrid to Gen synchronization failure due to bursted ACDG - Generator Battery. An external battery was used to power the Gen manually to restore power to the site. (No diesel outage after validation).
NOCINC0006464588 | External Reconciliation | Site Down | P4 | IHS_ANA_0890A | T4159 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 12:19 | Gbemisola Adedeji | 2025-11-27 12:16 | 2025-11-27 13:12 | 3415 | 2025-11-27 12:16 | 2025-11-27 13:12 | 0:57 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Augustine Okoro | Ademola Adekunle | Ademola Adekunle | Henry Wanogho | Ifeanyi Chukusa |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006469584 | External Reconciliation | Site Down | P4 | IHS_KWA_1018B | KW6462 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 03:07 | Osarieme Charles | 2025-11-28 03:05 | 2025-11-28 04:02 | 3403 | 2025-11-28 03:05 | 2025-11-28 04:02 | 0:57 | IPT | Fuel Outage (Probable) | Passive | DCDG Gen | DCDG - Fuel Pump | 1 / 1 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty Fuel pump was worked on
NOCINC0006462395 | External Reconciliation | Site Down | P2 | IHS_OKP_0004B | AN0326 | ASB | Asaba | Anambra | 3 - Low | AN0404 | SOUTH EAST |  | 2025-11-27 05:31 | Aderonke Olowojoba | 2025-11-27 05:19 | 2025-11-27 06:16 | 3402 | 2025-11-27 05:19 | 2025-11-27 06:16 | 0:57 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 2 | Failed charging alternator was excited (No diesel outage after validation).
NOCINC0006480178 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1141A | DL0630 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 13:44 | Ayomide Akindolie | 2025-11-29 13:42 | 2025-11-29 14:38 | 3399 | 2025-11-29 13:42 | 2025-11-29 14:38 | 0:57 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected passive, awaiting update
NOCINC0006445489 | External Reconciliation | Site Down | P2 | IHS_OSU_0061B | OS4254 | IBD | Ibadan | Osun | 3 - Low | OS0698 | WEST |  | 2025-11-25 06:03 | Damilola Paseda | 2025-11-25 06:01 | 2025-11-25 06:58 | 3391 | 2025-11-25 06:01 | 2025-11-25 06:58 | 0:57 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty hand primer was worked on | Faulty hand primer was worked on
NOCINC0006455670 | External Reconciliation | Site Down | P3 | IHS_WAR_0017B | DL0487 | ASB | Asaba | Delta | 3 - Low | DL0618 | SOUTH SOUTH |  | 2025-11-26 07:27 | Ayomide Akindolie | 2025-11-26 07:27 | 2025-11-26 08:24 | 3386 | 2025-11-26 07:27 | 2025-11-26 08:24 | 0:56 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 2 / 2 | Airtel NG, MTN NG |  | Emuesiri� Sunday |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty lift pump was worked on (No diesel outage after validation) | (No diesel outage after validation)
NOCINC0006488948 | Internal Reconciliation | Site Down | P2 | IHS_OND_1000A | OD4809 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 18:11 | Yewande Adeagbo | 2025-11-30 18:09 | 2025-11-30 19:05 | 3374 | 2025-11-30 18:09 | 2025-11-30 19:05 | 0:56 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Benjamin Onwu |  |  | Ibrahim Akinpelu | Benjamin Onwu |  | Victor Adeoye | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Hybrid synchronization failure due to frozen SMU was reset.
NOCINC0006473905 | Internal Reconciliation | Site Down | P2 | IHS_IBA_0038V | OY4028 | IBD | Ibadan | Oyo | 3 - Low | OY0161 | WEST |  | 2025-11-28 16:52 | Damilola Paseda | 2025-11-28 16:44 | 2025-11-28 17:40 | 3364 | 2025-11-28 16:44 | 2025-11-28 17:40 | 0:56 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 2 | Airtel NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Low water level in radiator, water was added.
NOCINC0006471392 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0737E | OS4701 | IBD | Ibadan | Osun | 3 - Low | OS0739 | WEST |  | 2025-11-28 10:37 | Praise Okezie | 2025-11-28 10:36 | 2025-11-28 11:32 | 3362 | 2025-11-28 10:36 | 2025-11-28 11:32 | 0:56 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | John Olasupo |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Generator servicing (ppm) was carried out at site with IHSREF/25112412172642126137
NOCINC0006470649 | Internal Reconciliation | Site Down | P2 | IHS_OND_0838A | T3930 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 08:50 | Testimony Akinyemi | 2025-11-28 08:49 | 2025-11-28 09:45 | 3360 | 2025-11-28 08:49 | 2025-11-28 09:45 | 0:56 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 3 | low voltage... Voltage Settings was adjusted
NOCINC0006447813 | External Reconciliation | Site Down | P1 | IHS_DEL_0835A | T2664 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 11:53 | Tracy Osarumwense | 2025-11-25 11:51 | 2025-11-25 12:47 | 3355 | 2025-11-25 11:51 | 2025-11-25 12:47 | 0:56 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | DG High Temperature due to low Coolant level, Coolant was added. | DG High Temperature due to low Coolant level, Coolant was added. (No diesel outage after validation).
NOCINC0006462062 | External Reconciliation | Site Down | P4 | IHS_OND_0033B | OD2599 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 02:59 | Oluwadara Bankole | 2025-11-27 02:56 | 2025-11-27 03:51 | 3353 | 2025-11-27 02:56 | 2025-11-27 03:51 | 0:56 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG Primed To Start
NOCINC0006471495 | Internal Reconciliation | Site Down | P3 | IHS_OYO_0925A | T3872 | IBD | Ibadan | Oyo | 3 - Low | OY1270 | WEST |  | 2025-11-28 10:45 | Praise Okezie | 2025-11-28 10:44 | 2025-11-28 11:40 | 3352 | 2025-11-28 10:44 | 2025-11-28 11:40 | 0:56 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Fatunwase Samuel |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Faulty refurbished DG generation with injector pump issue. Mixing Oil with diesel site ,Cut over was done to old DG
NOCINC0006483723 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0922A | T3550 | IBD | Ibadan | Oyo | 3 - Low | OY0712 | WEST |  | 2025-11-29 23:20 | Mutmainnah Saba | 2025-11-29 23:19 | 2025-11-30 00:14 | 3346 | 2025-11-29 23:19 | 2025-11-30 00:14 | 0:56 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | low oil pressure, oil was added
NOCINC0006466762 | External Reconciliation | Site Down | P3 | IHS_OSU_0110C | OS4664 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 17:31 | Titus Tosin | 2025-11-27 17:31 | 2025-11-27 18:26 | 3346 | 2025-11-27 17:31 | 2025-11-27 18:26 | 0:56 | IPT | Fuel Outage (Probable) | Passive | Diesel | Diesel Top-Up | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Low diesel pressure, diesel was topped
NOCINC0006455474 | External Reconciliation | Site Down | P2 | IHS_OND_0783A | T3423 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 07:02 | Ihuoma Opurum | 2025-11-26 07:01 | 2025-11-26 07:57 | 3343 | 2025-11-26 07:01 | 2025-11-26 07:57 | 0:56 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Start failure alarm was cleared
NOCINC0006467074 | External Reconciliation | Site Down | P1 | IHS_OND_0973A | OD4740 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 18:28 | Iyesioluwa Ola | 2025-11-27 18:28 | 2025-11-27 19:24 | 3343 | 2025-11-27 18:28 | 2025-11-27 19:24 | 0:56 | IPT | Grid Supply | Passive | Grid | National Grid - Low Current Supply | 2 / 2 | MTN NG, Airtel NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid-DG synchronisation failure due to low current, DG powered manually
NOCINC0006475149 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0042B | DL0624 | ASB | Asaba | Delta | 3 - Low | DL0809 | SOUTH SOUTH |  | 2025-11-28 20:00 | Bukola Olabanji | 2025-11-28 19:59 | 2025-11-28 20:55 | 3337 | 2025-11-28 19:59 | 2025-11-28 20:55 | 0:56 | BJ Bison NGA | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | Airtel NG, MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Fauty ATS contactor was bypassed (No diesel outage after validation)
NOCINC0006438039 | External Reconciliation | Site Down | P1 | IHS_BEN_0002B | ED4852 | IBD | Asaba | Edo | 3 - Low | ED0873 | SOUTH SOUTH |  | 2025-11-24 06:15 | Muhammed Hashirudeen | 2025-11-24 06:09 | 2025-11-24 07:04 | 3337 | 2025-11-24 06:09 | 2025-11-24 07:04 | 0:56 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 2 / 2 | Airtel NG, MTN NG |  | SIMON SUNDAY | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty water pump was worked on (No diesel outage after validation)
NOCINC0006461137 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH | NodeB Unavailable@2025-11-26 22:19:06@UED6221 | 2025-11-26 22:33 | System Administrator | 2025-11-26 22:24 | 2025-11-26 23:19 | 3330 | 2025-11-26 22:24 | 2025-11-26 23:19 | 0:56 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty Injector pump was worked on (No diesel outage after validation) | Faulty Injector pump was worked on (No diesel outage after validation)
NOCINC0006443009 | External Reconciliation | Site Down | P4 | IHS_EDO_1255B | ED5539 | IBD | Asaba | Edo | 3 - Low | ED1140 | SOUTH SOUTH |  | 2025-11-24 18:35 | Oluwatomisin Sogbesan | 2025-11-24 18:31 | 2025-11-24 19:27 | 3328 | 2025-11-24 18:31 | 2025-11-24 19:27 | 0:55 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Emergency Stop | 2 / 2 | MTN NG, Airtel NG |  | Kazeem Ajiboye |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty emergency stop button was bypassed to restore the site. (No diesel outage after validation). | Faulty emergency stop button was bypassed to restore the site. (No diesel outage after validation).
NOCINC0006482883 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0004B | ED2095 | IBD | Asaba | Edo | 3 - Low | ED0967 | SOUTH SOUTH |  | 2025-11-29 20:54 | Muhammed Hashirudeen | 2025-11-29 20:54 | 2025-11-29 21:49 | 3325 | 2025-11-29 20:54 | 2025-11-29 21:49 | 0:55 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Hammed Abubakar |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Tripped load breaker was enabled (No diesel outage after validation)
NOCINC0006445447 | External Reconciliation | Site Down | P1 | IHS_OSU_0801A | T3087 | IBD | Ibadan | Osun | 3 - Low | OS0765 | WEST |  | 2025-11-25 05:51 | Valentine Adinnu | 2025-11-25 05:49 | 2025-11-25 06:44 | 3323 | 2025-11-25 05:49 | 2025-11-25 06:44 | 0:55 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 8 | Grid-DG synchronization failure due to unstable grid supply, DG was powered manually | Grid-DG synchronization failure due to unstable grid supply, DG was powered manually
NOCINC0006464328 | External Reconciliation | Site Down | P3 | IHS_OSU_0073B | OS4386 | IBD | Ibadan | Osun | 3 - Low | OS0712 | WEST |  | 2025-11-27 11:47 | Okusanya Joseph | 2025-11-27 11:45 | 2025-11-27 12:40 | 3322 | 2025-11-27 11:45 | 2025-11-27 12:40 | 0:55 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on
NOCINC0006487660 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0969A | T3006 | IBD | Ibadan | Oyo | 3 - Low | OY1057 | WEST |  | 2025-11-30 14:52 | Aishat Oyedeji | 2025-11-30 14:52 | 2025-11-30 15:47 | 3315 | 2025-11-30 14:52 | 2025-11-30 15:47 | 0:55 | SPS | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 4 | Faulty injector pump was worked on | Faulty injector pump was worked on
NOCINC0006484935 | Internal Reconciliation | Site Down | P4 | IHS_OND_0858A | T3836 | IBD | Ibadan | Ondo | 3 - Low | - | - | Cascaded Incident from TTO6772049 - Cascade Removed From TTO6772049 | 2025-11-30 06:52 | Abisoye Olaleye | 2025-11-30 06:46 | 2025-11-30 07:41 | 3315 | 2025-11-30 06:46 | 2025-11-30 07:41 | 0:55 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Oluwaseun Awolope |  |  | Ibrahim Akinpelu | Oluwaseun Awolope |  | John Momoh | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to failed csu, csu was reset
NOCINC0006465523 | External Reconciliation | Site Down | P2 | IHS_OSU_1025H | OS2687 | IBD | Ibadan | Osun | 3 - Low | OS0778 | WEST |  | 2025-11-27 14:27 | Mutmainnah Saba | 2025-11-27 14:25 | 2025-11-27 15:20 | 3315 | 2025-11-27 14:25 | 2025-11-27 15:20 | 0:55 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006455564 | External Reconciliation | Site Down | P4 | IHS_KWA_0808A | T3199 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-26 07:05 | Azeezat Adekunle | 2025-11-26 07:05 | 2025-11-26 08:00 | 3311 | 2025-11-26 07:05 | 2025-11-26 08:00 | 0:55 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Afolabi Ganiyyu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to DG failed to start alarm was cleared and DG was Powered manually
NOCINC0006476465 | Internal Reconciliation | Site Down | P3 | IHS_ILO_0018B | KW4616 | IBD | Ibadan | Kwara | 3 - Low | KW0471 | WEST |  | 2025-11-29 00:12 | Titus Tosin | 2025-11-29 00:08 | 2025-11-29 01:03 | 3304 | 2025-11-29 00:08 | 2025-11-29 01:03 | 0:55 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 2 / 2 | MTN NG, Airtel NG |  | Olapade Babatunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty temperature sensor switch was worked on
NOCINC0006489874 | Internal Reconciliation | Site Down | P4 | IHS_ANA_0993A | T4879 | ASB | Asaba | Anambra | 3 - Low | AN1008 | SOUTH EAST |  | 2025-11-30 21:33 | Solomon Bankole | 2025-11-30 21:32 | 2025-11-30 22:27 | 3302 | 2025-11-30 21:32 | 2025-11-30 22:27 | 0:55 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 1 | Airtel NG |  | Esan Enoch |  |  | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted ( No diesel outage after validation) | Low DG frequency, Governor was adjusted ( No diesel outage after validation)
NOCINC0006447783 | External Reconciliation | Site Down | P3 | IHS_OSU_0731E | OS4656 | IBD | Ibadan | Osun | 3 - Low | OS0646 | WEST |  | 2025-11-25 11:48 | Hardy Oko | 2025-11-25 11:46 | 2025-11-25 12:41 | 3301 | 2025-11-25 11:46 | 2025-11-25 12:41 | 0:55 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | High DG engine temperature,coolant was added
NOCINC0006485229 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0780A | T3153 | IBD | Ibadan | Kwara | 3 - Low | KW0086 | WEST |  | 2025-11-30 08:14 | Precious Attah | 2025-11-30 08:13 | 2025-11-30 09:08 | 3301 | 2025-11-30 08:13 | 2025-11-30 09:08 | 0:55 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 2 | MTN NG |  | Afolabi Ganiyyu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out
NOCINC0006446017 | External Reconciliation | Site Down | P3 | IHS_OSU_0983C | OS4720 | IBD | Ibadan | Osun | 3 - Low | OS0748 | WEST |  | 2025-11-25 08:37 | Mutmainnah Saba | 2025-11-25 08:35 | 2025-11-25 09:30 | 3297 | 2025-11-25 08:35 | 2025-11-25 09:30 | 0:55 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG Underfrequency, frequency was adjusted
NOCINC0006461242 | External Reconciliation | Site Down | P2 | IHS_OSU_0908A | T3600 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 23:00 | Hardy Oko | 2025-11-26 22:57 | 2025-11-26 23:52 | 3293 | 2025-11-26 22:57 | 2025-11-26 23:52 | 0:55 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | Olatunde Babatunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Dg under voltage alarm was cleared
NOCINC0006488692 | Internal Reconciliation | Site Down | P2 | IHS_OND_0061B | OD4825 | IBD | Ibadan | Ondo | 3 - Low | ON0777 | WEST |  | 2025-11-30 17:29 | Ihuoma Opurum | 2025-11-30 17:28 | 2025-11-30 18:23 | 3289 | 2025-11-30 17:28 | 2025-11-30 18:23 | 0:55 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | MTN NG, Airtel NG |  | Sanusi Idowu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Rectifier controller failure due to faulty control module. Control module was isolated.
NOCINC0006482546 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1022A | T4859 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 19:46 | Kehinde Akinbowale | 2025-11-29 19:43 | 2025-11-29 20:38 | 3284 | 2025-11-29 19:43 | 2025-11-29 20:38 | 0:55 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Henry Ikede | Ayeni Banabas | Ayeni Banabas | Henry Wanogho | Ifeanyi Chukusa |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006472020 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0810A | T3002 | IBD | Ibadan | Oyo | 3 - Low | OY1028 | WEST |  | 2025-11-28 12:05 | Mutmainnah Saba | 2025-11-28 12:04 | 2025-11-28 12:58 | 3275 | 2025-11-28 12:04 | 2025-11-28 12:58 | 0:55 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Mosunmola Christopher |  |  | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Failed charging alternator was excited | Failed charging alternator was excited
NOCINC0006451348 | External Reconciliation | Site Down | P3 | IHS_OSU_0731E | OS4656 | IBD | Ibadan | Osun | 3 - Low | OS0646 | WEST |  | 2025-11-25 20:06 | Marvellous Emecheta | 2025-11-25 20:05 | 2025-11-25 21:00 | 3270 | 2025-11-25 20:05 | 2025-11-25 21:00 | 0:54 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG-Grid synchronisation failure due to unstable grid supply, Dg powered manually
NOCINC0006460748 | External Reconciliation | Site Down | P3 | IHS_OSU_0110C | OS4664 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 21:20 | Precious Attah | 2025-11-26 21:19 | 2025-11-26 22:13 | 3269 | 2025-11-26 21:19 | 2025-11-26 22:13 | 0:54 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006489830 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0827A | KW3987 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-30 21:24 | Praise Okezie | 2025-11-30 21:23 | 2025-11-30 22:17 | 3264 | 2025-11-30 21:23 | 2025-11-30 22:17 | 0:54 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Bello Saheed |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 9 | Hybrid Synchronization failure due to Low voltage, DG was power manually
NOCINC0006484919 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0091C | OS4340 | IBD | Ibadan | Osun | 3 - Low | OS0710 | WEST |  | 2025-11-30 06:51 | Okusanya Joseph | 2025-11-30 06:51 | 2025-11-30 07:45 | 3264 | 2025-11-30 06:51 | 2025-11-30 07:45 | 0:54 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Grid-DG Synchronization Failure due to unstable grid supply, DG was powered manually | Grid-DG Synchronization Failure due to unstable grid supply, DG was powered manually
NOCINC0006468383 | External Reconciliation | Site Down | P2 | IHS_BEN_0705E | ED2049 | IBD | Asaba | Edo | 3 - Low | ED0474 | SOUTH SOUTH |  | 2025-11-27 22:23 | Emmanuel Faleti | 2025-11-27 22:23 | 2025-11-27 23:17 | 3260 | 2025-11-27 22:23 | 2025-11-27 23:17 | 0:54 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 7 | Faulty injector pump was worked on. (No diesel outage after validation) | Faulty injector pump was worked on. (No diesel outage after validation)
NOCINC0006489309 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0939A | ED2014 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 19:29 | Oluwatomisin Sogbesan | 2025-11-30 19:29 | 2025-11-30 20:23 | 3260 | 2025-11-30 19:29 | 2025-11-30 20:23 | 0:54 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | MTN NG |  | Christopher Aiyenale |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Tripped load breaker was worked on (No diesel outage after validation)
NOCINC0006485778 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1061A | DL0305 | ASB | Asaba | Delta | 3 - Low | DL0743 | SOUTH SOUTH |  | 2025-11-30 10:01 | Ezinne Ubachukwu | 2025-11-30 09:58 | 2025-11-30 10:48 | 3050 | 2025-11-30 09:54 | 2025-11-30 10:48 | 0:54 | Tyllium NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty injector pump was worked on. (No diesel outage after validation) | Faulty injector pump was worked on. (No diesel outage after validation)
NOCINC0006487683 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1034A | OY2980 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 14:54 | Precious Attah | 2025-11-30 14:53 | 2025-11-30 15:48 | 3255 | 2025-11-30 14:53 | 2025-11-30 15:48 | 0:54 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 3 | Suspected passive Issue on site, Awaiting update from FSE
NOCINC0006482759 | Internal Reconciliation | Site Down | P4 | IHS_BEN_0032V | ED5182 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 20:32 | Muhammed Hashirudeen | 2025-11-29 20:29 | 2025-11-29 21:24 | 3253 | 2025-11-29 20:29 | 2025-11-29 21:24 | 0:54 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | SAMUEL ASUKWO |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Tripped load breaker was reset
NOCINC0006489098 | Internal Reconciliation | Site Down | P1 | IHS_ONT_0053B | AN0526 | ASB | Asaba | Anambra | 3 - Low | AN0423 | SOUTH EAST |  | 2025-11-30 18:43 | Ezinne Ubachukwu | 2025-11-30 18:41 | 2025-11-30 19:35 | 3252 | 2025-11-30 18:41 | 2025-11-30 19:35 | 0:54 | BJ Bison NGA | Equipment Repair | Passive | Control Panel | AC Breaker Tripped | 2 / 2 | MTN NG, Airtel NG |  | Kingsley Obele | Kingsley Obele | Kingsley Obele | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Tripped Breaker enabled (No diesel outage after validation) | Tripped Breaker enabled (No diesel outage after validation)
NOCINC0006470232 | External Reconciliation | Site Down | P1 | IHS_DEL_0899A | T2748 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 07:05 | Oluwatobiloba Are | 2025-11-28 07:03 | 2025-11-28 07:57 | 3247 | 2025-11-28 07:03 | 2025-11-28 07:57 | 0:54 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 1 / 1 | MTN NG |  | HENRY OMELE |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty solenoid coil was replaced (No diesel outage after validation) | Faulty solenoid coil was replaced (No diesel outage after validation)
NOCINC0006439820 | External Reconciliation | Site Down | P4 | IHS_PAT_0003B | KW4587 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 12:36 | Precious Attah | 2025-11-24 12:36 | 2025-11-24 13:30 | 3243 | 2025-11-24 12:36 | 2025-11-24 13:30 | 0:54 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 2 | MTN NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG under voltage alarm was cleared
NOCINC0006450317 | External Reconciliation | Site Down | P1 | IHS_IBA_0083B | OY4129 | IBD | Ibadan | Oyo | 3 - Low | OY0995 | WEST |  | 2025-11-25 16:55 | Victor Otugo | 2025-11-25 16:55 | 2025-11-25 17:49 | 3232 | 2025-11-25 16:55 | 2025-11-25 17:49 | 0:54 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | Airtel NG, MTN NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | DG undervoltage alarm was cleared
NOCINC0006466143 | External Reconciliation | Site Down | P1 | IHS_ANA_1035A | AN0117 | ASB | Asaba | Anambra | 3 - Low | AN0601 | SOUTH EAST |  | 2025-11-27 15:51 | Uthman Akinola | 2025-11-27 15:48 | 2025-11-27 16:42 | 3221 | 2025-11-27 15:48 | 2025-11-27 16:42 | 0:54 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Clogged Radiator | 2 / 2 | MTN NG, Airtel NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG shut down on engine temperature, radiator flushed, and coolant was added(no diesel outage after validation) | DG shut down on engine temperature, radiator flushed, and coolant was added(no diesel outage after validation)
NOCINC0006457277 | External Reconciliation | Site Down | P2 | IHS_EDO_0747A | T0161 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 11:59 | Azeezat Badmus | 2025-11-26 11:58 | 2025-11-26 12:51 | 3216 | 2025-11-26 11:58 | 2025-11-26 12:51 | 0:54 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | PPM was completed at site (No diesel outage after validation)
NOCINC0006439090 | External Reconciliation | Site Down | P1 | IHS_DEL_0824A | T2660 | ASB | Asaba | Delta | 3 - Low | DL0839 | SOUTH SOUTH |  | 2025-11-24 09:54 | Ezinne Ubachukwu | 2025-11-24 09:51 | 2025-11-24 10:45 | 3213 | 2025-11-24 09:51 | 2025-11-24 10:45 | 0:54 | Tyllium NGA | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | MTN NG, Airtel NG |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Grid failure due to incomplete phase voltage, DG powered to restore site. (No diesel outage after validation) | Grid failure due to incomplete phase voltage, DG powered to restore site. (No diesel outage after validation)
NOCINC0006463128 | External Reconciliation | Site Down | P3 | IHS_EDO_1184H | ED2105 | IBD | Asaba | Edo | 3 - Low | ED0862 | SOUTH SOUTH |  | 2025-11-27 08:40 | Muhammed Hashirudeen | 2025-11-27 08:39 | 2025-11-27 09:33 | 3213 | 2025-11-27 08:39 | 2025-11-27 09:33 | 0:54 | Huawei | Equipment Repair | Passive | Infrastructure | Armoured Cable | 2 / 2 | Airtel NG, MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Burnt load cable was worked on and re-terminated (No diesel outage after validation)
NOCINC0006445949 | External Reconciliation | Site Down | P4 | IHS_OYO_1058A | OY2762 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 08:18 | Mutmainnah Saba | 2025-11-25 08:15 | 2025-11-25 09:09 | 3211 | 2025-11-25 08:15 | 2025-11-25 09:09 | 0:54 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Emeh Henry |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | flat DG battery, external battery was used to power the site
NOCINC0006445302 | External Reconciliation | Site Down | P1 | IHS_ARA_0001B | DL0726 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-25 04:26:26@DL0726_Opp Ahade Market | 2025-11-25 04:39 | System Administrator | 2025-11-25 04:31 | 2025-11-25 05:25 | 3210 | 2025-11-25 04:31 | 2025-11-25 05:25 | 0:54 | Tyllium NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Weak DG was prime to start (No diesel outage after validation) | Weak DG was prime to start (No diesel outage after validation)
NOCINC0006442660 | External Reconciliation | Site Down | P2 | IHS_WAR_0707E | T2676 | ASB | Asaba | Delta | 3 - Low | - | - | Cascaded Incident from TTO6725218 - Cascade Removed From TTO6725218 | 2025-11-24 17:54 | Tracy Osarumwense | 2025-11-24 17:53 | 2025-11-24 18:46 | 3208 | 2025-11-24 17:53 | 2025-11-24 18:46 | 0:53 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 2 | Suspected Passive Issue, Awaiting Update from FSE. | Suspected Passive Issue, Awaiting Update from FSE.
NOCINC0006473075 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0091C | OS4340 | IBD | Ibadan | Osun | 3 - Low | OS0710 | WEST |  | 2025-11-28 14:55 | Okusanya Joseph | 2025-11-28 14:47 | 2025-11-28 15:40 | 3203 | 2025-11-28 14:47 | 2025-11-28 15:40 | 0:53 | Huawei | Grid Supply | Passive | Grid | National Grid - Low Current Supply | 2 / 2 | Airtel NG, MTN NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Grid-DG Synchronization Failure due to low voltage from grid, DG was powered manually
NOCINC0006444076 | External Reconciliation | Site Down | P2 | IHS_IBA_0003B | OY4356 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 21:37 | Kandervil Uwah | 2025-11-24 21:25 | 2025-11-24 22:18 | 3201 | 2025-11-24 21:25 | 2025-11-24 22:18 | 0:53 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Fan Belt | 1 / 1 | INQ |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Fan Belt was cut and Replaced
NOCINC0006476458 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-28 23:52:03@T2449_Apedegbais Qtrs Ojobo | 2025-11-29 00:09 | System Administrator | 2025-11-28 23:59 | 2025-11-29 01:05 | 3980 | 2025-11-29 00:12 | 2025-11-29 01:05 | 0:53 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Suspected passive fault, awaiting RCA
NOCINC0006466374 | External Reconciliation | Site Down | P2 | IHS_EDO_0995A | ED4866 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 16:28 | Muhammed Hashirudeen | 2025-11-27 16:26 | 2025-11-27 17:19 | 3192 | 2025-11-27 16:26 | 2025-11-27 17:19 | 0:53 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Burnt load breaker was replaced (No diesel outage after validation)
NOCINC0006445330 | External Reconciliation | Site Down | P3 | IHS_ILO_0058C | KW4689 | IBD | Ibadan | Kwara | 3 - Low | KW0514 | WEST |  | 2025-11-25 04:55 | Praise Okezie | 2025-11-25 04:55 | 2025-11-25 05:48 | 3190 | 2025-11-25 04:55 | 2025-11-25 05:48 | 0:53 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Over Speed | 2 / 2 | MTN NG, Airtel NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG over frequency alarm, governor speed was adjusted
NOCINC0006446954 | External Reconciliation | Site Down | P2 | IHS_EDO_0939A | ED2014 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 10:21 | Oluwatomisin Sogbesan | 2025-11-25 10:20 | 2025-11-25 11:13 | 3188 | 2025-11-25 10:20 | 2025-11-25 11:13 | 0:53 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | MTN NG |  | Christopher Aiyenale |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Suspected passive issue at site Awaiting RCA from the FSE | Suspected passive issue at site Awaiting RCA from the FSE
NOCINC0006440678 | External Reconciliation | Site Down | P4 | IHS_ANA_0801A | T4059/T6475 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 13:58 | Ezinne Ubachukwu | 2025-11-24 13:55 | 2025-11-24 14:48 | 3187 | 2025-11-24 13:55 | 2025-11-24 14:48 | 0:53 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Idowu Dare |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Dg under frequency governor was adjusted | Dg under frequency governor was adjusted
NOCINC0006466151 | External Reconciliation | Site Down | P1 | IHS_EDO_0958A | ED2002 | IBD | Asaba | Edo | 3 - Low | ED0454 | SOUTH SOUTH |  | 2025-11-27 15:53 | Bukola Olabanji | 2025-11-27 15:53 | 2025-11-27 16:46 | 3186 | 2025-11-27 15:53 | 2025-11-27 16:46 | 0:53 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Imomoh Sylvanus |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006468472 | External Reconciliation | Site Down | P3 | IHS_IBA_0009B | OY2916 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 22:39 | Ifechi Ugwueze | 2025-11-27 22:38 | 2025-11-27 23:31 | 3178 | 2025-11-27 22:38 | 2025-11-27 23:31 | 0:53 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | SUNDAY MOSES |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Under frequency alarm was Cleared
NOCINC0006458469 | External Reconciliation | Site Down | P2 | IHS_ILO_0009V | KW2396 | IBD | Ibadan | Kwara | 3 - Low | KW0667 | WEST |  | 2025-11-26 15:02 | Oluwatomisin Ogunleye | 2025-11-26 15:02 | 2025-11-26 15:55 | 3160 | 2025-11-26 15:02 | 2025-11-26 15:55 | 0:53 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Sensor Switch | 2 / 2 | Airtel NG, MTN NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | faulty oil switch was worked on
NOCINC0006461938 | External Reconciliation | Site Down | P1 | IHS_NNE_0002B | AN0055 | ASB | Asaba | Anambra | 3 - Low | AN0436 | SOUTH EAST |  | 2025-11-27 01:53 | Aderonke Olowojoba | 2025-11-27 01:49 | 2025-11-27 02:42 | 3158 | 2025-11-27 01:49 | 2025-11-27 02:42 | 0:53 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Ukanwa Reginald | Ukanwa Karachi | Ukanwa Karachi | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | failed charging alternator was excited (No diesel outage after validation) | failed charging alternator was excited (No diesel outage after validation)
NOCINC0006489362 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0822A | T3157 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-30 19:42 | Precious Attah | 2025-11-30 19:41 | 2025-11-30 20:34 | 3156 | 2025-11-30 19:41 | 2025-11-30 20:34 | 0:53 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 1 / 1 | MTN NG |  | Afolabi Ganiyyu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty radiator was worked on
NOCINC0006467050 | External Reconciliation | Site Down | P3 | IHS_OND_0891A | OD2405 | IBD | Ibadan | Ondo | 3 - Low | ON0672 | WEST |  | 2025-11-27 18:23 | Iyesioluwa Ola | 2025-11-27 18:22 | 2025-11-27 19:14 | 3152 | 2025-11-27 18:22 | 2025-11-27 19:14 | 0:53 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | hybrid synchronization failure due to under frequency alarm, under frequency alarm was cleared.
NOCINC0006452373 | External Reconciliation | Site Down | P3 | IHS_OYO_0940A | T3628 | IBD | Ibadan | Osun | 3 - Low | OS0731 | WEST |  | 2025-11-25 22:48 | Osarieme Charles | 2025-11-25 22:45 | 2025-11-25 23:37 | 3151 | 2025-11-25 22:45 | 2025-11-25 23:37 | 0:53 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Actuator | 2 / 2 | Airtel NG, MTN NG |  | Zechariah Akinbulejo | Opeyemi Ajibola | Opeyemi Ajibola | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty actuator was worked on
NOCINC0006450667 | External Reconciliation | Site Down | P2 | IHS_DEL_0899A | T2748 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 17:56 | Tracy Osarumwense | 2025-11-25 17:54 | 2025-11-25 18:47 | 3149 | 2025-11-25 17:54 | 2025-11-25 18:47 | 0:52 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | HENRY OMELE |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | DG high temperature due to low coolant level, coolant was added
NOCINC0006481818 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1185A | DL0719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-29 17:16:01@DL0719_NO 6 Old Warri Road Okuvweri | 2025-11-29 17:30 | System Administrator | 2025-11-29 17:21 | 2025-11-29 18:26 | 3866 | 2025-11-29 17:33 | 2025-11-29 18:26 | 0:52 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006489940 | Internal Reconciliation | Site Down | P1 | IHS_IBA_0074B | OY4200 | IBD | Ibadan | Oyo | 3 - Low | OY1031 | WEST |  | 2025-11-30 21:46 | Damilola Paseda | 2025-11-30 21:42 | 2025-11-30 22:35 | 3146 | 2025-11-30 21:42 | 2025-11-30 22:35 | 0:52 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | Airtel NG |  | SUNDAY MOSES |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | MDG under voltage alarm was cleared and DG was powered manually | MDG under voltage alarm was cleared and DG was powered manually
NOCINC0006458691 | External Reconciliation | Site Down | P4 | IHS_ANA_1155A | AN0759 | ASB | Asaba | Anambra | 3 - Low | AN1116 | SOUTH EAST |  | 2025-11-26 15:35 | Oluwatoyin Fagite | 2025-11-26 15:33 | 2025-11-26 16:25 | 3141 | 2025-11-26 15:33 | 2025-11-26 16:25 | 0:52 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Henry Ikede | Ayeni Banabas | Ayeni Banabas | Henry Wanogho | Ifeanyi Chukusa |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG High Engine temperature due to low coolant level, coolant added and DG powered manually (No diesel outage after validation). | DG High Engine temperature due to low coolant level, coolant added and DG powered manually (No diesel outage after validation).
NOCINC0006457873 | External Reconciliation | Site Down | P4 | IHS_DEL_0978A | DL2993 | ASB | Asaba | Delta | 3 - Low | DL0933 | SOUTH SOUTH |  | 2025-11-26 13:33 | Oluwatobiloba Are | 2025-11-26 13:31 | 2025-11-26 14:23 | 3136 | 2025-11-26 13:31 | 2025-11-26 14:23 | 0:52 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG under frequency Governor was adjusted (No diesel outage after validation)
NOCINC0006437057 | External Reconciliation | Site Down | P2 | IHS_KWA_0892A | KW4592 | IBD | Ibadan | Kwara | 3 - Low | KW0485 | WEST |  | 2025-11-24 01:09 | Okusanya Joseph | 2025-11-24 01:09 | 2025-11-24 02:01 | 3134 | 2025-11-24 01:09 | 2025-11-24 02:01 | 0:52 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Faulty injector pump was worked on
NOCINC0006487781 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1200B | DL4064 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 15:08 | Tracy Osarumwense | 2025-11-30 15:05 | 2025-11-30 15:57 | 3132 | 2025-11-30 15:05 | 2025-11-30 15:57 | 0:52 | BJ Bison NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Babatunde Jimoh� |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Hybrid synchronization failure. DG powered manually. | Hybrid synchronization failure. DG powered manually. (No diesel outage after validation).
NOCINC0006467480 | External Reconciliation | Site Down | P3 | IHS_WAR_0017B | DL0487 | ASB | Asaba | Delta | 3 - Low | DL0618 | SOUTH SOUTH |  | 2025-11-27 19:43 | Mary Odefemi | 2025-11-27 19:43 | 2025-11-27 20:35 | 3132 | 2025-11-27 19:43 | 2025-11-27 20:35 | 0:52 | BJ Bison NGA | Equipment Repair | Passive | Infrastructure | Armoured Cable | 2 / 2 | Airtel NG, MTN NG |  | Emuesiri� Sunday |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Burnt Armoured cable was reterminated (No diesel outage after validation)
NOCINC0006489285 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0906H | - | - | Asaba | Delta | 3 - Low | DL0248 | SOUTH SOUTH |  | 2025-11-30 19:23 | Ayokunle Samuel | 2025-11-30 19:13 | 2025-11-30 20:05 | 3128 | 2025-11-30 19:13 | 2025-11-30 20:05 | 0:52 | Tyllium NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, Smile |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Weak DG was primed to start ( No diesel outage after validation) | Weak DG was primed to start ( No diesel outage after validation)
NOCINC0006459368 | External Reconciliation | Site Down | P2 | IHS_OYO_1198H | OY2864 | IBD | Ibadan | Oyo | 3 - Low | OY0998 | WEST |  | 2025-11-26 17:24 | Ifechi Ugwueze | 2025-11-26 17:22 | 2025-11-26 18:14 | 3128 | 2025-11-26 17:22 | 2025-11-26 18:14 | 0:52 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Taiwo Abanikannda | Yusuf Gyang |  | Soye West | Ugwu Samuel Nnamdi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006484279 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0800A | T3086 | IBD | Ibadan | Osun | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-30 02:31:22@ | 2025-11-30 02:48 | System Administrator | 2025-11-30 02:35 | 2025-11-30 03:27 | 3119 | 2025-11-30 02:35 | 2025-11-30 03:27 | 0:52 | IPT | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 1 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | DG-Grid synchronisation failure due to unstable grid supply, Dg powered manually
NOCINC0006468010 | External Reconciliation | Site Down | P4 | IHS_DEL_0991A | DL0013 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 21:20 | Patrick Okoro | 2025-11-27 21:18 | 2025-11-27 22:10 | 3116 | 2025-11-27 21:18 | 2025-11-27 22:10 | 0:52 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled
NOCINC0006449495 | External Reconciliation | Site Down | P4 | IHS_EDO_1071C | ED6141 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 15:21 | Oluwatomisin Sogbesan | 2025-11-25 15:19 | 2025-11-25 16:11 | 3115 | 2025-11-25 15:19 | 2025-11-25 16:11 | 0:52 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG High temperature due to low coolant level, coolant was added and DG powered manually (No diesel outage after validation) | DG High temperature due to low coolant level, coolant was added and DG powered manually (No diesel outage after validation)
NOCINC0006445270 | External Reconciliation | Site Down | P1 | IHS_OYO_1197H | - | - | Ibadan | Oyo | 3 - Low | OY1033 | WEST |  | 2025-11-25 04:28 | Damilola Paseda | 2025-11-25 04:24 | 2025-11-25 05:16 | 3113 | 2025-11-25 04:24 | 2025-11-25 05:16 | 0:52 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG under voltage alarm was cleared | DG under voltage alarm was cleared
NOCINC0006476337 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0817C | DL3250 | ASB | Asaba | Delta | 3 - Low | DL0725 | SOUTH SOUTH |  | 2025-11-28 23:19 | Mary Odefemi | 2025-11-28 23:19 | 2025-11-29 00:11 | 3110 | 2025-11-28 23:19 | 2025-11-29 00:11 | 0:52 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006440475 | External Reconciliation | Site Down | P3 | IHS_OYO_1359B | OY4486 | IBD | Ibadan | Oyo | 3 - Low | OY1238 | WEST |  | 2025-11-24 13:24 | Victor Otugo | 2025-11-24 13:22 | 2025-11-24 14:14 | 3108 | 2025-11-24 13:22 | 2025-11-24 14:14 | 0:52 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Current | 2 / 2 | MTN NG, Airtel NG |  | Samuel Olaobaju |  |  | Abiola Adegbiji | Habeeb Adepoju |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | High GG current alarm was cleared and GG was powered manually. | High GG current alarm was cleared and GG was powered manually.
NOCINC0006475303 | Internal Reconciliation | Site Down | P3 | IHS_OND_0041B | OD4741 | IBD | Ibadan | Ondo | 3 - Low | ON0693 | WEST |  | 2025-11-28 20:26 | Testimony Akinyemi | 2025-11-28 20:19 | 2025-11-28 21:11 | 3105 | 2025-11-28 20:19 | 2025-11-28 21:11 | 0:52 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | Airtel NG |  | Usman Hammed |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | hybrid synchronization failure due to dg undervoltage alarm, dg powered manually
NOCINC0006461429 | External Reconciliation | Site Down | P3 | IHS_OSU_0110C | OS4664 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 23:47 | Precious Attah | 2025-11-26 23:46 | 2025-11-27 00:38 | 3104 | 2025-11-26 23:46 | 2025-11-27 00:38 | 0:52 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | faulty fuel pump was replaced
NOCINC0006489103 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0708E | OY4493 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 18:44 | Precious Attah | 2025-11-30 18:42 | 2025-11-30 19:34 | 3099 | 2025-11-30 18:42 | 2025-11-30 19:34 | 0:52 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006488673 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0990A | DL0050 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 17:26 | Ayomide Akindolie | 2025-11-30 17:26 | 2025-11-30 18:17 | 3091 | 2025-11-30 17:26 | 2025-11-30 18:17 | 0:52 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Over Voltage | 1 / 1 | MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 16 | Over Voltage Alarm, AVR was adjusted. | Over Voltage Alarm, AVR was adjusted. (No diesel outage after validation).
NOCINC0006478650 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0745A | T3467 | IBD | Ibadan | Ekiti | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-29 10:22:09@T3467_AyegunleEkiti | 2025-11-29 10:38 | System Administrator | 2025-11-29 10:25 | 2025-11-29 11:17 | 3090 | 2025-11-29 10:25 | 2025-11-29 11:17 | 0:52 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gas Flow | 1 / 1 | MTN NG |  | Kayode Ayansola |  |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Block gas line was work on
NOCINC0006460059 | External Reconciliation | Site Down | P4 | IHS_EDO_0950A | ED2018 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 19:22 | Emmanuel Faleti | 2025-11-26 19:20 | 2025-11-26 20:11 | 3089 | 2025-11-26 19:20 | 2025-11-26 20:11 | 0:51 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 1 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty lift pump was worked on (No diesel outage after validation) | Faulty lift pump was worked on (No diesel outage after validation)
NOCINC0006483134 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0810A | T3736 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 21:34 | Kandervil Uwah | 2025-11-29 21:28 | 2025-11-29 22:19 | 3081 | 2025-11-29 21:28 | 2025-11-29 22:19 | 0:51 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Yohanna Sabo |  |  | Ibrahim Akinpelu | Yohanna Sabo |  | Collins Edike | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid Synchronisation failure due to over voltage discharge alarm
NOCINC0006459889 | External Reconciliation | Site Down | P2 | IHS_BEN_0701E | ED5125 | IBD | Asaba | Edo | 3 - Low | ED0696 | SOUTH SOUTH |  | 2025-11-26 18:58 | Emmanuel Faleti | 2025-11-26 18:58 | 2025-11-26 19:49 | 3080 | 2025-11-26 18:58 | 2025-11-26 19:49 | 0:51 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | Airtel NG, MTN NG |  | Olusoji Megbodofo | Achebe Chigozie | Omoragbon Austin | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty AVR was worked on (No diesel outage after validation)
NOCINC0006481247 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0771C | DL0583 | ASB | Asaba | Delta | 3 - Low | DL0886 | SOUTH SOUTH |  | 2025-11-29 16:11 | Ayomide Akindolie | 2025-11-29 16:09 | 2025-11-29 17:00 | 3076 | 2025-11-29 16:09 | 2025-11-29 17:00 | 0:51 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty radiator was worked on (No diesel outage after validation) | Faulty radiator was worked on (No diesel outage after validation)
NOCINC0006470364 | External Reconciliation | Site Down | P1 | IHS_OSU_0720E | OS2692 | IBD | Ibadan | Osun | 3 - Low | OS0692 | WEST |  | 2025-11-28 07:47 | Marvellous Emecheta | 2025-11-28 07:44 | 2025-11-28 08:35 | 3069 | 2025-11-28 07:44 | 2025-11-28 08:35 | 0:51 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Avr Burnt Fuse/Avr Issue | 2 / 2 | Airtel NG, MTN NG |  | Samuel Ajibade |  |  | Abiola Adegbiji | Babalola Babajide |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Faulty battery fuse was worked | Faulty battery fuse was worked
NOCINC0006471493 | Internal Reconciliation | Site Down | P2 | IHS_OZO_0003B | DL0886 | ASB | Asaba | Delta | 3 - Low | DL0846 | SOUTH SOUTH | Cascaded Incident from TTO6756972 - Cascade Removed From TTO6756972 | 2025-11-28 10:45 | Abundance Otunola | 2025-11-28 10:40 | 2025-11-28 11:32 | 3069 | 2025-11-28 10:40 | 2025-11-28 11:32 | 0:51 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | MTN NG, Airtel NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Weak DG battery, External battery was used to power site. (No diesel outage after validation)
NOCINC0006476774 | Internal Reconciliation | Site Down | P3 | IHS_OND_0973A | OD4740 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 02:22 | Iyesioluwa Ola | 2025-11-29 02:21 | 2025-11-29 03:12 | 3060 | 2025-11-29 02:21 | 2025-11-29 03:12 | 0:51 | IPT | Fuel Outage (Probable) | Passive | Diesel | Water Separator Blockage | 2 / 2 | MTN NG, Airtel NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Water ingress. Water was separated from diesel
NOCINC0006461964 | External Reconciliation | Site Down | P1 | IHS_OYO_1186H | OY4460 | IBD | Ibadan | Oyo | 3 - Low | OY0767 | WEST |  | 2025-11-27 02:06 | Precious Attah | 2025-11-27 02:06 | 2025-11-27 02:56 | 3056 | 2025-11-27 02:06 | 2025-11-27 02:56 | 0:51 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | Airtel NG, MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | High Engine Temperature due to low coolant level. Coolant was added
NOCINC0006476516 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0732E | OS4698 | IBD | Ibadan | Osun | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-29 00:13:08@OS4698_IHS Oke-Amola Ikirun | 2025-11-29 00:27 | System Administrator | 2025-11-29 00:15 | 2025-11-29 01:06 | 3053 | 2025-11-29 00:15 | 2025-11-29 01:06 | 0:51 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Charging Alternator | 1 / 2 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006457417 | External Reconciliation | Site Down | P4 | IHS_EKI_0846A | EK2255 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-26 12:23 | Tunji Adejumo | 2025-11-26 12:21 | 2025-11-26 13:12 | 3052 | 2025-11-26 12:21 | 2025-11-26 13:12 | 0:51 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | hybrid synchronization failure, SMU was reset
NOCINC0006454708 | External Reconciliation | Site Down | P4 | IHS_DEL_0995A | DL2675 | ASB | Asaba | Delta | 3 - Low | DL0871 | SOUTH SOUTH |  | 2025-11-26 02:18 | Ayokunle Samuel | 2025-11-26 02:18 | 2025-11-26 03:09 | 3052 | 2025-11-26 02:18 | 2025-11-26 03:09 | 0:51 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | Airtel NG, MTN NG |  | Eno Eyon |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG under frequency, governor control was adjusted. (No diesel outage after validation) | DG under frequency, governor control was adjusted. (No diesel outage after validation)
NOCINC0006473681 | Internal Reconciliation | Site Down | P4 | IHS_BEN_0024V | ED5144 | IBD | Asaba | Edo | 3 - Low | ED1089 | SOUTH SOUTH |  | 2025-11-28 16:22 | Muhammed Hashirudeen | 2025-11-28 16:21 | 2025-11-28 17:12 | 3051 | 2025-11-28 16:21 | 2025-11-28 17:12 | 0:51 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 1 / 1 | Airtel NG |  | Edwin Emehian |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed rectifier CSU was reset (No diesel outage after validation)
NOCINC0006449786 | External Reconciliation | Site Down | P3 | IHS_KWA_0939C | KW6391 | IBD | Ibadan | Kwara | 3 - Low | KW0598 | WEST | Cascaded Incident from TTO6733053 - Cascade Removed From TTO6733053 | 2025-11-25 16:02 | Oluwatomisin Ogunleye | 2025-11-25 15:57 | 2025-11-25 16:48 | 3044 | 2025-11-25 15:57 | 2025-11-25 16:48 | 0:51 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG under voltage alarm was cleared
NOCINC0006468634 | External Reconciliation | Site Down | P1 | IHS_EKI_0889B | EK6324 | IBD | Ibadan | Ekiti | 3 - Low | - | - | Cascaded Incident from TTO6753882 - Cascade Removed From TTO6753882 | 2025-11-27 23:30 | Tunji Adejumo | 2025-11-27 23:26 | 2025-11-28 00:17 | 3041 | 2025-11-27 23:26 | 2025-11-28 00:17 | 0:51 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | DG under voltage alarm was cleared
NOCINC0006445547 | External Reconciliation | Site Down | P1 | IHS_OND_0992A | OD2433 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-25 06:23 | Maureen Uchehorke | 2025-11-25 06:20 | 2025-11-25 07:10 | 3035 | 2025-11-25 06:20 | 2025-11-25 07:10 | 0:51 | Huawei | Equipment Repair | Passive | Infrastructure | Armoured Cable | 1 / 1 | MTN NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | loosed armoured cable was reterminated
NOCINC0006449449 | External Reconciliation | Site Down | P1 | IHS_OYO_1008A | OY2827 | IBD | Ibadan | Oyo | 3 - Low | OY1664 | WEST |  | 2025-11-25 15:15 | Victor Otugo | 2025-11-25 15:15 | 2025-11-25 16:06 | 3035 | 2025-11-25 15:15 | 2025-11-25 16:06 | 0:51 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | Airtel NG, MTN NG |  | SUNDAY MOSES |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Low gen frequency, frequency was adjusted
NOCINC0006446041 | External Reconciliation | Site Down | P2 | IHS_EDO_0976A | ED2148 | IBD | Asaba | Edo | 3 - Low | ED0659 | SOUTH SOUTH |  | 2025-11-25 08:43 | Emmanuel Faleti | 2025-11-25 08:42 | 2025-11-25 09:33 | 3031 | 2025-11-25 08:42 | 2025-11-25 09:33 | 0:51 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 2 / 2 | MTN NG, Airtel NG |  | Hammed Abubakar |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty solenoid was replaced. (No diesel outage after validation) | Faulty solenoid was replaced. (No diesel outage after validation)
NOCINC0006437563 | External Reconciliation | Site Down | P4 | IHS_KWA_1028B | KW6507 | IBD | Ibadan | Kwara | 3 - Low | KW0665 | WEST |  | 2025-11-24 03:10 | Okusanya Joseph | 2025-11-24 03:08 | 2025-11-24 03:59 | 3026 | 2025-11-24 03:08 | 2025-11-24 03:59 | 0:50 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 2 / 2 | MTN NG, Airtel NG |  | David Oyebamiji |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | faulty lift pump was worked on
NOCINC0006452911 | External Reconciliation | Site Down | P2 | IHS_OSU_0091C | OS4340 | IBD | Ibadan | Osun | 3 - Low | OS0710 | WEST |  | 2025-11-26 00:21 | Azeezat Adekunle | 2025-11-26 00:19 | 2025-11-26 01:09 | 3021 | 2025-11-26 00:19 | 2025-11-26 01:09 | 0:50 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to unstable grid supply, DG was Powered manually
NOCINC0006466783 | External Reconciliation | Site Down | P1 | IHS_WAR_0064B | DL0891 | ASB | Asaba | Delta | 3 - Low | DL0835 | SOUTH SOUTH |  | 2025-11-27 17:33 | Bukola Olabanji | 2025-11-27 17:29 | 2025-11-27 18:19 | 3019 | 2025-11-27 17:29 | 2025-11-27 18:19 | 0:50 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 3 | MTN NG, Airtel NG |  | Stanley Odira |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Frozen Orion CSU was reset (no passive issue on site).
NOCINC0006450809 | External Reconciliation | Site Down | P1 | IHS_EDO_0984A | ED2042 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 18:29 | Oluwatomisin Sogbesan | 2025-11-25 18:27 | 2025-11-25 19:17 | 3015 | 2025-11-25 18:27 | 2025-11-25 19:17 | 0:50 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to fail to start alarm. Alarm was cleared and Gen powered manually to restore the site. (No diesel outage after validation). | Hybrid synchronization failure due to fail to start alarm. Alarm was cleared and Gen powered manually to restore the site. (No diesel outage after validation).
NOCINC0006458054 | External Reconciliation | Site Down | P4 | IHS_WAR_0951B | DL3357 | ASB | Asaba | Delta | 3 - Low | DL1186 | SOUTH SOUTH |  | 2025-11-26 14:00 | Oluwatobiloba Are | 2025-11-26 13:56 | 2025-11-26 14:46 | 3010 | 2025-11-26 13:56 | 2025-11-26 14:46 | 0:50 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low oil pressure, oil was added (no diesel outage after validation)
NOCINC0006473595 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1255H | OY4168 | IBD | Ibadan | Oyo | 3 - Low | OY1314 | WEST |  | 2025-11-28 16:13 | Mutmainnah Saba | 2025-11-28 16:13 | 2025-11-28 17:03 | 3007 | 2025-11-28 16:13 | 2025-11-28 17:03 | 0:50 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | Airtel NG, MTN NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Under voltage Alarm was cleared. | Under voltage Alarm was cleared.
NOCINC0006472941 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0984A | ED2042 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 14:39 | Azeezat Badmus | 2025-11-28 14:38 | 2025-11-28 15:28 | 3007 | 2025-11-28 14:38 | 2025-11-28 15:28 | 0:50 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Interface Module Faulty | 1 / 1 | MTN NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty DG module was worked on(No diesel outage after validation)
NOCINC0006462432 | External Reconciliation | Site Down | P2 | IHS_OSU_0804A | T3085 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 05:40 | Hardy Oko | 2025-11-27 05:36 | 2025-11-27 06:26 | 3007 | 2025-11-27 05:36 | 2025-11-27 06:26 | 0:50 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 1 / 1 | MTN NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | faulty Radiator was worked on
NOCINC0006458129 | External Reconciliation | Site Down | P2 | IHS_IBA_0095C | OY4148 | IBD | Ibadan | Oyo | 3 - Low | OY1136 | WEST |  | 2025-11-26 14:14 | Bosede Kutelu | 2025-11-26 14:11 | 2025-11-26 15:01 | 3002 | 2025-11-26 14:11 | 2025-11-26 15:01 | 0:50 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Fan Belt Issue | 2 / 2 | Airtel NG, MTN NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Cut fan belt was replaced.
NOCINC0006470090 | External Reconciliation | Site Down | P4 | IHS_OND_1006A | OD2578 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 06:21 | Mary Elaigwu | 2025-11-28 06:20 | 2025-11-28 07:10 | 3001 | 2025-11-28 06:20 | 2025-11-28 07:10 | 0:50 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | Benjamin Onwu |  |  | Ibrahim Akinpelu | Benjamin Onwu |  | Victor Adeoye | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Undervoltage alarm was cleared
NOCINC0006440851 | External Reconciliation | Site Down | P4 | IHS_EDO_1256B | ED5547 | IBD | Asaba | Edo | 3 - Low | ED0973 | SOUTH SOUTH |  | 2025-11-24 14:15 | Evelyn Emagurehor | 2025-11-24 14:14 | 2025-11-24 15:04 | 3001 | 2025-11-24 14:14 | 2025-11-24 15:04 | 0:50 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 2 | MTN NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on to restore power to the site. (No diesel outage after validation). | Faulty injector pump was worked on to restore power to the site. (No diesel outage after validation).
NOCINC0006442489 | External Reconciliation | Site Down | P2 | IHS_KWA_0785A | T3163 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 17:25 | Precious Attah | 2025-11-24 17:25 | 2025-11-24 18:15 | 3001 | 2025-11-24 17:25 | 2025-11-24 18:15 | 0:50 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Radiator | 1 / 1 | MTN NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Faulty radiator was worked on
NOCINC0006476601 | Internal Reconciliation | Site Down | P3 | IHS_OND_0726E | OD4725 | IBD | Ibadan | Osun | 3 - Low | ON0617 | WEST |  | 2025-11-29 00:58 | Iyesioluwa Ola | 2025-11-29 00:57 | 2025-11-29 01:47 | 3001 | 2025-11-29 00:57 | 2025-11-29 01:47 | 0:50 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Aja |  |  | Ibrahim Akinpelu | Emmanuel Aja |  | Oluwafemi Iyiola | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Weak DG battery, external battery was used to power site
NOCINC0006490277 | Internal Reconciliation | Site Down | P1 | IHS_OSU_0850A | T3616 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 22:58 | Valentine Adinnu | 2025-11-30 22:53 | 2025-11-30 23:43 | 2997 | 2025-11-30 22:53 | 2025-11-30 23:43 | 0:50 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 1 | MTN NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Grid-DG synchronization failure due to unstable grid supply, DG was powered manually. | Grid-DG synchronization failure due to unstable grid supply, DG was powered manually.
NOCINC0006472641 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0973A | T3358 | IBD | Asaba | Edo | 3 - Low | ED0496 | SOUTH SOUTH |  | 2025-11-28 13:52 | Muhammed Hashirudeen | 2025-11-28 13:47 | 2025-11-28 14:36 | 2991 | 2025-11-28 13:47 | 2025-11-28 14:36 | 0:50 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty Charging alternator was excited (No diesel outage after validation)
NOCINC0006462963 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-27 07:57 | Aderonke Olowojoba | 2025-11-27 07:38 | 2025-11-27 08:28 | 2987 | 2025-11-27 07:38 | 2025-11-27 08:28 | 0:50 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006459581 | External Reconciliation | Site Down | P4 | IHS_ANA_1456C | AN3523 | ASB | Asaba | Anambra | 3 - Low | AN1075 | SOUTH EAST |  | 2025-11-26 18:04 | Femi Olanipekun | 2025-11-26 18:04 | 2025-11-26 18:53 | 2986 | 2025-11-26 18:04 | 2025-11-26 18:53 | 0:50 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | Airtel NG, MTN NG |  | Emmanuel Emmanuel | Henry Ubawuchi | Henry Ubawuchi | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Team confirmed high DG temperature, coolant was added to power the site (No diesel outage after validation) | Team confirmed high DG temperature, coolant was added to power the site (No diesel outage after validation)
NOCINC0006455775 | External Reconciliation | Site Down | P1 | IHS_EDO_0993A | ED2116 | IBD | Asaba | Edo | 3 - Low | ED0800 | SOUTH SOUTH |  | 2025-11-26 07:53 | Evelyn Emagurehor | 2025-11-26 07:52 | 2025-11-26 08:41 | 2985 | 2025-11-26 07:52 | 2025-11-26 08:41 | 0:50 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | EKPU SUNDAY | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on. (No diesel outage after validation) | Faulty injector pump was worked on. (No diesel outage after validation)
NOCINC0006441682 | External Reconciliation | Site Down | P1 | IHS_WAR_0869H | DL0348 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 16:11 | Tracy Osarumwense | 2025-11-24 16:11 | 2025-11-24 17:01 | 2984 | 2025-11-24 16:11 | 2025-11-24 17:01 | 0:50 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed Charging Alternator was excited. | Failed Charging Alternator was excited. (No diesel outage after validation).
NOCINC0006441520 | External Reconciliation | Site Down | P4 | IHS_OND_0868A | T3871 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-24 15:39 | Ihuoma Opurum | 2025-11-24 15:39 | 2025-11-24 16:28 | 2978 | 2025-11-24 15:39 | 2025-11-24 16:28 | 0:50 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | Benjamin Onwu |  |  | Ibrahim Akinpelu | Benjamin Onwu |  | Victor Adeoye | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG undervoltage alarm cleared
NOCINC0006446628 | External Reconciliation | Site Down | P3 | IHS_OND_0917A | OD2448 | IBD | Ibadan | Ondo | 3 - Low | ON0646 | WEST |  | 2025-11-25 09:37 | Yewande Adeagbo | 2025-11-25 09:34 | 2025-11-25 10:24 | 2975 | 2025-11-25 09:34 | 2025-11-25 10:24 | 0:50 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 2 / 2 | MTN NG, Airtel NG |  | David Christopher |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty Solenoid, Solenoid Bypassed Pending Replacement.
NOCINC0006456151 | External Reconciliation | Site Down | P2 | IHS_WAR_0963C | DL4026 | ASB | Asaba | Delta | 3 - Low | DL0975 | SOUTH SOUTH |  | 2025-11-26 09:12 | Oluwatobiloba Are | 2025-11-26 09:10 | 2025-11-26 10:00 | 2975 | 2025-11-26 09:10 | 2025-11-26 10:00 | 0:50 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 4 | DG high temperature due to low colant level, coolant was added
NOCINC0006459411 | External Reconciliation | Site Down | P1 | IHS_KWA_0861A | KW2356 | IBD | Ibadan | Kwara | 3 - Low | KW0374 | WEST |  | 2025-11-26 17:30 | Titus Tosin | 2025-11-26 17:30 | 2025-11-26 18:19 | 2973 | 2025-11-26 17:30 | 2025-11-26 18:19 | 0:50 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - AVR | 2 / 2 | Airtel NG, MTN NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty AVR was worked on
NOCINC0006480606 | Internal Reconciliation | Site Down | P1 | IHS_IBA_0101C | OY4161 | IBD | Ibadan | Oyo | 3 - Low | OY1001 | WEST |  | 2025-11-29 14:40 | Maureen Idoko | 2025-11-29 14:37 | 2025-11-29 15:26 | 2970 | 2025-11-29 14:37 | 2025-11-29 15:26 | 0:50 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Fan Belt Issue | 2 / 2 | MTN NG, Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Damaged fan belt was replaced. | Damaged fan belt was replaced.
NOCINC0006467197 | External Reconciliation | Site Down | P1 | IHS_EDO_0958A | ED2002 | IBD | Asaba | Edo | 3 - Low | ED0454 | SOUTH SOUTH |  | 2025-11-27 18:48 | Bukola Olabanji | 2025-11-27 18:46 | 2025-11-27 19:36 | 2968 | 2025-11-27 18:46 | 2025-11-27 19:36 | 0:49 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Phase Controller | 2 / 2 | MTN NG, Airtel NG |  | Imomoh Sylvanus |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | faulty Rectifier CSU was isolated
NOCINC0006452018 | External Reconciliation | Site Down | P3 | IHS_KWA_1035B | - | - | Ibadan | Kwara | 3 - Low | KW0574 | WEST |  | 2025-11-25 21:26 | Azeezat Adekunle | 2025-11-25 21:25 | 2025-11-25 22:14 | 2957 | 2025-11-25 21:25 | 2025-11-25 22:14 | 0:49 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006482177 | Internal Reconciliation | Site Down | P2 | IHS_IBA_0073B | OY4092 | IBD | Ibadan | Oyo | 3 - Low | OY1337 | WEST |  | 2025-11-29 18:40 | Damilola Paseda | 2025-11-29 18:39 | 2025-11-29 19:28 | 2956 | 2025-11-29 18:39 | 2025-11-29 19:28 | 0:49 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | MDG Undervoltage alarm was cleared and DG powered | MDG Undervoltage alarm was cleared and DG powered
NOCINC0006451376 | External Reconciliation | Site Down | P3 | IHS_EDO_1051C | ED6129 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 20:11 | Emmanuel Faleti | 2025-11-25 20:08 | 2025-11-25 20:57 | 2948 | 2025-11-25 20:08 | 2025-11-25 20:57 | 0:49 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty DG Injector Pump was worked on to restore power to the site. (No diesel outage after validation). | Faulty DG Injector Pump was worked on to restore power to the site. (No diesel outage after validation).
NOCINC0006475471 | Internal Reconciliation | Site Down | P1 | IHS_OND_0964A | OD4714 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 20:53 | Iyesioluwa Ola | 2025-11-28 20:52 | 2025-11-28 21:41 | 2944 | 2025-11-28 20:52 | 2025-11-28 21:41 | 0:49 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | Habeed Yunus |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 3 | False low oil pressure alarm was cleared
NOCINC0006443359 | External Reconciliation | Site Down | P2 | IHS_WAR_0928B | DL3323 | ASB | Asaba | Delta | 3 - Low | DL0890 | SOUTH SOUTH |  | 2025-11-24 19:38 | Ayokunle Samuel | 2025-11-24 19:34 | 2025-11-24 19:54 | 1216 | 2025-11-24 19:34 | 2025-11-24 20:23 | 0:49 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Contactor | 2 / 2 | MTN NG, Airtel NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty load contactor was worked on ( No diesel outage after validation) | Faulty load contactor was worked on ( No diesel outage after validation)
NOCINC0006477432 | Internal Reconciliation | Site Down | P3 | IHS_OSU_1043B | OS4746 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-29 06:36 | Sheriff Salami | 2025-11-29 06:33 | 2025-11-29 07:22 | 2940 | 2025-11-29 06:33 | 2025-11-29 07:22 | 0:49 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Fan Belt | 1 / 1 | MTN NG |  | Odufu Friday |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Cut fan belt was replaced
NOCINC0006484183 | Internal Reconciliation | Site Down | P3 | IHS_OND_0955A | OD2525 | IBD | Ibadan | Ondo | 3 - Low | ON0798 | WEST | CSL Fault@2025-11-30 01:54:59@OD2525_OANDO_ORE | 2025-11-30 02:09 | System Administrator | 2025-11-30 01:55 | 2025-11-30 02:44 | 2937 | 2025-11-30 01:55 | 2025-11-30 02:44 | 0:49 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | MTN NG, Airtel NG |  | Oluwaseun Awolope |  |  | Ibrahim Akinpelu | Oluwaseun Awolope |  | John Momoh | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Weak DG battery, external battery was used to power site
NOCINC0006466718 | External Reconciliation | Site Down | P1 | IHS_EDO_0958A | ED2002 | IBD | Asaba | Edo | 3 - Low | ED0454 | SOUTH SOUTH |  | 2025-11-27 17:27 | Mary Odefemi | 2025-11-27 17:24 | 2025-11-27 18:13 | 2936 | 2025-11-27 17:24 | 2025-11-27 18:13 | 0:49 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | Airtel NG, MTN NG |  | Imomoh Sylvanus |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Low DG frequency, governor was adjusted (No diesel outage after validation)
NOCINC0006455205 | External Reconciliation | Site Down | P4 | IHS_ANA_1332B | AN3183 | ASB | Asaba | Anambra | 3 - Low | AN1013 | SOUTH EAST |  | 2025-11-26 05:57 | Ayokunle Samuel | 2025-11-26 05:56 | 2025-11-26 06:45 | 2934 | 2025-11-26 05:56 | 2025-11-26 06:45 | 0:49 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | MTN NG, Airtel NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Frozen CSU was reset (No diesel outage after validation) | Frozen CSU was reset (No diesel outage after validation)
NOCINC0006487864 | Internal Reconciliation | Site Down | P4 | IHS_ANA_0854A | T4118 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 15:18 | Aderonke Olowojoba | 2025-11-30 15:14 | 2025-11-30 15:37 | 1372 | 2025-11-30 15:14 | 2025-11-30 16:03 | 0:49 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 1 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted(No diesel outage after validation) | Low DG frequency, Governor was adjusted(No diesel outage after validation)
NOCINC0006444638 | External Reconciliation | Site Down | P3 | IHS_OYO_0984A | OY3788 | IBD | Ibadan | Oyo | 3 - Low | OY1235 | WEST |  | 2025-11-24 23:42 | Damilola Paseda | 2025-11-24 23:41 | 2025-11-25 00:29 | 2930 | 2025-11-24 23:41 | 2025-11-25 00:29 | 0:49 | IPT | Fuel Outage (Probable) | Passive | Diesel | Diesel Top-Up | 2 / 2 | MTN NG, Airtel NG |  | Olalekan Saheed | Adewale Adejumo | Adewale Adejumo | Ogbuma Oluwafemi | Adekanmi Ajayi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Low diesel level, diesel was topped up | Low diesel level, diesel was topped up
NOCINC0006446936 | External Reconciliation | Site Down | P2 | IHS_OYO_0950A | T3694 | IBD | Ibadan | Oyo | 3 - Low | OY1012 | WEST |  | 2025-11-25 10:17 | Victor Otugo | 2025-11-25 10:16 | 2025-11-25 11:04 | 2923 | 2025-11-25 10:16 | 2025-11-25 11:04 | 0:49 | IPT | Fuel Outage (Probable) | Passive | Diesel | Fuel Line Issue | 2 / 2 | Airtel NG, MTN NG |  | Imoleayo Amoo | Olalekan Ajibola | Olalekan Ajibola | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | blocked fuel line was flushed
NOCINC0006439177 | External Reconciliation | Site Down | P1 | IHS_EDO_0891A | T3363 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 10:10 | Evelyn Emagurehor | 2025-11-24 10:08 | 2025-11-24 10:22 | 798 | 2025-11-24 10:08 | 2025-11-24 10:57 | 0:49 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed rectifier module was reset (No diesel outage after validation) | Failed rectifier module was reset
NOCINC0006451897 | External Reconciliation | Site Down | P1 | IHS_OYO_0969A | T3006 | IBD | Ibadan | Oyo | 3 - Low | OY1057 | WEST |  | 2025-11-25 21:04 | Aishat Oyedeji | 2025-11-25 21:02 | 2025-11-25 21:51 | 2914 | 2025-11-25 21:02 | 2025-11-25 21:51 | 0:49 | SPS | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on | Faulty injector pump was worked on
NOCINC0006482144 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1470B | AN3650 | ASB | Asaba | Anambra | 3 - Low | AN1080 | SOUTH EAST | Cascaded Incident from TTO6768943 - Cascade Removed From TTO6768943 | 2025-11-29 18:34 | Abundance Otunola | 2025-11-29 18:28 | 2025-11-29 19:17 | 2913 | 2025-11-29 18:28 | 2025-11-29 19:17 | 0:49 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 2 / 2 | MTN NG, Airtel NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty water pump was replaced to restore site(No diesel outage after validation) | Faulty water pump was replaced to restore site(No diesel outage after validation)
NOCINC0006450173 | External Reconciliation | Site Down | P4 | IHS_ANA_1071A | AN0307 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 16:47 | Oluwatoyin Fagite | 2025-11-25 16:45 | 2025-11-25 17:33 | 2904 | 2025-11-25 16:45 | 2025-11-25 17:33 | 0:48 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation) | Low DG frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006484714 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0947A | T2279 | ASB | Asaba | Delta | 3 - Low | DL0251 | SOUTH SOUTH |  | 2025-11-30 05:33 | Uthman Akinola | 2025-11-30 05:28 | 2025-11-30 06:16 | 2894 | 2025-11-30 05:28 | 2025-11-30 06:16 | 0:48 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Over Voltage | 2 / 2 | MTN NG, Airtel NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG over voltage, AVR was adjusted and alarm was cleared(no diesel outage after validation)
NOCINC0006472308 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1410H | AN0648 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 12:54 | Gbemisola Adedeji | 2025-11-28 12:49 | 2025-11-28 13:38 | 2886 | 2025-11-28 12:49 | 2025-11-28 13:38 | 0:48 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure, DG was powered manually(No diesel outage after validation) | Hybrid synchronization failure, DG was powered manually(No diesel outage after validation)
NOCINC0006484991 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0904A | T3561 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 07:07 | Mutmainnah Saba | 2025-11-30 07:03 | 2025-11-30 07:51 | 2881 | 2025-11-30 07:03 | 2025-11-30 07:51 | 0:48 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | voltage fluctuation due to absence of BUB, GG powered manually
NOCINC0006472931 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0911A | T2775 | ASB | Asaba | Delta | 3 - Low | DL0560 | SOUTH SOUTH |  | 2025-11-28 14:37 | Bukola Olabanji | 2025-11-28 14:37 | 2025-11-28 15:25 | 2881 | 2025-11-28 14:37 | 2025-11-28 15:25 | 0:48 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 2 / 2 | Airtel NG, MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty water pump was worked on | Faulty water pump was worked on (No diesel outage after validation)
NOCINC0006469790 | External Reconciliation | Site Down | P2 | IHS_EDO_0952A | ED2016 | IBD | Asaba | Edo | 3 - Low | ED0836 | SOUTH SOUTH |  | 2025-11-28 05:02 | Emmanuel Faleti | 2025-11-28 05:02 | 2025-11-28 05:50 | 2879 | 2025-11-28 05:02 | 2025-11-28 05:50 | 0:48 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 2 | Weak DG primed to start. (No diesel outage after validation) | Weak DG primed to start. (No diesel outage after validation)
NOCINC0006438287 | External Reconciliation | Site Down | P3 | IHS_OLE_0001B | - | - | Asaba | Delta | 3 - Low | DL0460 | SOUTH SOUTH |  | 2025-11-24 07:32 | Uthman Akinola | 2025-11-24 07:28 | 2025-11-24 08:16 | 2876 | 2025-11-24 07:28 | 2025-11-24 08:16 | 0:48 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | Airtel NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG under frequency, Governor was adjusted. (No diesel outage after validation) | DG under frequency, Governor was adjusted. (No diesel outage after validation)
NOCINC0006473885 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0735A | T3463 | IBD | Ibadan | Ekiti | 3 - Low | EK0533 | WEST |  | 2025-11-28 16:51 | Testimony Akinyemi | 2025-11-28 16:49 | 2025-11-28 17:36 | 2808 | 2025-11-28 16:48 | 2025-11-28 17:36 | 0:48 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Load Cable | 2 / 2 | MTN NG, Airtel NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Burnt load cable was reterminated
NOCINC0006466408 | External Reconciliation | Site Down | P2 | IHS_OSU_0953A | OS4274 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 16:34 | Mutmainnah Saba | 2025-11-27 16:30 | 2025-11-27 17:18 | 2868 | 2025-11-27 16:30 | 2025-11-27 17:18 | 0:48 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006484347 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1092A | DL0590 | ASB | Asaba | Delta | 3 - Low | DL1324 | SOUTH SOUTH |  | 2025-11-30 03:13 | Uthman Akinola | 2025-11-30 03:09 | 2025-11-30 03:57 | 2865 | 2025-11-30 03:09 | 2025-11-30 03:57 | 0:48 | Tyllium NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | hybrid sychronization failure due to frozen Orion, it was reset (no diesel outage after validation)
NOCINC0006458559 | External Reconciliation | Site Down | P4 | IHS_DEL_0884A | T2688 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 15:14 | Oluwatobiloba Are | 2025-11-26 15:12 | 2025-11-26 16:00 | 2860 | 2025-11-26 15:12 | 2025-11-26 16:00 | 0:48 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty DG battery, External battery was used to power site
NOCINC0006462590 | External Reconciliation | Site Down | P2 | IHS_OSU_0820A | T3606 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 06:24 | Hardy Oko | 2025-11-27 06:19 | 2025-11-27 07:06 | 2859 | 2025-11-27 06:19 | 2025-11-27 07:06 | 0:48 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Logic Board | 1 / 1 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 3 | Faulty logic board was worked on
NOCINC0006438155 | External Reconciliation | Site Down | P3 | IHS_DEL_1117A | DL0747 | ASB | Asaba | Delta | 3 - Low | DL0586 | SOUTH SOUTH |  | 2025-11-24 06:48 | Muhammed Hashirudeen | 2025-11-24 06:43 | 2025-11-24 07:31 | 2892 | 2025-11-24 06:43 | 2025-11-24 07:30 | 0:48 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | Gen Temp High | 2 / 2 | MTN NG, Airtel NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Coolant was added and DG high Temperature alarm was cleared. (No diesel outage after validation) | Coolant was added and DG high Temperature alarm was cleared. (No diesel outage after validation)
NOCINC0006439205 | External Reconciliation | Site Down | P2 | IHS_OND_0894A | OD2408 | IBD | Ibadan | Ondo | 3 - Low | ON0706 | WEST |  | 2025-11-24 10:19 | Ihuoma Opurum | 2025-11-24 10:17 | 2025-11-24 11:04 | 2847 | 2025-11-24 10:17 | 2025-11-24 11:04 | 0:47 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty Injector Pump Worked On
NOCINC0006458261 | External Reconciliation | Site Down | P1 | IHS_KWA_0880A | KW2375 | IBD | Ibadan | Kwara | 3 - Low | KW0431 | WEST |  | 2025-11-26 14:31 | Titus Tosin | 2025-11-26 14:31 | 2025-11-26 15:18 | 2829 | 2025-11-26 14:31 | 2025-11-26 15:18 | 0:47 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | Airtel NG, MTN NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Faulty fuel pump was worked on
NOCINC0006475467 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0059B | OS2661 | IBD | Ibadan | Osun | 3 - Low | OS0684 | WEST |  | 2025-11-28 20:52 | Titus Tosin | 2025-11-28 20:50 | 2025-11-28 21:38 | 2822 | 2025-11-28 20:50 | 2025-11-28 21:38 | 0:47 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid-DG synchronization failure due to unstable grid supply issue. DG was powered manually.
NOCINC0006472403 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0921B | EK6303 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-28 13:05 | Maureen Uchehorke | 2025-11-28 13:02 | 2025-11-28 13:49 | 2819 | 2025-11-28 13:02 | 2025-11-28 13:49 | 0:47 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Low Oil Pressure | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Low oil Pressure, oil was added
NOCINC0006452509 | External Reconciliation | Site Down | P3 | IHS_DEL_1143A | DL0638 | ASB | Asaba | Delta | 3 - Low | DL0596 | SOUTH SOUTH |  | 2025-11-25 22:55 | Ayomide Akindolie | 2025-11-25 22:53 | 2025-11-25 23:40 | 2819 | 2025-11-25 22:53 | 2025-11-25 23:40 | 0:47 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Babatunde Jimoh� | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on (No diesel outage after validation)
NOCINC0006482739 | Internal Reconciliation | Site Down | P3 | IHS_OND_0810A | T3456 | IBD | Ibadan | Ondo | 3 - Low | ON0728 | WEST |  | 2025-11-29 20:27 | Abisoye Olaleye | 2025-11-29 20:24 | 2025-11-29 21:11 | 2808 | 2025-11-29 20:24 | 2025-11-29 21:11 | 0:47 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG under voltage alarm was cleared and DG powered manually
NOCINC0006488639 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1251H | OY4116 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 17:20 | Aishat Oyedeji | 2025-11-30 17:20 | 2025-11-30 18:07 | 2795 | 2025-11-30 17:20 | 2025-11-30 18:07 | 0:47 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 2 | MTN NG |  | BANKOLE SODIQ |  | Filani Oluwatobi | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization due to frozen CSU, CSU was Reset | Hybrid synchronization failure due to frozen CSU, CSU was reset
NOCINC0006473268 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0948A | OS2623 | IBD | Ibadan | Osun | 3 - Low | OS0682 | WEST |  | 2025-11-28 15:24 | Valentine Adinnu | 2025-11-28 15:24 | 2025-11-28 16:11 | 2794 | 2025-11-28 15:24 | 2025-11-28 16:11 | 0:47 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Faulty injector pump was worked on | Faulty injector pump was worked on
NOCINC0006484841 | Internal Reconciliation | Site Down | P3 | IHS_EDO_1043C | ED6117 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 06:28 | Muhammed Hashirudeen | 2025-11-30 06:27 | 2025-11-30 07:14 | 2791 | 2025-11-30 06:27 | 2025-11-30 07:14 | 0:47 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 1 / 1 | MTN NG |  | Kazeem Ajiboye |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Faulty fuel pump was serviced (No diesel outage after validation) | Faulty fuel pump was serviced (No diesel outage after validation)
NOCINC0006465715 | External Reconciliation | Site Down | P1 | IHS_DEL_1115A | DL0492 | ASB | Asaba | Delta | 3 - Low | DL0920 | SOUTH SOUTH |  | 2025-11-27 14:56 | Mary Odefemi | 2025-11-27 14:55 | 2025-11-27 15:41 | 2784 | 2025-11-27 14:55 | 2025-11-27 15:41 | 0:46 | Huawei | Equipment Repair | Passive | Infrastructure | Armoured Cable | 1 / 2 | Airtel NG |  | David Uja |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Burnt DC load cable was replaced (No diesel outage after validation)
NOCINC0006464850 | External Reconciliation | Site Down | P2 | IHS_OSU_0949A | OS2838 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 12:53 | Titus Tosin | 2025-11-27 12:52 | 2025-11-27 13:38 | 2782 | 2025-11-27 12:52 | 2025-11-27 13:38 | 0:46 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Solenoid Coil | 1 / 1 | MTN NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty solonoid was replaced
NOCINC0006457739 | External Reconciliation | Site Down | P3 | IHS_EDO_0749A | T0218 | IBD | Asaba | Edo | 3 - Low | ED0700 | SOUTH SOUTH |  | 2025-11-26 13:07 | Emmanuel Faleti | 2025-11-26 13:07 | 2025-11-26 13:53 | 2776 | 2025-11-26 13:07 | 2025-11-26 13:53 | 0:46 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Outage Issue | 2 / 2 | Airtel NG, MTN NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | delay in grid synchronization due to weak bub, DG powered manaully (No diesel ouatge after validation) (No diesel ouatge after validation)
NOCINC0006466824 | External Reconciliation | Site Down | P1 | IHS_OSU_0732E | OS4698 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 17:40 | Samuel Omole | 2025-11-27 17:22 | 2025-11-27 18:01 | 2351 | 2025-11-27 17:22 | 2025-11-27 18:08 | 0:46 | IPT | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | MTN NG, Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to incomplete phase, DG was powered manually.
NOCINC0006481601 | Internal Reconciliation | Site Down | P3 | IHS_EDO_1000A | ED4857 | IBD | Asaba | Edo | 3 - Low | ED1062 | SOUTH SOUTH |  | 2025-11-29 17:02 | Evelyn Emagurehor | 2025-11-29 17:01 | 2025-11-29 17:48 | 2764 | 2025-11-29 17:01 | 2025-11-29 17:48 | 0:46 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | High temperature due to coolant low level in the ACDG – Radiator. Water and coolant added and Gen power to restore the site. (No diesel outage after validation). | High temperature due to coolant low level in the ACDG – Radiator. Water and coolant added and Gen power to restore the site. (No diesel outage after validation).
NOCINC0006469389 | External Reconciliation | Site Down | P1 | IHS_DEL_1032A | DL0344 | ASB | Asaba | Delta | 3 - Low | DL1259 | SOUTH SOUTH |  | 2025-11-28 01:38 | Oluwatobiloba Are | 2025-11-28 01:36 | 2025-11-28 02:22 | 2764 | 2025-11-28 01:36 | 2025-11-28 02:22 | 0:46 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty rectifier module was replaced
NOCINC0006461975 | External Reconciliation | Site Down | P3 | IHS_EKI_0923B | EK4552 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-27 02:13 | Oluwadara Bankole | 2025-11-27 02:09 | 2025-11-27 02:55 | 2764 | 2025-11-27 02:09 | 2025-11-27 02:55 | 0:46 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Weak crank battery, External battery was used to power site. | Weak crank battery, External battery was used to power site.
NOCINC0006461229 | External Reconciliation | Site Down | P3 | IHS_EDO_1184H | ED2105 | IBD | Asaba | Edo | 3 - Low | ED0862 | SOUTH SOUTH |  | 2025-11-26 22:57 | Oluwatomisin Sogbesan | 2025-11-26 22:57 | 2025-11-26 23:43 | 2763 | 2025-11-26 22:57 | 2025-11-26 23:43 | 0:46 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset (No diesel outage after validation) | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006472310 | Internal Reconciliation | Site Down | P1 | IHS_OND_0964A | OD4714 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 12:54 | Testimony Akinyemi | 2025-11-28 12:53 | 2025-11-28 13:39 | 2760 | 2025-11-28 12:53 | 2025-11-28 13:39 | 0:46 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Habeed Yunus |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | hybrid synchronization failure due to frozen CSU was reset
NOCINC0006469743 | External Reconciliation | Site Down | P1 | IHS_EDO_0814A | T3489 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 04:22 | Patrick Okoro | 2025-11-28 04:19 | 2025-11-28 05:05 | 2757 | 2025-11-28 04:19 | 2025-11-28 05:05 | 0:46 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | MICHAEL TONDO | Micheal Tondo | Micheal Tondo | Cornelius Yakubu | Elochukwu Umeohana |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty injector was worked on | Faulty injector was worked on
NOCINC0006459455 | External Reconciliation | Site Down | P3 | IHS_EDO_1059C | ED6110 | IBD | Asaba | Edo | 3 - Low | ED0737 | SOUTH SOUTH |  | 2025-11-26 17:38 | Azeezat Badmus | 2025-11-26 17:35 | 2025-11-26 18:21 | 2751 | 2025-11-26 17:35 | 2025-11-26 18:21 | 0:46 | MPI NGA | Equipment Repair | Passive | Hybrid | Hybrid Module | 2 / 2 | MTN NG, Airtel NG |  | Asukwo Effiong | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure,DG powered manually (No diesel outage after validation)
NOCINC0006466172 | External Reconciliation | Site Down | P1 | IHS_ANA_1097A | AN4831 | ASB | Asaba | Anambra | 3 - Low | AN0583 | SOUTH EAST |  | 2025-11-27 15:57 | Uthman Akinola | 2025-11-27 15:57 | 2025-11-27 16:43 | 2748 | 2025-11-27 15:57 | 2025-11-27 16:43 | 0:46 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Emmanuel | Henry Ubawuchi | Henry Ubawuchi | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Frozen CSU was reset(no diesel outage after validation)
NOCINC0006473294 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1163H | T3359 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 15:27 | Muhammed Hashirudeen | 2025-11-28 15:27 | 2025-11-28 16:13 | 2747 | 2025-11-28 15:27 | 2025-11-28 16:13 | 0:46 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 1 | MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | faulty lift pump was worked on (No diesel outage after validation)
NOCINC0006483234 | Internal Reconciliation | Site Down | P2 | IHS_OSU_1016H | T3833 | IBD | Ibadan | Osun | 3 - Low | OS0520 | WEST |  | 2025-11-29 21:42 | Okusanya Joseph | 2025-11-29 21:41 | 2025-11-29 22:27 | 2745 | 2025-11-29 21:41 | 2025-11-29 22:27 | 0:46 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Grid synchronization failure from grid to DG due to grid supply issue , DG powered manually
NOCINC0006487063 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1436B | AN3472 | ASB | Asaba | Anambra | 3 - Low | AN0997 | SOUTH EAST |  | 2025-11-30 13:17 | Ayokunle Samuel | 2025-11-30 13:17 | 2025-11-30 14:03 | 2744 | 2025-11-30 13:17 | 2025-11-30 14:03 | 0:46 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Weak DG was prime to start. (No diesel outage after validation) | Weak DG was prime to start. (No diesel outage after validation)
NOCINC0006439148 | External Reconciliation | Site Down | P4 | IHS_EDO_1240B | ED5542 | IBD | Asaba | Edo | 3 - Low | ED1126 | SOUTH SOUTH |  | 2025-11-24 10:04 | Tracy Osarumwense | 2025-11-24 10:04 | 2025-11-24 10:50 | 2739 | 2025-11-24 10:04 | 2025-11-24 10:50 | 0:46 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 2 / 2 | MTN NG, Airtel NG |  | Jude Audu | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty Lift Pump was worked on. | Faulty Lift Pump was worked on. (No diesel outage after validation).
NOCINC0006461792 | External Reconciliation | Site Down | P1 | IHS_DEL_0811A | T2654 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 00:59 | Ezinne Ubachukwu | 2025-11-27 00:57 | 2025-11-27 01:42 | 2739 | 2025-11-27 00:57 | 2025-11-27 01:42 | 0:46 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 1 / 1 | MTN NG |  | Dare Oguyemi | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 8 | Faulty water pump was worked on (No diesel outage after validation) | Faulty water pump was worked on (No diesel outage after validation)
NOCINC0006465387 | External Reconciliation | Site Down | P2 | IHS_OSU_0061B | OS4254 | IBD | Ibadan | Osun | 3 - Low | OS0698 | WEST |  | 2025-11-27 14:11 | Mutmainnah Saba | 2025-11-27 14:09 | 2025-11-27 14:55 | 2737 | 2025-11-27 14:09 | 2025-11-27 14:55 | 0:46 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Low oil pressure oil was added
NOCINC0006450120 | External Reconciliation | Site Down | P2 | IHS_OSU_0710E | OS4660 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 16:42 | Hardy Oko | 2025-11-25 16:37 | 2025-11-25 17:23 | 2730 | 2025-11-25 16:37 | 2025-11-25 17:23 | 0:46 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 2 | MTN NG |  | Odufu Friday |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | DG high temperature, thermostat was bypassed
NOCINC0006450969 | External Reconciliation | Site Down | P1 | IHS_ANA_1072A | AN0304 | ASB | Asaba | Anambra | 3 - Low | AN0717 | SOUTH EAST |  | 2025-11-25 18:55 | Oluwatoyin Fagite | 2025-11-25 18:53 | 2025-11-25 19:39 | 2730 | 2025-11-25 18:53 | 2025-11-25 19:39 | 0:46 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Flat DG battery. external battery used to power site. (No diesel outage after validation) | Flat DG battery. external battery used to power site. (No diesel outage after validation)
NOCINC0006462238 | External Reconciliation | Site Down | P4 | IHS_WAR_0771C | DL0583 | ASB | Asaba | Delta | 3 - Low | DL0886 | SOUTH SOUTH |  | 2025-11-27 04:30 | Tracy Osarumwense | 2025-11-27 04:29 | 2025-11-27 05:15 | 2729 | 2025-11-27 04:29 | 2025-11-27 05:15 | 0:45 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | Airtel NG, MTN NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty Radiator was worked on. | Faulty Radiator was worked on. (No diesel outage after validation).
NOCINC0006457671 | External Reconciliation | Site Down | P1 | IHS_EDO_0766A | T3213 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 12:53 | Emmanuel Faleti | 2025-11-26 12:49 | 2025-11-26 13:34 | 2723 | 2025-11-26 12:49 | 2025-11-26 13:34 | 0:45 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 1 / 1 | MTN NG |  | Imomoh Sylvanus |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Grid to DG synchronization failure due to Grid Incomplete Phase, DG was powered manually.
NOCINC0006448239 | External Reconciliation | Site Down | P3 | IHS_OND_0901A | OD2419 | IBD | Ibadan | Ondo | 3 - Low | ON0806 | WEST |  | 2025-11-25 12:48 | Tunji Adejumo | 2025-11-25 12:46 | 2025-11-25 13:32 | 2723 | 2025-11-25 12:46 | 2025-11-25 13:32 | 0:45 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | John Kunamon |  |  | Ibrahim Akinpelu | John Kunamon |  | Fagbemi Solomon | Ibrahim Yekini | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | High DG temperature, coolant was added and alarm was cleared
NOCINC0006460254 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-26 20:04 | Azeezat Badmus | 2025-11-26 20:02 | 2025-11-26 20:48 | 2717 | 2025-11-26 20:02 | 2025-11-26 20:48 | 0:45 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation) | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006454891 | External Reconciliation | Site Down | P2 | IHS_DEL_0863A | T2724 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 04:01 | Ayokunle Samuel | 2025-11-26 04:01 | 2025-11-26 04:46 | 2716 | 2025-11-26 04:01 | 2025-11-26 04:46 | 0:45 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Eno Eyon |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to flat cracking battery, external battery was used to power the site (No diesel outage after validation) | Hybrid synchronization failure due to flat cracking battery, external battery was used to power the site (No diesel outage after validation)
NOCINC0006484071 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1246B | ED5521 | IBD | Asaba | Edo | 3 - Low | ED1124 | SOUTH SOUTH |  | 2025-11-30 01:25 | Bukola Olabanji | 2025-11-30 01:23 | 2025-11-30 02:08 | 2711 | 2025-11-30 01:23 | 2025-11-30 02:08 | 0:45 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Oil pressure alarm cleared, oil top-up completed
NOCINC0006481384 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0028B | DL0570 | ASB | Asaba | Delta | 3 - Low | DL0973 | SOUTH SOUTH |  | 2025-11-29 16:31 | Ayomide Akindolie | 2025-11-29 16:30 | 2025-11-29 17:15 | 2707 | 2025-11-29 16:30 | 2025-11-29 17:15 | 0:45 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator Leakage | 2 / 2 | MTN NG, Airtel NG |  | Kevwe Oshoture |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Radiator leakage at site, sealant was applied (No diesel outage after validation)
NOCINC0006489240 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0865A | T3680 | IBD | Ibadan | Osun | 3 - Low | OS0949 | WEST |  | 2025-11-30 19:12 | Aishat Oyedeji | 2025-11-30 19:12 | 2025-11-30 19:57 | 2705 | 2025-11-30 19:12 | 2025-11-30 19:57 | 0:45 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 2 | MTN NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed rectifier module was reset
NOCINC0006477846 | Internal Reconciliation | Site Down | P2 | IHS_OND_1037B | OD6245 | IBD | Ibadan | Ondo | 3 - Low | ON0886 | WEST |  | 2025-11-29 08:25 | Testimony Akinyemi | 2025-11-29 08:23 | 2025-11-29 09:08 | 2704 | 2025-11-29 08:23 | 2025-11-29 09:08 | 0:45 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Radiator Leakage | 2 / 2 | MTN NG, Airtel NG |  | David Christopher |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | High engine temperature due to radiator leakage, radiator was sealed and coolant added
NOCINC0006440623 | External Reconciliation | Site Down | P3 | IHS_DEL_1231B | - | - | Asaba | Delta | 3 - Low | DL0924 | SOUTH SOUTH |  | 2025-11-24 13:47 | Ayomide Akindolie | 2025-11-24 13:47 | 2025-11-24 14:32 | 2701 | 2025-11-24 13:47 | 2025-11-24 14:32 | 0:45 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | Airtel NG |  | David Uja |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled (No diesel outage after validation) | Tripped load breaker was enabled (No diesel outage after validation)
NOCINC0006471021 | Internal Reconciliation | Site Down | P4 | IHS_OSU_1059B | OS4807 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 09:42 | Oluwatomisin Ogunleye | 2025-11-28 09:41 | 2025-11-28 10:26 | 2700 | 2025-11-28 09:41 | 2025-11-28 10:26 | 0:45 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Charging Alternator | 1 / 1 | MTN NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty charging alternator was replaced | Faulty charging alternator was replaced
NOCINC0006464942 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-27 13:03 | Bukola Olabanji | 2025-11-27 12:43 | 2025-11-27 13:28 | 2699 | 2025-11-27 12:43 | 2025-11-27 13:28 | 0:45 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site I.D:-IHS_WAR_0747C Access Ref:-IHSREF/25112605474226012828 Company:- UZIBEN/GAIO SYSTEMS Purpose of visitation:- RMS REINSTALLATION DAY 1 RMS Engineer Name: NNADI EMMANUEL Phone Number:- 08033305048
NOCINC0006466004 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST |  | 2025-11-27 15:33 | Mutmainnah Saba | 2025-11-27 15:30 | 2025-11-27 16:15 | 2698 | 2025-11-27 15:30 | 2025-11-27 16:15 | 0:45 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | hybrid synchronization failure due to frozen csu, csu was reset.
NOCINC0006459687 | External Reconciliation | Site Down | P3 | IHS_ILO_0033B | KW4613 | IBD | Ibadan | Kwara | 3 - Low | KW0468 | WEST |  | 2025-11-26 18:25 | Titus Tosin | 2025-11-26 18:23 | 2025-11-26 19:08 | 2697 | 2025-11-26 18:23 | 2025-11-26 19:08 | 0:45 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Tripped load breaker enabled
NOCINC0006476006 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0866A | T4100 | ASB | Asaba | Anambra | 3 - Low | AN0699 | SOUTH EAST |  | 2025-11-28 22:05 | Akachukwu Ugwu | 2025-11-28 22:02 | 2025-11-28 22:47 | 2694 | 2025-11-28 22:02 | 2025-11-28 22:47 | 0:45 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Harrison Igbinedion | Harrison Igbinedion | Harrison Igbinedion | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Failed charging alternator was excited (No diesel outage after validation). | Failed charging alternator was excited (No diesel outage after validation).
NOCINC0006487243 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1047C | ED6121 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 13:35 | Evelyn Emagurehor | 2025-11-30 13:32 | 2025-11-30 14:17 | 2694 | 2025-11-30 13:32 | 2025-11-30 14:17 | 0:45 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006441741 | External Reconciliation | Site Down | P4 | IHS_OYO_1447B | - | - | Ibadan | Oyo | 3 - Low | OY1565 | WEST |  | 2025-11-24 16:22 | Victor Otugo | 2025-11-24 16:15 | 2025-11-24 17:00 | 2690 | 2025-11-24 16:15 | 2025-11-24 17:00 | 0:45 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | Airtel NG |  | Mohammed Soliu |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting passive update from Fse.
NOCINC0006462037 | External Reconciliation | Site Down | P1 | IHS_ANA_0950A | T4047 | ASB | Asaba | Anambra | 3 - Low | AN0566 | SOUTH EAST |  | 2025-11-27 02:48 | Aderonke Olowojoba | 2025-11-27 02:45 | 2025-11-27 03:30 | 2687 | 2025-11-27 02:45 | 2025-11-27 03:30 | 0:45 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Low DG frequency, Governor was adjusted (No diesel outage after validation) | Low DG frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006466131 | External Reconciliation | Site Down | P1 | IHS_ANA_0791A | T0184 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 15:49 | Uthman Akinola | 2025-11-27 15:46 | 2025-11-27 16:31 | 2686 | 2025-11-27 15:46 | 2025-11-27 16:31 | 0:45 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Idowu Dare |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006470235 | External Reconciliation | Site Down | P1 | IHS_OSU_0850A | T3616 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 07:06 | Mary Elaigwu | 2025-11-28 07:04 | 2025-11-28 07:49 | 2681 | 2025-11-28 07:04 | 2025-11-28 07:49 | 0:45 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Failed charging alternator excited
NOCINC0006436517 | External Reconciliation | Site Down | P2 | IHS_KWA_0785A | T3163 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 00:11 | Okusanya Joseph | 2025-11-24 00:11 | 2025-11-24 00:56 | 2681 | 2025-11-24 00:11 | 2025-11-24 00:56 | 0:45 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Radiator | 1 / 1 | MTN NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | DG high temperature due to faulty radiator was worked on
NOCINC0006489060 | Resolved | Site Down | P4 | IHS_EDO_0738E | ED5369 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 18:32 | Tracy Osarumwense | 2025-11-30 18:32 | 2025-11-30 19:17 | 2679 | 2025-11-30 18:32 | 2025-11-30 19:17 | 0:45 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Flat DG Battery, External Battery was used to power site. | Flat DG Battery, External Battery was used to power site.
NOCINC0006440184 | External Reconciliation | Site Down | P3 | IHS_EDO_0987A | ED2044 | IBD | Asaba | Edo | 3 - Low | ED0551 | SOUTH SOUTH |  | 2025-11-24 13:07 | Evelyn Emagurehor | 2025-11-24 13:06 | 2025-11-24 13:51 | 2674 | 2025-11-24 13:06 | 2025-11-24 13:51 | 0:45 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 2 | Airtel NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was replaced to restore power to the site. (No diesel outage after validation). | Weak DG was replaced to restore power to the site. (No diesel outage after validation).
NOCINC0006469898 | External Reconciliation | Site Down | P4 | IHS_ANA_1168A | AN0642 | ASB | Asaba | Anambra | 3 - Low | AN0551 | SOUTH EAST |  | 2025-11-28 05:40 | Oluwatoyin Fagite | 2025-11-28 05:35 | 2025-11-28 06:19 | 2673 | 2025-11-28 05:35 | 2025-11-28 06:19 | 0:45 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 2 / 2 | MTN NG, Airtel NG |  | Oladele Segun | David Ndubuisi | David Ndubuisi | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty kick starter was worked on (No diesel outage after validation) | Faulty kick starter was worked on (No diesel outage after validation)
NOCINC0006489239 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1247B | ED5524 | IBD | Asaba | Edo | 3 - Low | ED1138 | SOUTH SOUTH |  | 2025-11-30 19:12 | Oluwatomisin Sogbesan | 2025-11-30 19:08 | 2025-11-30 19:52 | 2666 | 2025-11-30 19:08 | 2025-11-30 19:52 | 0:44 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation). | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation).
NOCINC0006458095 | External Reconciliation | Site Down | P2 | IHS_ILO_0005V | KW4728 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-26 14:09 | Oluwatomisin Ogunleye | 2025-11-26 14:08 | 2025-11-26 14:52 | 2656 | 2025-11-26 14:08 | 2025-11-26 14:52 | 0:44 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, INQ |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Grid-DG synchronization failure due to unstable grid supply issue. DG was powered manually.
NOCINC0006465839 | External Reconciliation | Site Down | P2 | IHS_OND_0838A | T3930 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 15:16 | Iyesioluwa Ola | 2025-11-27 15:16 | 2025-11-27 16:00 | 2654 | 2025-11-27 15:16 | 2025-11-27 16:00 | 0:44 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gas Flow | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 3 | Frozen gas line was worked on
NOCINC0006443727 | External Reconciliation | Site Down | P3 | IHS_WAR_0771C | DL0583 | ASB | Asaba | Delta | 3 - Low | DL0886 | SOUTH SOUTH |  | 2025-11-24 20:43 | Quadri Ogundare | 2025-11-24 20:42 | 2025-11-24 21:26 | 2650 | 2025-11-24 20:42 | 2025-11-24 21:26 | 0:44 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | High engine temperature, Coolant was topped (No diesel outage after validation) | High engine temperature, Coolant was topped (No diesel outage after validation)
NOCINC0006468451 | External Reconciliation | Site Down | P4 | IHS_EKI_0813A | T3747 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-27 22:34 | Tunji Adejumo | 2025-11-27 22:33 | 2025-11-27 23:17 | 2644 | 2025-11-27 22:33 | 2025-11-27 23:17 | 0:44 | Inhouse | Equipment Repair | Passive | ACDG Gen | Gen Temp High | 1 / 1 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG high temperature alarm was cleared
NOCINC0006437891 | External Reconciliation | Site Down | P3 | IHS_OND_1131B | - | - | Ibadan | Ondo | 3 - Low | ON0805 | WEST |  | 2025-11-24 05:24 | Abisoye Olaleye | 2025-11-24 05:21 | 2025-11-24 06:05 | 2640 | 2025-11-24 05:21 | 2025-11-24 06:05 | 0:44 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | Airtel NG |  | Sanusi Idowu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | faulty injector pump was worked on
NOCINC0006467144 | External Reconciliation | Site Down | P1 | IHS_DEL_0984A | DL0006 | ASB | Asaba | Delta | 3 - Low | DL1272 | SOUTH SOUTH |  | 2025-11-27 18:38 | Uthman Akinola | 2025-11-27 18:38 | 2025-11-27 19:22 | 2635 | 2025-11-27 18:38 | 2025-11-27 19:22 | 0:44 | Tyllium NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 2 / 2 | MTN NG, Airtel NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty hand primer was worked on (No diesel outage after validation) | Faulty hand primer was worked on (No diesel outage after validation)
NOCINC0006481485 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1200B | DL4064 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 16:47 | Ayomide Akindolie | 2025-11-29 16:44 | 2025-11-29 17:28 | 2633 | 2025-11-29 16:44 | 2025-11-29 17:28 | 0:44 | BJ Bison NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Babatunde Jimoh� |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid delay due to fail to start alarm, alarm was cleared (No diesel outage after validation) | Hybrid delay due to fail to start alarm, alarm was cleared (No diesel outage after validation)
NOCINC0006486409 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0958B | KW4553 | IBD | Ibadan | Kwara | 3 - Low | - | - | Site Abis control link broken@2025-11-30 11:27:53@KW0641 | 2025-11-30 11:51 | System Administrator | 2025-11-30 11:28 | 2025-11-30 12:12 | 2628 | 2025-11-30 11:28 | 2025-11-30 12:12 | 0:44 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | Airtel NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006447379 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-25 11:07 | Emmanuel Faleti | 2025-11-25 11:06 | 2025-11-25 11:50 | 2622 | 2025-11-25 11:06 | 2025-11-25 11:50 | 0:44 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty Radiator was worked on to restore power on site (No diesel outage after validation) | Faulty Radiator was worked on to restore power on site (No diesel outage after validation)
NOCINC0006442449 | External Reconciliation | Site Down | P1 | IHS_EDO_0808A | T3232 | IBD | Asaba | Edo | 3 - Low | ED0739 | SOUTH SOUTH |  | 2025-11-24 17:20 | Evelyn Emagurehor | 2025-11-24 17:18 | 2025-11-24 18:02 | 2621 | 2025-11-24 17:18 | 2025-11-24 18:02 | 0:44 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Lifting Pump Faulty | 2 / 2 | Airtel NG, MTN NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty lift pump was worked on (No diesel outage after validation) | Faulty lift pump was worked on (No diesel outage after validation)
NOCINC0006467778 | External Reconciliation | Site Down | P2 | IHS_OND_0027B | OD4755 | IBD | Ibadan | Osun | 3 - Low | ON0568 | WEST |  | 2025-11-27 20:35 | Mary Elaigwu | 2025-11-27 20:34 | 2025-11-27 21:18 | 2618 | 2025-11-27 20:34 | 2025-11-27 21:18 | 0:44 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 2 / 2 | MTN NG, Airtel NG |  | Olatunde Babatunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty DG temperature Sensoe switch was worked on
NOCINC0006476489 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0904A | T3561 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 00:16 | Bosede Kutelu | 2025-11-29 00:12 | 2025-11-29 00:56 | 2606 | 2025-11-29 00:12 | 2025-11-29 00:56 | 0:43 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Voltage fluctuations due to absence of BUB at site, GG auto restart
NOCINC0006481999 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0777A | T3159 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-29 18:07 | Azeezat Adekunle | 2025-11-29 18:04 | 2025-11-29 18:47 | 2605 | 2025-11-29 18:04 | 2025-11-29 18:47 | 0:43 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Afolabi Ganiyyu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was serviced
NOCINC0006445028 | External Reconciliation | Site Down | P1 | IHS_KWA_0759A | T3136 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 02:31 | Praise Okezie | 2025-11-25 02:28 | 2025-11-25 03:11 | 2602 | 2025-11-25 02:28 | 2025-11-25 03:11 | 0:43 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | faulty injector pump was worked on
NOCINC0006484999 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0004B | ED2095 | IBD | Asaba | Edo | 3 - Low | ED0967 | SOUTH SOUTH |  | 2025-11-30 07:09 | Muhammed Hashirudeen | 2025-11-30 07:09 | 2025-11-30 07:52 | 2600 | 2025-11-30 07:09 | 2025-11-30 07:52 | 0:43 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | MTN NG, Airtel NG |  | Hammed Abubakar |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Frozen rectifier CSU controller was reset (No diesel outage after validation) | Frozen rectifier CSU controller was reset (No diesel outage after validation)
NOCINC0006476695 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0951B | DL3357 | ASB | Asaba | Delta | 3 - Low | DL1186 | SOUTH SOUTH |  | 2025-11-29 01:48 | Mary Odefemi | 2025-11-29 01:41 | 2025-11-29 02:24 | 2598 | 2025-11-29 01:41 | 2025-11-29 02:24 | 0:43 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006469733 | External Reconciliation | Site Down | P4 | IHS_EDO_1071C | ED6141 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 04:17 | Emmanuel Faleti | 2025-11-28 04:16 | 2025-11-28 04:59 | 2586 | 2025-11-28 04:16 | 2025-11-28 04:59 | 0:43 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 1 / 1 | MTN NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to faulty kickstarter, faulty kick starter was worked on and DG powered manually. (No diesel outage after validation) | Hybrid synchronization failure due to faulty Kickstarter, faulty kick starter was worked on and DG powered manually. (No diesel outage after validation)
NOCINC0006481794 | Internal Reconciliation | Site Down | P2 | IHS_OND_0826A | T3421 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 17:29 | Testimony Akinyemi | 2025-11-29 17:27 | 2025-11-29 18:10 | 2586 | 2025-11-29 17:27 | 2025-11-29 18:10 | 0:43 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | David Christopher |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Failed Charging Alternator Was Excited
NOCINC0006483551 | Internal Reconciliation | Site Down | P3 | IHS_OSU_1058B | OS4802 | IBD | Ibadan | Osun | 3 - Low | - | - | Cascaded Incident from TTO6770449 - Cascade Removed From TTO6770449 | 2025-11-29 22:35 | Mutmainnah Saba | 2025-11-29 22:25 | 2025-11-29 23:08 | 2582 | 2025-11-29 22:25 | 2025-11-29 23:08 | 0:43 | IPT | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify | 2 | Frozen CSU was reset
NOCINC0006484130 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0738C | DL1027 | ASB | Asaba | Delta | 3 - Low | DL0732 | SOUTH SOUTH |  | 2025-11-30 02:03 | Bukola Olabanji | 2025-11-30 02:03 | 2025-11-30 02:46 | 2580 | 2025-11-30 02:03 | 2025-11-30 02:46 | 0:43 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Kevwe Oshoture |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG low frequency governor was adjusted
NOCINC0006488362 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0944B | DL3327 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 16:39 | Ezinne Ubachukwu | 2025-11-30 16:34 | 2025-11-30 17:17 | 2576 | 2025-11-30 16:34 | 2025-11-30 17:17 | 0:43 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier - Circuit Breaker | 1 / 1 | MTN NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Tripped Load breaker was enabled (No diesel outage after validation) | Tripped Load breaker was enabled (No diesel outage after validation)
NOCINC0006440321 | External Reconciliation | Site Down | P1 | IHS_DEL_0914A | T2746 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 13:15 | Ayomide Akindolie | 2025-11-24 13:12 | 2025-11-24 13:55 | 2574 | 2025-11-24 13:12 | 2025-11-24 13:55 | 0:43 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Radiator Leakage | 1 / 1 | MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | DG high temperature due to Radiator Leakage, Radiator was worked on.. | DG high temperature due to Radiator Leakage, Radiator was worked on.. (No diesel outage after validation).
NOCINC0006485950 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1151A | DL0675 | ASB | Asaba | Delta | 3 - Low | DL0761 | SOUTH SOUTH |  | 2025-11-30 10:36 | Ayomide Akindolie | 2025-11-30 10:35 | 2025-11-30 11:18 | 2573 | 2025-11-30 10:35 | 2025-11-30 11:18 | 0:43 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | Airtel NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Tripped DG load breaker was enabled (No diesel outage after validation) | Tripped DG load breaker was enabled (No diesel outage after validation).
NOCINC0006450641 | External Reconciliation | Site Down | P1 | IHS_WAR_0740C | DL1063 | ASB | Asaba | Delta | 3 - Low | DL0937 | SOUTH SOUTH |  | 2025-11-25 17:52 | Ezinne Ubachukwu | 2025-11-25 17:50 | 2025-11-25 18:33 | 2573 | 2025-11-25 17:50 | 2025-11-25 18:33 | 0:43 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | MTN NG, Airtel NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Frozen orion was rest (No diesel outage after validation) | Frozen orion was rest (No diesel outage after validation)
NOCINC0006469184 | External Reconciliation | Site Down | P1 | IHS_OYO_0989A | OY2802 | IBD | Ibadan | Oyo | 3 - Low | OY0956 | WEST |  | 2025-11-28 00:49 | Ifechi Ugwueze | 2025-11-28 00:48 | 2025-11-28 01:31 | 2569 | 2025-11-28 00:48 | 2025-11-28 01:31 | 0:43 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Over Frequency | 2 / 2 | MTN NG, Airtel NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Under frequency alarm was cleared
NOCINC0006463207 | External Reconciliation | Site Down | P3 | IHS_IBA_0705E | OY3696 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 08:58 | Mutmainnah Saba | 2025-11-27 08:54 | 2025-11-27 09:37 | 2566 | 2025-11-27 08:54 | 2025-11-27 09:37 | 0:43 | SPS | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Smile |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | PPM (generator servicing) was carried out with ref IHSREF/25111412132702706592
NOCINC0006463522 | External Reconciliation | Site Down | P1 | IHS_ANA_0790A | T4023 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 09:58 | Gbemisola Adedeji | 2025-11-27 09:56 | 2025-11-27 10:38 | 2565 | 2025-11-27 09:56 | 2025-11-27 10:38 | 0:43 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Sensor Switch | 1 / 1 | MTN NG |  | Appeal John |  |  | Erik Nwodo | Nwigbo Chijioke |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty oil switch was worked on (No diesel outage after validation) | Faulty oil switch was worked on (No diesel outage after validation)
NOCINC0006462554 | External Reconciliation | Site Down | P1 | IHS_EDO_0979A | ED2145 | IBD | Asaba | Edo | 3 - Low | ED0499 | SOUTH SOUTH |  | 2025-11-27 06:10 | Oluwatomisin Sogbesan | 2025-11-27 06:06 | 2025-11-27 06:49 | 2564 | 2025-11-27 06:06 | 2025-11-27 06:49 | 0:43 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low oil pressure was added (No diesel outage after validation) | Low oil pressure was added (No diesel outage after validation)
NOCINC0006460117 | External Reconciliation | Site Down | P4 | IHS_DEL_0997A | DL0010 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 19:36 | Patrick Okoro | 2025-11-26 19:30 | 2025-11-26 20:13 | 2559 | 2025-11-26 19:30 | 2025-11-26 20:13 | 0:43 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | faulty AVR was worked on (No diesel outage after validation) | faulty AVR was worked on (No diesel outage after validation)
NOCINC0006477226 | Internal Reconciliation | Site Down | P4 | IHS_BEN_0032V | ED5182 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 05:25 | Elizabeth Apata | 2025-11-29 05:23 | 2025-11-29 06:06 | 2558 | 2025-11-29 05:23 | 2025-11-29 06:06 | 0:43 | MPI NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | SAMUEL ASUKWO |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure, DG was powered manually
NOCINC0006480415 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0804A | T3777 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 14:08 | Zainab Bello | 2025-11-29 14:08 | 2025-11-29 14:50 | 2551 | 2025-11-29 14:08 | 2025-11-29 14:50 | 0:43 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Over Voltage | 1 / 1 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG over voltage alarm was cleared
NOCINC0006445014 | External Reconciliation | Site Down | P3 | IHS_EDO_1051C | ED6129 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 02:22 | Azeezat Badmus | 2025-11-25 02:15 | 2025-11-25 02:57 | 2548 | 2025-11-25 02:15 | 2025-11-25 02:57 | 0:42 | MPI NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006477176 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1169H | ED2065 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 05:08 | Elizabeth Apata | 2025-11-29 05:06 | 2025-11-29 05:48 | 2548 | 2025-11-29 05:06 | 2025-11-29 05:48 | 0:42 | Huawei | Site Intrusion | Intrusion On Site | Intrusion On Site | Intrusion - Vandalism/Sabotage | 1 / 1 | MTN NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Intrusion on site, Attempted theft at site
NOCINC0006473432 | Internal Reconciliation | Site Down | P1 | IHS_OYO_1282H | OY4049 | IBD | Ibadan | Oyo | 3 - Low | OY0971 | WEST |  | 2025-11-28 15:49 | Okusanya Joseph | 2025-11-28 15:48 | 2025-11-28 16:30 | 2548 | 2025-11-28 15:48 | 2025-11-28 16:30 | 0:42 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Low gen frequency, governor was adjusted
NOCINC0006460929 | External Reconciliation | Site Down | P3 | IHS_EDO_1051C | ED6129 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 21:55 | Oluwatomisin Sogbesan | 2025-11-26 21:53 | 2025-11-26 22:35 | 2542 | 2025-11-26 21:53 | 2025-11-26 22:35 | 0:42 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Priming Motor Faulty | 1 / 1 | MTN NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty hand primer was worked on (No diesel outage after validation) | Faulty hand primer was worked on (No diesel outage after validation)
NOCINC0006477263 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0901A | KW4588 | IBD | Ibadan | Kwara | 3 - Low | KW0466 | WEST |  | 2025-11-29 05:42 | Titus Tosin | 2025-11-29 05:42 | 2025-11-29 06:24 | 2537 | 2025-11-29 05:42 | 2025-11-29 06:24 | 0:42 | IPT | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | MTN NG, Airtel NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Grid to DG synchronization failure due to incomplete phase, DG was powered manually.
NOCINC0006481538 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0084B | OS4412 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-29 16:55 | Valentine Adinnu | 2025-11-29 16:53 | 2025-11-29 17:35 | 2535 | 2025-11-29 16:53 | 2025-11-29 17:35 | 0:42 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Emergency Stop | 1 / 1 | MTN NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify | 1 | Emergency stop alarm was cleared and DG was powered | Emergency stop alarm was cleared and DG was powered
NOCINC0006448524 | External Reconciliation | Site Down | P4 | IHS_OSU_1052B | OS4798 | IBD | Ibadan | Osun | 3 - Low | OS0942 | WEST |  | 2025-11-25 13:25 | Mutmainnah Saba | 2025-11-25 13:23 | 2025-11-25 14:05 | 2533 | 2025-11-25 13:23 | 2025-11-25 14:05 | 0:42 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on
NOCINC0006461319 | External Reconciliation | Site Down | P2 | IHS_OND_1100B | OD2536 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 23:17 | Oluwadara Bankole | 2025-11-26 23:13 | 2025-11-26 23:56 | 2532 | 2025-11-26 23:13 | 2025-11-26 23:56 | 0:42 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 1 / 1 | MTN NG |  | John Kunamon |  |  | Ibrahim Akinpelu | John Kunamon |  | Fagbemi Solomon | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty kick starter was worked on | Faulty kick starter was worked on
NOCINC0006470454 | External Reconciliation | Site Down | P1 | IHS_EKI_0739A | T3704 | IBD | Ibadan | Ekiti | 3 - Low | EK0399 | WEST |  | 2025-11-28 08:05 | Mary Elaigwu | 2025-11-28 08:05 | 2025-11-28 08:47 | 2524 | 2025-11-28 08:05 | 2025-11-28 08:47 | 0:42 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 2 / 2 | MTN NG, Airtel NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG crank battery, external battery was used to start the GG
NOCINC0006468216 | External Reconciliation | Site Down | P3 | IHS_OSU_1061B | - | - | Ibadan | Osun | 3 - Low | OS0866 | WEST |  | 2025-11-27 21:56 | Osarieme Charles | 2025-11-27 21:49 | 2025-11-27 22:31 | 2519 | 2025-11-27 21:49 | 2025-11-27 22:31 | 0:42 | IPT | Fuel Outage (Probable) | Passive | DCDG Gen | DCDG - Fuel Pump | 1 / 1 | Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | faulty fuel pump was replaced
NOCINC0006482054 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0057B | OS2650 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-29 18:17 | Favour Ahize | 2025-11-29 18:14 | 2025-11-29 18:56 | 2516 | 2025-11-29 18:14 | 2025-11-29 18:56 | 0:42 | IPT | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on
NOCINC0006465664 | External Reconciliation | Site Down | P1 | IHS_EDO_0905A | T3379 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 14:49 | Elizabeth Apata | 2025-11-27 14:41 | 2025-11-27 15:23 | 2515 | 2025-11-27 14:41 | 2025-11-27 15:23 | 0:42 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | SAHEED SHONDE | Babatunde Olayiwola | Shonde Saheed | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Suspected passive fault, awaiting update from FSE
NOCINC0006444424 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-24 22:38 | Kehinde Akinbowale | 2025-11-24 22:35 | 2025-11-24 23:17 | 2514 | 2025-11-24 22:35 | 2025-11-24 23:17 | 0:42 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Weak DG was primed to start(No diesel outage after validation) | Weak DG was primed to start(No diesel outage after validation)
NOCINC0006460404 | External Reconciliation | Site Down | P2 | IHS_EDO_1026A | ED2161 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 20:24 | Azeezat Badmus | 2025-11-26 20:19 | 2025-11-26 21:01 | 2513 | 2025-11-26 20:19 | 2025-11-26 21:01 | 0:42 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 2 | Flat DG crank battery, external battery was used to restore power on site (No diesel outage after validation) | Flat DG crank battery, external battery was used to restore power on site (No diesel outage after validation)
NOCINC0006466686 | External Reconciliation | Site Down | P1 | IHS_DEL_0788A | T2656 | ASB | Asaba | Delta | 3 - Low | DL0078 | SOUTH SOUTH |  | 2025-11-27 17:20 | Bukola Olabanji | 2025-11-27 17:19 | 2025-11-27 18:01 | 2513 | 2025-11-27 17:19 | 2025-11-27 18:01 | 0:42 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 2 | MTN NG |  | Babatunde Jimoh� |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 6 | Faulty lift pump was worked on
NOCINC0006470712 | External Reconciliation | Site Down | P1 | IHS_EDO_0820A | T3238 | IBD | Asaba | Edo | 3 - Low | - | - | Cascaded Incident from TTO6756161 - Cascade Removed From TTO6756161 | 2025-11-28 08:59 | Muhammed Hashirudeen | 2025-11-28 08:57 | 2025-11-28 09:38 | 2511 | 2025-11-28 08:57 | 2025-11-28 09:38 | 0:42 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | DG PPM was carried out (No diesel outage after validation)
NOCINC0006459689 | External Reconciliation | Site Down | P1 | IHS_DEL_0960A | DL2994 | ASB | Asaba | Delta | 3 - Low | DL0799 | SOUTH SOUTH |  | 2025-11-26 18:25 | Oluwatobiloba Are | 2025-11-26 18:24 | 2025-11-26 19:06 | 2502 | 2025-11-26 18:24 | 2025-11-26 19:06 | 0:42 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low oil pressure, oil was added (No diesel outage after validation)
NOCINC0006455471 | External Reconciliation | Site Down | P1 | IHS_ANA_0991A | T4167 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 07:01 | Ayokunle Samuel | 2025-11-26 07:01 | 2025-11-26 07:42 | 2435 | 2025-11-26 07:00 | 2025-11-26 07:42 | 0:42 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Obinna Clinton |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty injector pump was serviced (No diesel outage after validation) | Faulty injector pump was serviced (No diesel outage after validation)
NOCINC0006462277 | External Reconciliation | Site Down | P2 | IHS_OYO_0904A | T3561 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 04:49 | Victor Otugo | 2025-11-27 04:46 | 2025-11-27 05:28 | 2495 | 2025-11-27 04:46 | 2025-11-27 05:28 | 0:42 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | voltage fluctuation due to zero backup batteries at site
NOCINC0006459040 | External Reconciliation | Site Down | P1 | IHS_SAP_0008B | DL0851 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 16:25 | Oluwatobiloba Are | 2025-11-26 16:10 | 2025-11-26 16:52 | 2493 | 2025-11-26 16:10 | 2025-11-26 16:52 | 0:42 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006478866 | Internal Reconciliation | Site Down | P2 | IHS_EDO_1179H | ED5348 | IBD | Asaba | Edo | 3 - Low | ED1137 | SOUTH SOUTH |  | 2025-11-29 11:03 | Evelyn Emagurehor | 2025-11-29 10:45 | 2025-11-29 11:27 | 2490 | 2025-11-29 10:45 | 2025-11-29 11:27 | 0:42 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 4 | Smile, INQ |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Low DG frequency ,Governor was adjusted (No diesel outage after validation).
NOCINC0006450036 | External Reconciliation | Site Down | P1 | IHS_ANA_0995A | T4199 | ASB | Asaba | Anambra | 3 - Low | AN0605 | SOUTH EAST |  | 2025-11-25 16:33 | Ezinne Ubachukwu | 2025-11-25 16:30 | 2025-11-25 17:11 | 2483 | 2025-11-25 16:30 | 2025-11-25 17:11 | 0:41 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | DG Low Battery | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Emmanuel | Henry Ubawuchi | Henry Ubawuchi | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | weak DG battery External battery was used
NOCINC0006465898 | External Reconciliation | Site Down | P3 | IHS_OLE_0002B | DL0693 | ASB | Asaba | Delta | 3 - Low | DL0844 | SOUTH SOUTH |  | 2025-11-27 15:24 | Uthman Akinola | 2025-11-27 15:21 | 2025-11-27 16:02 | 2468 | 2025-11-27 15:21 | 2025-11-27 16:02 | 0:41 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Lifting Pump Faulty | 2 / 2 | Airtel NG, MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty lifting pump was worked on(no diesel outage after validation)
NOCINC0006463519 | External Reconciliation | Site Down | P1 | IHS_DEL_0925A | T2913 | ASB | Asaba | Delta | 3 - Low | DL0767 | SOUTH SOUTH |  | 2025-11-27 09:56 | Mary Odefemi | 2025-11-27 09:56 | 2025-11-27 10:37 | 2465 | 2025-11-27 09:56 | 2025-11-27 10:37 | 0:41 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on (No diesel outage after validation)
NOCINC0006487071 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1156A | DL0671 | ASB | Asaba | Delta | 3 - Low | DL1250 | SOUTH SOUTH |  | 2025-11-30 13:19 | Tracy Osarumwense | 2025-11-30 13:19 | 2025-11-30 14:00 | 2462 | 2025-11-30 13:19 | 2025-11-30 14:00 | 0:41 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG Under Frequency, Governor was adjusted. | DG Under Frequency, Governor was adjusted. (No diesel outage after validation).
NOCINC0006489356 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0061B | OS4254 | IBD | Ibadan | Osun | 3 - Low | OS0698 | WEST |  | 2025-11-30 19:41 | Victor Otugo | 2025-11-30 19:35 | 2025-11-30 20:16 | 2460 | 2025-11-30 19:35 | 2025-11-30 20:16 | 0:41 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | Airtel NG, MTN NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Under frequency, frequency was adjusted in the governor. | Under frequency, frequency was adjusted in the governor.
NOCINC0006472307 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0710E | OS4660 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 12:53 | Oluwatomisin Ogunleye | 2025-11-28 12:50 | 2025-11-28 13:31 | 2459 | 2025-11-28 12:50 | 2025-11-28 13:31 | 0:41 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 2 | MTN NG |  | Odufu Friday |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | High engine temperature due to low coolant level, Coolant was added
NOCINC0006455561 | External Reconciliation | Site Down | P3 | IHS_OND_0812A | T3941 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 07:03 | Testimony Akinyemi | 2025-11-26 07:02 | 2025-11-26 07:43 | 2459 | 2025-11-26 07:02 | 2025-11-26 07:43 | 0:41 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Daniel Akinfenwa |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Weak crank battery. An external battery was used to power the site
NOCINC0006484896 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0057B | ED5096 | IBD | Asaba | Edo | 3 - Low | ED0664 | SOUTH SOUTH |  | 2025-11-30 06:43 | Muhammed Hashirudeen | 2025-11-30 06:41 | 2025-11-30 07:22 | 2458 | 2025-11-30 06:41 | 2025-11-30 07:22 | 0:41 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Ismail Adeyinka |  |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low frequency governor was adjusted (No diesel outage after validation)
NOCINC0006459134 | External Reconciliation | Site Down | P4 | IHS_EDO_1190H | ED2062 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 16:42 | Azeezat Badmus | 2025-11-26 16:39 | 2025-11-26 17:20 | 2448 | 2025-11-26 16:39 | 2025-11-26 17:20 | 0:41 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Smile |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | High temperature due to coolant low level water and coolant added. DG powered manually.(No diesel outage after validation) | High temperature due to coolant low level water and coolant added. DG powered manually.(No diesel outage after validation)
NOCINC0006466733 | External Reconciliation | Site Down | P1 | IHS_ANA_0802A | T4037 | ASB | Asaba | Anambra | 3 - Low | AI0520 | SOUTH EAST |  | 2025-11-27 17:28 | Femi Olanipekun | 2025-11-27 17:24 | 2025-11-27 18:05 | 2443 | 2025-11-27 17:24 | 2025-11-27 18:05 | 0:41 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Team confirmed high DG temperature, coolant was added to power the site (No diesel outage after validation) | Team confirmed high DG temperature, coolant was added to power the site (No diesel outage after validation)
NOCINC0006474464 | Internal Reconciliation | Site Down | P3 | IHS_BEN_0030V | - | - | Asaba | Edo | 3 - Low | ED0567 | SOUTH SOUTH |  | 2025-11-28 18:13 | Quadri Ogundare | 2025-11-28 18:09 | 2025-11-28 18:50 | 2436 | 2025-11-28 18:09 | 2025-11-28 18:50 | 0:41 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | Airtel NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak starter battery, external battery was used to power site. | Weak starter battery, external battery was used to power site.
NOCINC0006451922 | External Reconciliation | Site Down | P1 | IHS_OSU_0801A | T3087 | IBD | Ibadan | Osun | 3 - Low | OS0765 | WEST |  | 2025-11-25 21:09 | Osarieme Charles | 2025-11-25 21:02 | 2025-11-25 21:43 | 2436 | 2025-11-25 21:02 | 2025-11-25 21:43 | 0:41 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | Airtel NG, MTN NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 8 | DG-Grid synchronisation failure due to unstable grid supply, Dg powered manually
NOCINC0006460955 | External Reconciliation | Site Down | P2 | IHS_OSU_0929A | OS2725 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 22:05 | Victor Otugo | 2025-11-26 22:03 | 2025-11-26 22:43 | 2435 | 2025-11-26 22:03 | 2025-11-26 22:43 | 0:41 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | DG lost compression another engine was swapped
NOCINC0006468641 | External Reconciliation | Site Down | P4 | IHS_KWA_0913A | KW3124 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 23:32 | Osarieme Charles | 2025-11-27 23:29 | 2025-11-28 00:10 | 2433 | 2025-11-27 23:29 | 2025-11-28 00:10 | 0:41 | IPT | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 1 / 1 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG-Grid synchronisation failure due to Grid incomplete Phase, Dg powered manually
NOCINC0006482991 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1189H | ED2066 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 21:12 | Muhammed Hashirudeen | 2025-11-29 21:12 | 2025-11-29 21:52 | 2432 | 2025-11-29 21:12 | 2025-11-29 21:52 | 0:41 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG under voltage, AVR was adjusted (No diesel outage after validation)
NOCINC0006490194 | Resolved | Site Down | P2 | IHS_ANA_1416H | AN0708 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 22:41 | Kehinde Akinbowale | 2025-11-30 22:36 | 2025-11-30 23:17 | 2431 | 2025-11-30 22:36 | 2025-11-30 23:17 | 0:41 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on(No diesel outage after validation) | Faulty injector pump was worked on(No diesel outage after validation)
NOCINC0006481731 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0928B | DL3323 | ASB | Asaba | Delta | 3 - Low | DL0890 | SOUTH SOUTH |  | 2025-11-29 17:23 | Ayokunle Samuel | 2025-11-29 17:22 | 2025-11-29 18:03 | 2428 | 2025-11-29 17:22 | 2025-11-29 18:03 | 0:40 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 2 / 2 | MTN NG, Airtel NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty kick starter was worked on. (No diesel outage after validation) | Faulty kick starter was worked on. (No diesel outage after validation)
NOCINC0006452056 | External Reconciliation | Site Down | P1 | IHS_EKI_0739A | T3704 | IBD | Ibadan | Ekiti | 3 - Low | EK0399 | WEST |  | 2025-11-25 21:34 | Ihuoma Opurum | 2025-11-25 21:33 | 2025-11-25 22:13 | 2427 | 2025-11-25 21:33 | 2025-11-25 22:13 | 0:40 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 2 / 2 | MTN NG, Airtel NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Start failure alarm due to weak crank battery. Alarm was cleared.
NOCINC0006477451 | Internal Reconciliation | Site Down | P4 | IHS_OND_0897A | OD2401 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 06:42 | Iyesioluwa Ola | 2025-11-29 06:41 | 2025-11-29 07:21 | 2426 | 2025-11-29 06:41 | 2025-11-29 07:21 | 0:40 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Oluwaseun Awolope |  |  | Ibrahim Akinpelu | Oluwaseun Awolope |  | John Momoh | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure was reset
NOCINC0006484482 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1053A | OY2956 | IBD | Ibadan | Oyo | 3 - Low | OY1693 | WEST |  | 2025-11-30 04:15 | Mutmainnah Saba | 2025-11-30 04:11 | 2025-11-30 04:51 | 2425 | 2025-11-30 04:11 | 2025-11-30 04:51 | 0:40 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Olalekan Saheed | Adewale Adejumo | Adewale Adejumo | Ogbuma Oluwafemi | Adekanmi Ajayi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Failed rectifier module was reset
NOCINC0006478722 | Internal Reconciliation | Site Down | P3 | IHS_DEL_0952A | T2607 | ASB | Asaba | Delta | 3 - Low | DL1041 | SOUTH SOUTH |  | 2025-11-29 10:48 | Ayokunle Samuel | 2025-11-29 10:48 | 2025-11-29 11:28 | 2413 | 2025-11-29 10:48 | 2025-11-29 11:28 | 0:40 | Tyllium NGA | Equipment Repair | Passive | Control Panel | Circuit Breaker Tripped | 2 / 2 | Airtel NG, MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Tripped breaker was energized. (No diesel outage after validation). | Tripped breaker was energized. (No diesel outage after validation).
NOCINC0006445456 | External Reconciliation | Site Down | P4 | IHS_WAR_0766C | DL0543 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 05:54 | Quadri Ogundare | 2025-11-25 05:54 | 2025-11-25 06:34 | 2412 | 2025-11-25 05:54 | 2025-11-25 06:34 | 0:40 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid sync failure due to flat DG battery, external battery was used to power site | Hybrid sync failure due to flat DG battery, external battery was used to power site
NOCINC0006450518 | External Reconciliation | Site Down | P3 | IHS_OND_0891A | OD2405 | IBD | Ibadan | Ondo | 3 - Low | ON0672 | WEST |  | 2025-11-25 17:30 | Mary Elaigwu | 2025-11-25 17:28 | 2025-11-25 18:08 | 2407 | 2025-11-25 17:28 | 2025-11-25 18:08 | 0:40 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Over Frequency | 2 / 2 | MTN NG, Airtel NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 2 | DG over frequency alarm was cleared
NOCINC0006468097 | External Reconciliation | Site Down | P1 | IHS_OND_0925A | OD2519 | IBD | Ibadan | Ondo | 3 - Low | ON0695 | WEST |  | 2025-11-27 21:36 | Mary Elaigwu | 2025-11-27 21:34 | 2025-11-27 22:14 | 2400 | 2025-11-27 21:34 | 2025-11-27 22:14 | 0:40 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 2 / 2 | Airtel NG, MTN NG |  | Oluwaseun Awolope |  |  | Ibrahim Akinpelu | Oluwaseun Awolope |  | John Momoh | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting fse passive update
NOCINC0006488640 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1027A | AN0061 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 17:21 | Aderonke Olowojoba | 2025-11-30 17:17 | 2025-11-30 17:57 | 2400 | 2025-11-30 17:17 | 2025-11-30 17:57 | 0:40 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 1 / 1 | MTN NG |  | Ugochuku Agbamuche | Ugo Agamuche | Ugo Agamuche | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low Oil Pressure, Oil was added(No diesel outage after validation) | Low Oil Pressure, Oil was added(No diesel outage after validation)
NOCINC0006471023 | Internal Reconciliation | Site Down | P2 | IHS_ILO_0065C | KW4737 | IBD | Ibadan | Kwara | 3 - Low | KW0486 | WEST |  | 2025-11-28 09:42 | Praise Okezie | 2025-11-28 09:40 | 2025-11-28 10:20 | 2399 | 2025-11-28 09:40 | 2025-11-28 10:20 | 0:40 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty AVR was adjusted
NOCINC0006477295 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1119A | AN0681 | ASB | Asaba | Anambra | 3 - Low | AN0854 | SOUTH EAST |  | 2025-11-29 05:58 | Akachukwu Ugwu | 2025-11-29 05:53 | 2025-11-29 06:32 | 2398 | 2025-11-29 05:53 | 2025-11-29 06:32 | 0:40 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 2 | Airtel NG |  | ThankGod Amadi | Femi Balogun | Femi Balogun | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low DG frequency, governor was adjusted (No diesel outage after validation)
NOCINC0006454732 | External Reconciliation | Site Down | P2 | IHS_OYO_0904A | T3561 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 02:31 | Aishat Oyedeji | 2025-11-26 02:30 | 2025-11-26 03:10 | 2395 | 2025-11-26 02:30 | 2025-11-26 03:10 | 0:40 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Voltage fluctuation due to no BUB, GG auto-restarted.
NOCINC0006485493 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0959A | ED2030 | IBD | Asaba | Edo | 3 - Low | ED0492 | SOUTH SOUTH |  | 2025-11-30 09:07 | Evelyn Emagurehor | 2025-11-30 09:06 | 2025-11-30 09:46 | 2383 | 2025-11-30 09:06 | 2025-11-30 09:46 | 0:40 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | MTN NG, Airtel NG |  | Edwin Emehian | Achebe Chigozie | Omoragbon Austin | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Failed rectifier, CSU was reset. (No diesel outage after validation). | Failed rectifier, CSU was reset. (No diesel outage after validation).
NOCINC0006469635 | External Reconciliation | Site Down | P2 | IHS_WAR_0906H | - | - | Asaba | Delta | 3 - Low | DL0248 | SOUTH SOUTH |  | 2025-11-28 03:39 | Patrick Okoro | 2025-11-28 03:38 | 2025-11-28 04:18 | 2378 | 2025-11-28 03:38 | 2025-11-28 04:18 | 0:40 | Tyllium NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Smile, Airtel NG |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | WeaK DG was primed to start | WeaK DG was primed to start
NOCINC0006459068 | External Reconciliation | Site Down | P3 | IHS_BEN_0731E | ED5199 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 16:31 | Azeezat Badmus | 2025-11-26 16:28 | 2025-11-26 17:07 | 2376 | 2025-11-26 16:28 | 2025-11-26 17:07 | 0:40 | MPI NGA | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Olusoji Megbodofo |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006447507 | External Reconciliation | Site Down | P1 | IHS_DEL_0952A | T2607 | ASB | Asaba | Delta | 3 - Low | DL1041 | SOUTH SOUTH |  | 2025-11-25 11:13 | Ezinne Ubachukwu | 2025-11-25 11:11 | 2025-11-25 11:50 | 2376 | 2025-11-25 11:11 | 2025-11-25 11:50 | 0:40 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 64 | Tripped DG Breaker was energized
NOCINC0006477174 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1074A | DL0441 | ASB | Asaba | Delta | 3 - Low | DL0847 | SOUTH SOUTH |  | 2025-11-29 05:06 | Femi Olanipekun | 2025-11-29 05:04 | 2025-11-29 05:44 | 2374 | 2025-11-29 05:04 | 2025-11-29 05:44 | 0:40 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | DG under frequency, governor was adjusted to restore the site (No diesel outage after validation) | DG under frequency, governor was adjusted to restore the site (No diesel outage after validation)
NOCINC0006437192 | External Reconciliation | Site Down | P2 | IHS_ANA_1243C | AN0958 | ASB | Asaba | Anambra | 3 - Low | AN0812 | SOUTH EAST |  | 2025-11-24 01:17 | Gbemisola Adedeji | 2025-11-24 01:14 | 2025-11-24 01:54 | 2371 | 2025-11-24 01:14 | 2025-11-24 01:54 | 0:40 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Anwah Chike |  |  | Erik Nwodo | Nwigbo Chijioke |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization failure was reset. DG was powered Manually (No diesel outage after validation). | Hybrid synchronization failure was reset. DG was powered Manually (No diesel outage after validation).
NOCINC0006450759 | External Reconciliation | Site Down | P2 | IHS_OSU_0772A | T3024 | IBD | Ibadan | Osun | 3 - Low | OS0768 | WEST |  | 2025-11-25 18:18 | Hardy Oko | 2025-11-25 18:15 | 2025-11-25 18:55 | 2370 | 2025-11-25 18:15 | 2025-11-25 18:55 | 0:40 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Contactor | 2 / 2 | Airtel NG, MTN NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | failed load contactor, dg powered manually
NOCINC0006460113 | External Reconciliation | Site Down | P2 | IHS_OND_0027B | OD4755 | IBD | Ibadan | Osun | 3 - Low | ON0568 | WEST |  | 2025-11-26 19:35 | Iyesioluwa Ola | 2025-11-26 19:34 | 2025-11-26 20:14 | 2361 | 2025-11-26 19:34 | 2025-11-26 20:14 | 0:39 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Olatunde Babatunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | High engine temperature due to low coolant level, coolant was added
NOCINC0006469592 | External Reconciliation | Site Down | P3 | IHS_ILO_0020B | KW4554 | IBD | Ibadan | Kwara | 3 - Low | KW0563 | WEST |  | 2025-11-28 03:12 | Osarieme Charles | 2025-11-28 03:09 | 2025-11-28 03:48 | 2360 | 2025-11-28 03:09 | 2025-11-28 03:48 | 0:39 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | MTN NG, Airtel NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Burst DG Battery was disconnected
NOCINC0006440203 | External Reconciliation | Site Down | P3 | IHS_OYO_1424B | - | - | Ibadan | Oyo | 3 - Low | OY1305 | WEST |  | 2025-11-24 13:12 | Aishat Oyedeji | 2025-11-24 13:08 | 2025-11-24 13:48 | 2359 | 2025-11-24 13:08 | 2025-11-24 13:48 | 0:39 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | Airtel NG |  | Azeez Yusuf | John Eze | John Eze | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | failed rectifier module was reset
NOCINC0006459213 | External Reconciliation | Site Down | P3 | IHS_ILO_0058C | KW4689 | IBD | Ibadan | Kwara | 3 - Low | KW0514 | WEST |  | 2025-11-26 16:57 | Titus Tosin | 2025-11-26 16:57 | 2025-11-26 17:36 | 2357 | 2025-11-26 16:57 | 2025-11-26 17:36 | 0:39 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled.
NOCINC0006465247 | External Reconciliation | Site Down | P2 | IHS_OSU_0953A | OS4274 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 13:53 | Mutmainnah Saba | 2025-11-27 13:51 | 2025-11-27 14:30 | 2355 | 2025-11-27 13:51 | 2025-11-27 14:30 | 0:39 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006460547 | External Reconciliation | Site Down | P1 | IHS_WAR_0908H | DL0044 | ASB | Asaba | Delta | 3 - Low | DL0411 | SOUTH SOUTH | Cascaded Incident from TTO6744823 - Cascade Removed From TTO6744823 | 2025-11-26 20:44 | Ezinne Ubachukwu | 2025-11-26 20:37 | 2025-11-26 21:16 | 2354 | 2025-11-26 20:37 | 2025-11-26 21:16 | 0:39 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 3 / 3 | MTN NG, Smile, Airtel NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty water pump temporary worked on pending replacement (No diesel outage after validation) | Faulty water pump temporary worked on pending replacement (No diesel outage after validation)
NOCINC0006466169 | External Reconciliation | Site Down | P4 | IHS_EDO_1071C | ED6141 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 15:57 | Muhammed Hashirudeen | 2025-11-27 15:57 | 2025-11-27 16:36 | 2353 | 2025-11-27 15:57 | 2025-11-27 16:36 | 0:39 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 1 / 1 | MTN NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty kick starter was worked on (No diesel outage after validation) | Faulty kick starter was worked on (No diesel outage after validation)
NOCINC0006455302 | External Reconciliation | Site Down | P2 | IHS_OND_1100B | OD2536 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 06:29 | Testimony Akinyemi | 2025-11-26 06:26 | 2025-11-26 07:05 | 2350 | 2025-11-26 06:26 | 2025-11-26 07:05 | 0:39 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 1 / 1 | MTN NG |  | John Kunamon |  |  | Ibrahim Akinpelu | John Kunamon |  | Fagbemi Solomon | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty kick starter was worked on
NOCINC0006488755 | Internal Reconciliation | Site Down | P3 | IHS_DEL_0995A | DL2675 | ASB | Asaba | Delta | 3 - Low | DL0871 | SOUTH SOUTH |  | 2025-11-30 17:42 | Ezinne Ubachukwu | 2025-11-30 17:40 | 2025-11-30 18:19 | 2346 | 2025-11-30 17:40 | 2025-11-30 18:19 | 0:39 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | Airtel NG, MTN NG |  | Eno Eyon |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Dg high temperature. Coolant was added (No diesel outage after validation) | Dg high temperature. Coolant was added (No diesel outage after validation)
NOCINC0006474324 | Internal Reconciliation | Site Down | P3 | IHS_OSU_1035H | OS4263 | IBD | Ibadan | Osun | 3 - Low | OS0894 | WEST |  | 2025-11-28 17:52 | Valentine Adinnu | 2025-11-28 17:50 | 2025-11-28 18:29 | 2345 | 2025-11-28 17:50 | 2025-11-28 18:29 | 0:39 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Adejumobi Tunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Burnt rectifier module replaced | Burnt rectifier module replaced
NOCINC0006436560 | External Reconciliation | Site Down | P4 | IHS_ANA_1040A | AN0030 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 00:19 | Uthman Akinola | 2025-11-24 00:16 | 2025-11-24 00:55 | 2341 | 2025-11-24 00:16 | 2025-11-24 00:55 | 0:39 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 1 / 1 | MTN NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Frozen Rectifier CSU was reset (no diesel outage after validation)
NOCINC0006470862 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0071B | OS4380 | IBD | Ibadan | Osun | 3 - Low | OS0864 | WEST |  | 2025-11-28 09:17 | Mutmainnah Saba | 2025-11-28 09:15 | 2025-11-28 09:54 | 2340 | 2025-11-28 09:15 | 2025-11-28 09:54 | 0:39 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | Airtel NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Tripped load breaker was replaced
NOCINC0006457114 | External Reconciliation | Site Down | P2 | IHS_OSU_0961A | OS4294 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 11:38 | Ifechi Ugwueze | 2025-11-26 11:36 | 2025-11-26 12:15 | 2327 | 2025-11-26 11:36 | 2025-11-26 12:15 | 0:39 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled
NOCINC0006487939 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1056A | DL0450 | ASB | Asaba | Delta | 3 - Low | DL0488 | SOUTH SOUTH |  | 2025-11-30 15:29 | Ezinne Ubachukwu | 2025-11-30 15:26 | 2025-11-30 16:05 | 2327 | 2025-11-30 15:26 | 2025-11-30 16:05 | 0:39 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | MTN NG |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Suspected passive issue, Awaiting RCA from FSE | Suspected passive issue, Awaiting RCA from FSE
NOCINC0006439496 | External Reconciliation | Site Down | P1 | IHS_EDO_0891A | T3363 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 11:20 | Evelyn Emagurehor | 2025-11-24 11:17 | 2025-11-24 11:31 | 868 | 2025-11-24 11:17 | 2025-11-24 11:55 | 0:39 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed rectifier module was reset (No diesel outage after validation) | Failed rectifier module was reset (No diesel outage after validation)
NOCINC0006466343 | External Reconciliation | Site Down | P4 | IHS_OSU_0888A | T3830 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 16:24 | Mutmainnah Saba | 2025-11-27 16:18 | 2025-11-27 16:57 | 2325 | 2025-11-27 16:18 | 2025-11-27 16:57 | 0:39 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006446758 | External Reconciliation | Site Down | P2 | IHS_OYO_1065A | OY4048 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 09:59 | Precious Attah | 2025-11-25 09:58 | 2025-11-25 10:36 | 2320 | 2025-11-25 09:58 | 2025-11-25 10:36 | 0:39 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Olapo Adebunmi |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Weak DG was primed to start
NOCINC0006438858 | External Reconciliation | Site Down | P2 | IHS_OND_0894A | OD2408 | IBD | Ibadan | Ondo | 3 - Low | ON0706 | WEST |  | 2025-11-24 09:25 | Yewande Adeagbo | 2025-11-24 09:24 | 2025-11-24 10:03 | 2318 | 2025-11-24 09:24 | 2025-11-24 10:03 | 0:39 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty Injector Pump Worked On
NOCINC0006458752 | External Reconciliation | Site Down | P3 | IHS_EDO_0749A | T0218 | IBD | Asaba | Edo | 3 - Low | ED0700 | SOUTH SOUTH |  | 2025-11-26 15:38 | Azeezat Badmus | 2025-11-26 15:37 | 2025-11-26 16:15 | 2315 | 2025-11-26 15:37 | 2025-11-26 16:15 | 0:39 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Outage Issue | 2 / 2 | MTN NG, Airtel NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | delay in grid synchronization due to weak bub, DG powered manaully (No diesel ouatge after validation) (No diesel ouatge after validation)
NOCINC0006477225 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0774A | T0090 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 05:25 | Bosede Kutelu | 2025-11-29 05:20 | 2025-11-29 05:58 | 2312 | 2025-11-29 05:20 | 2025-11-29 05:58 | 0:39 | SPS | Fuel Outage (Probable) | Passive | Diesel | Fuel Line Issue | 2 / 3 | MTN NG, Smile |  | BASHIR ABDULRASAQ | Yusuf Gyang |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Blocked Fuel Line was flushed
NOCINC0006488171 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0925B | DL3319 | ASB | Asaba | Delta | 3 - Low | DL0700 | SOUTH SOUTH |  | 2025-11-30 16:09 | Ayomide Akindolie | 2025-11-30 16:09 | 2025-11-30 16:47 | 2308 | 2025-11-30 16:09 | 2025-11-30 16:47 | 0:38 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Hooked injector pump was worked on (No diesel outage after validation) | Hooked injector pump was worked on (No diesel outage after validation)
NOCINC0006445664 | External Reconciliation | Site Down | P1 | IHS_AGB_0005B | DL0430 | ASB | Asaba | Delta | 3 - Low | DL0522 | SOUTH SOUTH |  | 2025-11-25 07:06 | Solomon Bankole | 2025-11-25 07:03 | 2025-11-25 07:40 | 2244 | 2025-11-25 07:03 | 2025-11-25 07:41 | 0:38 | Tyllium NGA | Site Asset Theft | Theft | Theft | Generator Battery Theft | 2 / 2 | MTN NG, Airtel NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Dg starter battery theft. external battery was used to power site. ( No diesel outage after validation) | Dg starter battery theft. external battery was used to power site. ( No diesel outage after validation)
NOCINC0006473881 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 16:50 | Uthman Akinola | 2025-11-28 16:44 | 2025-11-28 17:22 | 2302 | 2025-11-28 16:44 | 2025-11-28 17:22 | 0:38 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | High Engine Temp, Coolant added and Radiator Flushed. (No diesel outage after validation)
NOCINC0006467707 | External Reconciliation | Site Down | P4 | IHS_EDO_0738E | ED5369 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 20:24 | Mary Odefemi | 2025-11-27 20:20 | 2025-11-27 20:58 | 2300 | 2025-11-27 20:20 | 2025-11-27 20:58 | 0:38 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 1 / 1 | MTN NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty solenoid coil was worked on
NOCINC0006477875 | Internal Reconciliation | Site Down | P4 | IHS_DEL_0942A | T2916 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 08:34 | Ayokunle Samuel | 2025-11-29 08:34 | 2025-11-29 09:12 | 2300 | 2025-11-29 08:34 | 2025-11-29 09:12 | 0:38 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Speed | 1 / 1 | MTN NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG under speed alarm was cleared, Governor was adjusted ( No diesel outage after validation) | DG under speed alarm was cleared, Governor was adjusted ( No diesel outage after validation)
NOCINC0006463614 | External Reconciliation | Site Down | P2 | IHS_EDO_0747A | T0161 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 10:12 | Muhammed Hashirudeen | 2025-11-27 10:12 | 2025-11-27 10:50 | 2293 | 2025-11-27 10:12 | 2025-11-27 10:50 | 0:38 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset (No diesel outage after validation) | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006479305 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0936A | T2991 | ASB | Asaba | Delta | 3 - Low | DL0750 | SOUTH SOUTH |  | 2025-11-29 12:01 | Ayomide Akindolie | 2025-11-29 11:58 | 2025-11-29 12:36 | 2292 | 2025-11-29 11:58 | 2025-11-29 12:36 | 0:38 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 2 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Low DG frequency, governor was adjusted (No diesel outage after validation)
NOCINC0006444450 | External Reconciliation | Site Down | P1 | IHS_EKI_0854A | EK2262 | IBD | Ibadan | Ekiti | 3 - Low | EK0427 | WEST |  | 2025-11-24 22:44 | Kandervil Uwah | 2025-11-24 22:44 | 2025-11-24 23:22 | 2287 | 2025-11-24 22:44 | 2025-11-24 23:22 | 0:38 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Solomon Manchan |  |  | Ibrahim Akinpelu | Solomon Manchan |  | Ismail Hammed | Ibrahim Yekini | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG under voltage alarm was cleared
NOCINC0006447904 | External Reconciliation | Site Down | P1 | IHS_OND_0972A | OD4737 | IBD | Ibadan | Ondo | 3 - Low | ON0597 | WEST |  | 2025-11-25 12:06 | Mary Elaigwu | 2025-11-25 12:05 | 2025-11-25 12:43 | 2281 | 2025-11-25 12:05 | 2025-11-25 12:43 | 0:38 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Control Panel | 2 / 2 | MTN NG, Airtel NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty control panel was worked on
NOCINC0006477748 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0017B | DL0487 | ASB | Asaba | Delta | 3 - Low | DL0618 | SOUTH SOUTH |  | 2025-11-29 07:59 | Mary Odefemi | 2025-11-29 07:55 | 2025-11-29 08:33 | 2281 | 2025-11-29 07:55 | 2025-11-29 08:33 | 0:38 | BJ Bison NGA | Equipment Repair | Passive | Control Panel | ATS Relay Faulty | 2 / 2 | MTN NG, Airtel NG |  | Emuesiri� Sunday |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty ATS contactor was manually energized (No diesel outage after validation)
NOCINC0006447832 | External Reconciliation | Site Down | P4 | IHS_DEL_1149A | DL0635 | ASB | Asaba | Delta | 3 - Low | DL0723 | SOUTH SOUTH |  | 2025-11-25 11:54 | Tracy Osarumwense | 2025-11-25 11:54 | 2025-11-25 12:32 | 2281 | 2025-11-25 11:54 | 2025-11-25 12:32 | 0:38 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | Airtel NG, MTN NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG High Temperature due to low Coolant level, Coolant was added. | DG High Temperature due to low Coolant level, Coolant was added.(No diesel outage after validation).
NOCINC0006449787 | External Reconciliation | Site Down | P1 | IHS_WAR_0898H | DL0376 | ASB | Asaba | Delta | 3 - Low | DL0606 | SOUTH SOUTH |  | 2025-11-25 16:02 | Oluwatobiloba Are | 2025-11-25 16:02 | 2025-11-25 16:40 | 2281 | 2025-11-25 16:02 | 2025-11-25 16:40 | 0:38 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Kevwe Oshoture |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | DG high temperature due to low coolant level, coolant was added | DG high temperature due to low coolant level, coolant was added. (No diesel outage after validation).
NOCINC0006482868 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0928C | KW4703 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-29 20:52 | Okusanya Joseph | 2025-11-29 20:50 | 2025-11-29 21:28 | 2274 | 2025-11-29 20:50 | 2025-11-29 21:28 | 0:38 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 1 / 1 | MTN NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | faulty fuel pump was worked on
NOCINC0006466225 | External Reconciliation | Site Down | P3 | IHS_OYO_1005A | OY2845 | IBD | Ibadan | Oyo | 3 - Low | OY1148 | WEST |  | 2025-11-27 16:03 | Oluwatomisin Ogunleye | 2025-11-27 16:02 | 2025-11-27 16:40 | 2272 | 2025-11-27 16:02 | 2025-11-27 16:40 | 0:38 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Oluwaseun Alaba |  |  | Paul Akpomie | Oluwaseun Alaba |  | Luke Eke | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen SMU, SMU was reset.
NOCINC0006445747 | External Reconciliation | Site Down | P1 | IHS_DEL_0910A | T2732 | ASB | Asaba | Delta | 3 - Low | DL0775 | SOUTH SOUTH |  | 2025-11-25 07:18 | Solomon Bankole | 2025-11-25 07:17 | 2025-11-25 07:55 | 2270 | 2025-11-25 07:17 | 2025-11-25 07:55 | 0:38 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | MTN NG, Airtel NG |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Frozen orion was reset (No diesel outage after validation) | Frozen orion was reset (No diesel outage after validation)
NOCINC0006456044 | External Reconciliation | Site Down | P1 | IHS_EDO_1028A | ED4923 | IBD | Asaba | Edo | 3 - Low | ED1071 | South South |  | 2025-11-26 08:49 | Azeezat Badmus | 2025-11-26 08:48 | 2025-11-26 09:26 | 2269 | 2025-11-26 08:48 | 2025-11-26 09:26 | 0:38 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 3 | MTN NG |  | EKPU SUNDAY |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty AVR was worked on (No diesel outage after validation)
NOCINC0006443894 | External Reconciliation | Site Down | P4 | IHS_OYO_0942A | T3597 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 21:11 | Valentine Adinnu | 2025-11-24 21:09 | 2025-11-24 21:47 | 2265 | 2025-11-24 21:09 | 2025-11-24 21:47 | 0:38 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | MTN NG |  | Effiong Asukwo |  |  | Paul Akpomie | Effiong Asukwo |  | Victor Olanrewaju | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled | Tripped load breaker was enabled
NOCINC0006478657 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0755A | T0230 | IBD | Asaba | Edo | 3 - Low | ED0450 | SOUTH SOUTH |  | 2025-11-29 10:39 | Evelyn Emagurehor | 2025-11-29 10:37 | 2025-11-29 11:15 | 2260 | 2025-11-29 10:37 | 2025-11-29 11:15 | 0:38 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 3 / 3 | MTN NG, Smile, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 7 | Faulty ATS contactor was worked on (No diesel outage after validation).
NOCINC0006449199 | External Reconciliation | Site Down | P3 | IHS_WAR_0004B | - | - | Asaba | Delta | 3 - Low | DL0394 | SOUTH SOUTH |  | 2025-11-25 14:41 | Oluwatobiloba Are | 2025-11-25 14:41 | 2025-11-25 15:19 | 2253 | 2025-11-25 14:41 | 2025-11-25 15:19 | 0:38 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | Airtel NG |  | Babatunde Jimoh� |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed charging alternator was excited | Failed charging alternator was excited
NOCINC0006445767 | External Reconciliation | Site Down | P1 | IHS_ANA_1001A | T4870 | ASB | Asaba | Anambra | 3 - Low | AN0530 | SOUTH EAST |  | 2025-11-25 07:20 | Solomon Bankole | 2025-11-25 07:18 | 2025-11-25 07:56 | 2252 | 2025-11-25 07:18 | 2025-11-25 07:56 | 0:38 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Emergency Stop | 2 / 2 | MTN NG, Airtel NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | emergency stop alarm was cleared (No diesel outage after validation) | emergency stop alarm was cleared (No diesel outage after validation)
NOCINC0006489020 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0782C | DL1020 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 18:26 | Ayomide Akindolie | 2025-11-30 18:25 | 2025-11-30 19:03 | 2248 | 2025-11-30 18:25 | 2025-11-30 19:03 | 0:37 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Urhoma Joseph | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty Injector pump was worked on. | Faulty Injector pump was worked on. (No diesel outage after validation).
NOCINC0006454693 | External Reconciliation | Site Down | P2 | IHS_KWA_1000H | KW4605 | IBD | Ibadan | Kwara | 3 - Low | KW0489 | WEST |  | 2025-11-26 02:06 | Azeezat Adekunle | 2025-11-26 02:02 | 2025-11-26 02:39 | 2246 | 2025-11-26 02:02 | 2025-11-26 02:39 | 0:37 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 2 / 2 | MTN NG, Airtel NG |  | Afolabi Ganiyyu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty solenoid coil was worked on
NOCINC0006480518 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0937A | OS2706 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-29 14:29 | Favour Ahize | 2025-11-29 14:26 | 2025-11-29 15:03 | 2243 | 2025-11-29 14:26 | 2025-11-29 15:03 | 0:37 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Adejumobi Tunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | PPM (generator servicing) was done at site.
NOCINC0006458830 | External Reconciliation | Site Down | P1 | IHS_ANA_1065A | AN0202 | ASB | Asaba | Anambra | 3 - Low | AN0827 | SOUTH EAST |  | 2025-11-26 15:48 | Akachukwu Ugwu | 2025-11-26 15:46 | 2025-11-26 16:24 | 2241 | 2025-11-26 15:46 | 2025-11-26 16:24 | 0:37 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Oladele Segun | David Ndubuisi | David Ndubuisi | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | DG under frequency, governor was adjusted (No diesel outage after validation). | DG under frequency, governor was adjusted (No diesel outage after validation).
NOCINC0006457371 | External Reconciliation | Site Down | P3 | IHS_EDO_1245B | ED5509 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 12:17 | Oluwatobiloba Are | 2025-11-26 12:13 | 2025-11-26 13:32 | 4734 | 2025-11-26 12:55 | 2025-11-26 13:32 | 0:37 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Suspected passive, Awaiting update from FSE
NOCINC0006454836 | External Reconciliation | Site Down | P3 | IHS_WAR_0953B | DL3351 | ASB | Asaba | Delta | 3 - Low | DL0653 | SOUTH SOUTH |  | 2025-11-26 03:24 | Ayomide Akindolie | 2025-11-26 03:23 | 2025-11-26 04:01 | 2235 | 2025-11-26 03:23 | 2025-11-26 04:01 | 0:37 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | Airtel NG |  | David Uja |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled (No diesel outage after validation)
NOCINC0006444482 | External Reconciliation | Site Down | P1 | IHS_IBA_0099C | OY4157 | IBD | Ibadan | Oyo | 3 - Low | OY1034 | WEST |  | 2025-11-24 22:50 | Damilola Paseda | 2025-11-24 22:48 | 2025-11-24 23:26 | 2233 | 2025-11-24 22:48 | 2025-11-24 23:26 | 0:37 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | MTN NG, Airtel NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Hybrid Synchronization failure due to weak crank battery, external battery was used to power site. | Hybrid Synchronization failure due to weak crank battery, external battery was used to power site.
NOCINC0006437669 | External Reconciliation | Site Down | P2 | IHS_ILO_0005V | KW4728 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 04:16 | Okusanya Joseph | 2025-11-24 04:16 | 2025-11-24 04:53 | 2229 | 2025-11-24 04:16 | 2025-11-24 04:53 | 0:37 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 2 | MTN NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Flat dg battery external battery was used
NOCINC0006487286 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0921B | EK6303 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-30 13:47 | Ihuoma Opurum | 2025-11-30 13:47 | 2025-11-30 14:24 | 2224 | 2025-11-30 13:47 | 2025-11-30 14:24 | 0:37 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Weak crank battery. An external battery was used to power site.
NOCINC0006439700 | External Reconciliation | Site Down | P3 | IHS_OND_1131B | - | - | Ibadan | Ondo | 3 - Low | ON0805 | WEST |  | 2025-11-24 12:11 | Ihuoma Opurum | 2025-11-24 12:04 | 2025-11-24 12:41 | 2222 | 2025-11-24 12:04 | 2025-11-24 12:41 | 0:37 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 1 / 1 | Airtel NG |  | Sanusi Idowu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | faulty radiator worked on
NOCINC0006484958 | Internal Reconciliation | Site Down | P4 | IHS_OND_0063B | OD4807 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 06:55 | Abisoye Olaleye | 2025-11-30 06:52 | 2025-11-30 07:29 | 2221 | 2025-11-30 06:52 | 2025-11-30 07:29 | 0:37 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Usman Hammed |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | hybrid synchronization failure due to frozen csu, csu was reset.
NOCINC0006458793 | External Reconciliation | Site Down | P2 | IHS_ANA_0843A | T4140 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 15:43 | Femi Olanipekun | 2025-11-26 15:43 | 2025-11-26 16:20 | 2215 | 2025-11-26 15:43 | 2025-11-26 16:20 | 0:37 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Team confirmed high DG temperature, coolant was added to power the site (No diesel outage after validation) | Team confirmed high DG temperature, coolant was added to power the site (No diesel outage after validation)
NOCINC0006445927 | External Reconciliation | Site Down | P4 | IHS_DEL_1186A | DL0488 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 08:10 | Azeezat Badmus | 2025-11-25 08:07 | 2025-11-25 08:44 | 2211 | 2025-11-25 08:07 | 2025-11-25 08:44 | 0:37 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed Charging Alternator was excited. | Failed Charging Alternator was excited. (No diesel outage after validation).
NOCINC0006488125 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0929A | T2950 | ASB | Asaba | Delta | 3 - Low | DL0580 | SOUTH SOUTH |  | 2025-11-30 16:04 | Ezinne Ubachukwu | 2025-11-30 16:01 | 2025-11-30 16:38 | 2211 | 2025-11-30 16:01 | 2025-11-30 16:38 | 0:37 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Over Frequency | 2 / 2 | MTN NG, Airtel NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | DG over frquency, Governor was adjusted (No diesel outage after validation) | DG over frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006449200 | External Reconciliation | Site Down | P3 | IHS_OND_0006B | OD4715 | IBD | Ibadan | Ondo | 3 - Low | ON0700 | WEST |  | 2025-11-25 14:41 | Oluwadara Bankole | 2025-11-25 14:38 | 2025-11-25 15:15 | 2207 | 2025-11-25 14:38 | 2025-11-25 15:15 | 0:37 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | Airtel NG |  | Obuseh Williams |  |  | Ibrahim Akinpelu | Obuseh Williams |  | Lukman Amusat | Ibrahim Yekini | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failed due to frozen SMU. Frozen SMU was reset. | Hybrid synchronization failed due to frozen SMU. Frozen SMU was reset.
NOCINC0006465407 | External Reconciliation | Site Down | P3 | IHS_OSU_0058B | OS4265 | IBD | Ibadan | Osun | 3 - Low | OS0701 | WEST |  | 2025-11-27 14:14 | Mutmainnah Saba | 2025-11-27 14:12 | 2025-11-27 14:49 | 2207 | 2025-11-27 14:12 | 2025-11-27 14:49 | 0:37 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on
NOCINC0006452752 | External Reconciliation | Site Down | P1 | IHS_WAR_0792C | DL1055 | ASB | Asaba | Delta | 3 - Low | DL0634 | SOUTH SOUTH |  | 2025-11-25 23:29 | Ayomide Akindolie | 2025-11-25 23:29 | 2025-11-26 | 1864 | 2025-11-25 23:29 | 2025-11-26 00:06 | 0:37 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Kenneth Oboniye |  |  | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty rectifier module was replaced (No diesel outage after validation)
NOCINC0006451250 | External Reconciliation | Site Down | P2 | IHS_ANA_1044A | AN0021 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 19:52 | Ezinne Ubachukwu | 2025-11-25 19:50 | 2025-11-25 20:26 | 2202 | 2025-11-25 19:50 | 2025-11-25 20:26 | 0:37 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Coolant added and Radiator flushed. (No diesel outage after validation) | Coolant added and Radiator flushed. (No diesel outage after validation)
NOCINC0006462002 | External Reconciliation | Site Down | P3 | IHS_EDO_1184H | ED2105 | IBD | Asaba | Edo | 3 - Low | ED0862 | SOUTH SOUTH |  | 2025-11-27 02:27 | Oluwatomisin Sogbesan | 2025-11-27 02:25 | 2025-11-27 03:02 | 2199 | 2025-11-27 02:25 | 2025-11-27 03:02 | 0:37 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset (No diesel outage after validation) | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006451889 | External Reconciliation | Site Down | P1 | IHS_EKI_0009B | EK2277 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-25 21:01 | Ihuoma Opurum | 2025-11-25 21:01 | 2025-11-25 21:37 | 2192 | 2025-11-25 21:01 | 2025-11-25 21:37 | 0:37 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | Oluwafemi Oluwasegun |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG undervoltage alarm was cleared and DG was powered manually.
NOCINC0006442823 | External Reconciliation | Site Down | P4 | IHS_KWA_1020B | KW6466 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 18:14 | Azeezat Adekunle | 2025-11-24 18:14 | 2025-11-24 18:50 | 2191 | 2025-11-24 18:14 | 2025-11-24 18:50 | 0:37 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset
NOCINC0006485476 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1165A | DL0627 | ASB | Asaba | Delta | 3 - Low | DL0994 | SOUTH SOUTH |  | 2025-11-30 09:01 | Ayomide Akindolie | 2025-11-30 09:01 | 2025-11-30 09:37 | 2189 | 2025-11-30 09:01 | 2025-11-30 09:37 | 0:36 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low Oil Pressure, Oil was added. | Low Oil Pressure, Oil was added. (No diesel outage after validation).
NOCINC0006471079 | Internal Reconciliation | Site Down | P1 | IHS_OSU_0829A | T3620 | IBD | Ibadan | Osun | 3 - Low | OS0664 | WEST | gNodeB Out of Service@2025-11-28 09:37:39@N3620 | 2025-11-28 09:51 | System Administrator | 2025-11-28 09:46 | 2025-11-28 10:22 | 2187 | 2025-11-28 09:46 | 2025-11-28 10:22 | 0:36 | Biswal | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Ben Johnson-Nsikan |  |  | Abiola Adegbiji | Babalola Babajide |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | PPM was carried out at the site with IHSREF/25110413472911844726 | PPM was carried out at the site with IHSREF/25110413472911844726
NOCINC0006446896 | External Reconciliation | Site Down | P4 | IHS_WAR_0776C | DL0650 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 10:12 | Tracy Osarumwense | 2025-11-25 10:12 | 2025-11-25 10:48 | 2184 | 2025-11-25 10:12 | 2025-11-25 10:48 | 0:36 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 1 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Name: Joshua bulus Company: GAIOsystems Purpose: RMS REINSTALLATION Date :25/11/2025 Site Id:IHS_WAR_0776C IHSREF/25112416270706458415 SARID0009029020 | Name: Joshua bulus Company: GAIOsystems Purpose: RMS REINSTALLATION Date :25/11/2025 Site Id:IHS_WAR_0776C IHSREF/25112416270706458415 SARID0009029020
NOCINC0006468448 | External Reconciliation | Site Down | P2 | IHS_OSU_0838A | T3611 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 22:34 | Ifechi Ugwueze | 2025-11-27 22:33 | 2025-11-27 23:09 | 2180 | 2025-11-27 22:33 | 2025-11-27 23:09 | 0:36 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 1 / 1 | MTN NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 4 | Faulty fuel pump was worked on
NOCINC0006463704 | External Reconciliation | Site Down | P1 | IHS_DEL_0765A | T0154 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 10:29 | Bukola Olabanji | 2025-11-27 10:27 | 2025-11-27 11:03 | 2176 | 2025-11-27 10:27 | 2025-11-27 11:03 | 0:36 | BJ Bison NGA | Equipment Repair | Passive | Infrastructure | Armoured Cable | 1 / 1 | MTN NG |  | Babatunde Jimoh� |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Faulty amoured cable was replaced
NOCINC0006439207 | External Reconciliation | Site Down | P1 | IHS_DEL_1144A | DL0757 | ASB | Asaba | Delta | 3 - Low | DL0648 | SOUTH SOUTH |  | 2025-11-24 10:19 | Ayokunle Samuel | 2025-11-24 10:18 | 2025-11-24 10:55 | 2174 | 2025-11-24 10:18 | 2025-11-24 10:55 | 0:36 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty charging alternator was worked on to restore the site. (No diesel outage after validation) | Faulty charging alternator was worked on to restore the site. (No diesel outage after validation)
NOCINC0006446092 | External Reconciliation | Site Down | P4 | IHS_OSU_0026B | OS4289 | IBD | Ibadan | Osun | 3 - Low | OS0601 | WEST | BTS O&M LINK FAILURE@2025-11-25 08:06:18@OS0601 | 2025-11-25 08:51 | System Administrator | 2025-11-25 08:06 | 2025-11-25 08:42 | 2171 | 2025-11-25 08:06 | 2025-11-25 08:42 | 0:36 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006483716 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0937A | ED3318 | IBD | Asaba | Edo | 3 - Low | ED0375 | SOUTH SOUTH |  | 2025-11-29 23:18 | Bukola Olabanji | 2025-11-29 23:18 | 2025-11-29 23:54 | 2166 | 2025-11-29 23:18 | 2025-11-29 23:54 | 0:36 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | Samuel Asukwo |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Low oil alarm cleared, oil top-up completed at site
NOCINC0006459706 | External Reconciliation | Site Down | P4 | IHS_BEN_0078C | ED5153 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 18:26 | Emmanuel Faleti | 2025-11-26 18:26 | 2025-11-26 19:02 | 2165 | 2025-11-26 18:26 | 2025-11-26 19:02 | 0:36 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Weak DG primed to start weak DG primed to start (No diesel outage after validation) | Weak DG primed to start weak DG primed to start (No diesel outage after validation)
NOCINC0006484074 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0738C | DL1027 | ASB | Asaba | Delta | 3 - Low | DL0732 | SOUTH SOUTH |  | 2025-11-30 01:26 | Bukola Olabanji | 2025-11-30 01:24 | 2025-11-30 02:00 | 2163 | 2025-11-30 01:24 | 2025-11-30 02:00 | 0:36 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Kevwe Oshoture |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG low frequency, governor was adjusted
NOCINC0006485796 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1416H | AN0708 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 10:04 | Abundance Otunola | 2025-11-30 10:01 | 2025-11-30 10:37 | 2162 | 2025-11-30 10:01 | 2025-11-30 10:37 | 0:36 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on (No diesel outage after validation) | Faulty injector pump was worked on (No diesel outage after validation)
NOCINC0006474949 | Internal Reconciliation | Site Down | P3 | IHS_ILO_0051B | KW4567 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 19:28 | Okusanya Joseph | 2025-11-28 19:27 | 2025-11-28 20:03 | 2161 | 2025-11-28 19:27 | 2025-11-28 20:03 | 0:36 | Energy Vision Nigeria | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Abubakar Saheed |  |  | Nosakhare Imade | Sani Nasir |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG high temperature due to low coolant level in the radiator, coolant was added and site restored.
NOCINC0006460127 | External Reconciliation | Site Down | P1 | IHS_OSU_0781A | T3091 | IBD | Ibadan | Osun | 3 - Low | OS0661 | WEST | Huawei 2G SiteDown@2025-11-26 19:23:58@T3091_SaratVenturesLtd | 2025-11-26 19:39 | System Administrator | 2025-11-26 19:27 | 2025-11-26 20:03 | 2160 | 2025-11-26 19:27 | 2025-11-26 20:03 | 0:36 | IPT | Fuel Outage (Probable) | Passive | DCDG Gen | DCDG - Fuel Pump | 1 / 2 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on
NOCINC0006455999 | External Reconciliation | Site Down | P1 | IHS_OYO_1001A | OY2809 | IBD | Ibadan | Oyo | 3 - Low | OY0922 | WEST |  | 2025-11-26 08:41 | Bosede Kutelu | 2025-11-26 08:38 | 2025-11-26 09:14 | 2153 | 2025-11-26 08:38 | 2025-11-26 09:14 | 0:36 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 3 | Airtel NG, MTN NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Tripped ACDG Load breaker was replaced
NOCINC0006443396 | External Reconciliation | Site Down | P4 | IHS_EDO_1030A | ED2041 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 19:45 | Oluwatomisin Sogbesan | 2025-11-24 19:45 | 2025-11-24 20:21 | 2151 | 2025-11-24 19:45 | 2025-11-24 20:21 | 0:36 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 1 | MTN NG |  | Mike Imomoh | Mike Imomoh | Mike Imomoh | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty manual lift pump was worked on (No diesel outage fater validation)
NOCINC0006442430 | External Reconciliation | Site Down | P1 | IHS_EDO_0891A | T3363 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 17:17 | Oluwatomisin Sogbesan | 2025-11-24 17:14 | 2025-11-24 17:50 | 2150 | 2025-11-24 17:14 | 2025-11-24 17:50 | 0:36 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed rectifier module was reset (No diesel outage after validation) | Failed rectifier module was reset (No diesel outage after validation)
NOCINC0006457315 | External Reconciliation | Site Down | P1 | IHS_ANA_0790A | T4023 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 12:06 | Akachukwu Ugwu | 2025-11-26 12:05 | 2025-11-26 12:41 | 2149 | 2025-11-26 12:05 | 2025-11-26 12:41 | 0:36 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 1 / 1 | MTN NG |  | Appeal John |  |  | Erik Nwodo | Nwigbo Chijioke |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Low Oil Pressure alarm was cleared oil was added (No diesel outage after validation). | Low Oil Pressure alarm was cleared oil was added (No diesel outage after validation).
NOCINC0006458061 | External Reconciliation | Site Down | P3 | IHS_EDO_1245B | ED5509 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 14:02 | Oluwatobiloba Are | 2025-11-26 13:58 | 2025-11-26 14:23 | 1549 | 2025-11-26 13:48 | 2025-11-26 14:23 | 0:36 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Suspected passive, Awaiting update from FSE
NOCINC0006490273 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1358B | OY1036 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 22:57 | Damilola Paseda | 2025-11-30 22:55 | 2025-11-30 23:30 | 2148 | 2025-11-30 22:55 | 2025-11-30 23:30 | 0:36 | SPS | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on | Faulty injector pump was worked on
NOCINC0006459576 | External Reconciliation | Site Down | P4 | IHS_EKI_0874K | EK4417 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-26 18:03 | Mary Elaigwu | 2025-11-26 18:01 | 2025-11-26 18:37 | 2147 | 2025-11-26 18:01 | 2025-11-26 18:37 | 0:36 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gas Flow | 1 / 1 | MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | frozen gas line was worked on
NOCINC0006460894 | External Reconciliation | Site Down | P1 | IHS_OND_0853A | T3443 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 21:50 | Oluwadara Bankole | 2025-11-26 21:46 | 2025-11-26 22:22 | 2145 | 2025-11-26 21:46 | 2025-11-26 22:22 | 0:36 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | DG Under frequency, Governor Adjusted
NOCINC0006467087 | External Reconciliation | Site Down | P4 | IHS_DEL_0933A | T2785 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 18:30 | Femi Olanipekun | 2025-11-27 18:30 | 2025-11-27 19:06 | 2143 | 2025-11-27 18:30 | 2025-11-27 19:06 | 0:36 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG under frequency, governor was adjusted to restore the site (No diesel outage after validation)
NOCINC0006474623 | Internal Reconciliation | Site Down | P1 | IHS_OND_0829A | T3950 | IBD | Ibadan | Ondo | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-28 18:16:10@T3950_AkinwunmiPlotA | 2025-11-28 18:32 | System Administrator | 2025-11-28 18:22 | 2025-11-28 18:58 | 2139 | 2025-11-28 18:22 | 2025-11-28 18:58 | 0:36 | IPT | Equipment Repair | Passive | Control Panel | ATS Relay Faulty | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty ATS Gave Bypassed Pending Replacement
NOCINC0006470058 | External Reconciliation | Site Down | P2 | IHS_OND_0838A | T3930 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 06:10 | Mary Elaigwu | 2025-11-28 06:10 | 2025-11-28 06:45 | 2136 | 2025-11-28 06:10 | 2025-11-28 06:45 | 0:36 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Fan Belt Issue | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 3 | Cut fan belt was replaced
NOCINC0006437759 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST | CSL Fault@2025-11-24 04:32:15@AN0763_Km12 Plywood Mkt | 2025-11-24 04:44 | System Administrator | 2025-11-24 04:38 | 2025-11-24 05:14 | 2135 | 2025-11-24 04:38 | 2025-11-24 05:14 | 0:36 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | weak DG primed to start (No diesel outage after validation). | weak DG primed to start (No diesel outage after validation).
NOCINC0006472377 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0838A | T3302 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 13:02 | Azeezat Badmus | 2025-11-28 13:00 | 2025-11-28 13:36 | 2129 | 2025-11-28 13:00 | 2025-11-28 13:36 | 0:35 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG under frequency was worked on (No diesel outage after validation)
NOCINC0006474718 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0826A | T3626 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 18:42 | Okusanya Joseph | 2025-11-28 18:42 | 2025-11-28 19:17 | 2126 | 2025-11-28 18:42 | 2025-11-28 19:17 | 0:35 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Suspected passive issue at site Awaiting update from FSE
NOCINC0006477179 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0718E | - | - | Asaba | Edo | 3 - Low | ED0748 | SOUTH SOUTH |  | 2025-11-29 05:09 | Elizabeth Apata | 2025-11-29 05:07 | 2025-11-29 05:43 | 2123 | 2025-11-29 05:07 | 2025-11-29 05:43 | 0:35 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | Airtel NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006461484 | External Reconciliation | Site Down | P1 | IHS_DEL_0797A | T2636 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 23:57 | Ezinne Ubachukwu | 2025-11-26 23:54 | 2025-11-27 00:30 | 2123 | 2025-11-26 23:54 | 2025-11-27 00:30 | 0:35 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | High engine temperature, coolant was added (No diesel outage after validation) | High engine temperature, coolant was added (No diesel outage after validation)
NOCINC0006437567 | External Reconciliation | Site Down | P2 | IHS_OYO_1299B | OY2890 | IBD | Ibadan | Oyo | 3 - Low | OY1699 | WEST |  | 2025-11-24 03:20 | Osarieme Charles | 2025-11-24 03:16 | 2025-11-24 03:51 | 2119 | 2025-11-24 03:16 | 2025-11-24 03:51 | 0:35 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Hybrid Synchronization Failure due to frozen smu, smu was reset
NOCINC0006482505 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0882C | EK4514 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 19:37 | Maureen Uchehorke | 2025-11-29 19:35 | 2025-11-29 20:10 | 2118 | 2025-11-29 19:35 | 2025-11-29 20:10 | 0:35 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - CBC | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | faculty CBC was replaced
NOCINC0006483536 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1205B | DL4069 | ASB | Asaba | Delta | 3 - Low | DL1001 | SOUTH SOUTH |  | 2025-11-29 22:32 | Uthman Akinola | 2025-11-29 22:32 | 2025-11-29 23:08 | 2115 | 2025-11-29 22:32 | 2025-11-29 23:08 | 0:35 | Tyllium NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Hybrid synchronisation failure due to Weak stater battery. DG powered with external battery and placed on manual.
NOCINC0006479865 | Internal Reconciliation | Site Down | P2 | IHS_OND_1100B | OD2536 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 13:04 | Zainab Bello | 2025-11-29 13:02 | 2025-11-29 13:37 | 2105 | 2025-11-29 13:02 | 2025-11-29 13:37 | 0:35 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | John Kunamon |  |  | Ibrahim Akinpelu | John Kunamon |  | Fagbemi Solomon | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Under voltage alarm was cleared
NOCINC0006473037 | Internal Reconciliation | Site Down | P1 | IHS_OND_0789A | T3408 | IBD | Ibadan | Ondo | 3 - Low | ON0576 | WEST |  | 2025-11-28 14:51 | Maureen Uchehorke | 2025-11-28 14:50 | 2025-11-28 15:25 | 2102 | 2025-11-28 14:50 | 2025-11-28 15:25 | 0:35 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Sensor Switch | 2 / 2 | MTN NG, Airtel NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | faulty oil switch was worked on
NOCINC0006461861 | External Reconciliation | Site Down | P4 | IHS_IBA_0086B | OY4185 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 01:08 | Victor Otugo | 2025-11-27 01:07 | 2025-11-27 01:42 | 2101 | 2025-11-27 01:07 | 2025-11-27 01:42 | 0:35 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Oremade Yusuf |  | Iyiola Azeez | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | hybrid synchronization failure due to frozen csu, csu was reset.
NOCINC0006468394 | External Reconciliation | Site Down | P1 | IHS_OND_0831A | T3963 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 22:26 | Mary Elaigwu | 2025-11-27 22:25 | 2025-11-27 23:00 | 2100 | 2025-11-27 22:25 | 2025-11-27 23:00 | 0:35 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 14 | Start failure alarm was cleared ...DCGG RESTARTED
NOCINC0006464329 | External Reconciliation | Site Down | P2 | IHS_OSU_0061B | OS4254 | IBD | Ibadan | Osun | 3 - Low | OS0698 | WEST |  | 2025-11-27 11:47 | Mutmainnah Saba | 2025-11-27 11:45 | 2025-11-27 12:20 | 2098 | 2025-11-27 11:45 | 2025-11-27 12:20 | 0:35 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on
NOCINC0006460222 | External Reconciliation | Site Down | P1 | IHS_DEL_0838A | T2646 | ASB | Asaba | Delta | 3 - Low | DL0735 | SOUTH SOUTH |  | 2025-11-26 20:01 | Oluwatobiloba Are | 2025-11-26 20:01 | 2025-11-26 20:36 | 2097 | 2025-11-26 20:01 | 2025-11-26 20:36 | 0:35 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 2 / 2 | Airtel NG, MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Faulty Kick Starter was worked on. | Faulty Kick Starter was worked on. (No diesel outage after validation).
NOCINC0006470359 | External Reconciliation | Site Down | P2 | IHS_ANA_1386H | AN0371 | ASB | Asaba | Anambra | 3 - Low | AN0501 | SOUTH EAST |  | 2025-11-28 07:46 | Patrick Okoro | 2025-11-28 07:46 | 2025-11-28 08:21 | 2095 | 2025-11-28 07:46 | 2025-11-28 08:21 | 0:35 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | Smile, Airtel NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Weak DG battery, External battery was used. (No diesel outage after validation) | Weak DG battery, External battery was used. (No diesel outage after validation)
NOCINC0006486167 | Internal Reconciliation | Site Down | P1 | IHS_OSU_0780A | T3090 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 11:14 | Aishat Oyedeji | 2025-11-30 11:13 | 2025-11-30 11:48 | 2094 | 2025-11-30 11:13 | 2025-11-30 11:48 | 0:35 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 7 | PPM (Generator servicing) was carried out on site with REF IHSREF/25112307333957978528 | PPM (Generator servicing) was carried out on site with REF IHSREF/25112307333957978528
NOCINC0006487401 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0889A | KW4597 | IBD | Ibadan | Kwara | 3 - Low | KW0508 | WEST |  | 2025-11-30 14:07 | Azeezat Adekunle | 2025-11-30 14:05 | 2025-11-30 14:40 | 2090 | 2025-11-30 14:05 | 2025-11-30 14:40 | 0:35 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | MTN NG, Airtel NG |  | Afolabi Ganiyyu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Grid to DG synchronization failure due to grid incomplete phase, DG powered manually.
NOCINC0006484753 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0028V | ED5181 | IBD | Asaba | Edo | 3 - Low | ED0421 | SOUTH SOUTH |  | 2025-11-30 05:50 | Muhammed Hashirudeen | 2025-11-30 05:50 | 2025-11-30 06:25 | 2089 | 2025-11-30 05:50 | 2025-11-30 06:25 | 0:35 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | Airtel NG, MTN NG |  | Ismail Adeyinka |  |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty ats contactor was worked on (No diesel outage after validation)
NOCINC0006441609 | External Reconciliation | Site Down | P1 | IHS_OSU_0903A | OS3648 | IBD | Ibadan | Osun | 3 - Low | OS0695 | WEST |  | 2025-11-24 15:59 | Victor Otugo | 2025-11-24 15:55 | 2025-11-24 16:30 | 2087 | 2025-11-24 15:55 | 2025-11-24 16:30 | 0:35 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | frozen rectifier module was reset
NOCINC0006443676 | External Reconciliation | Site Down | P1 | IHS_OND_0886A | T3915 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-24 20:32 | Kandervil Uwah | 2025-11-24 20:28 | 2025-11-24 21:03 | 2085 | 2025-11-24 20:28 | 2025-11-24 21:03 | 0:35 | Inhouse | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Obuseh Williams |  |  | Ibrahim Akinpelu | Obuseh Williams |  | Lukman Amusat | Ibrahim Yekini | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Failed rectifer module was reset
NOCINC0006460754 | External Reconciliation | Site Down | P3 | IHS_EDO_0920A | T3354 | IBD | Asaba | Kogi | 3 - Low | - | - |  | 2025-11-26 21:22 | Oluwatomisin Sogbesan | 2025-11-26 21:15 | 2025-11-26 21:50 | 2083 | 2025-11-26 21:15 | 2025-11-26 21:50 | 0:35 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Adekoya Adetunji |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006463021 | External Reconciliation | Site Down | P4 | IHS_ANA_1185A | AN0665 | ASB | Asaba | Anambra | 3 - Low | AN1133 | SOUTH EAST |  | 2025-11-27 08:14 | Gbemisola Adedeji | 2025-11-27 08:11 | 2025-11-27 08:46 | 2079 | 2025-11-27 08:11 | 2025-11-27 08:46 | 0:35 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Ezimeruwe ANTHONY |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty AVR was worked on (No diesel outage after validation) | Faulty AVR was worked on (No diesel outage after validation)
NOCINC0006456305 | External Reconciliation | Site Down | P4 | IHS_EDO_0836A | T3260 | IBD | Asaba | Edo | 3 - Low | ED1055 | SOUTH SOUTH |  | 2025-11-26 09:40 | Azeezat Badmus | 2025-11-26 09:38 | 2025-11-26 10:12 | 2078 | 2025-11-26 09:38 | 2025-11-26 10:12 | 0:35 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on (No diesel outage after validation) | Faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006457719 | External Reconciliation | Site Down | P1 | IHS_KWA_0733A | T3103 | IBD | Ibadan | Kwara | 3 - Low | KW0368 | WEST |  | 2025-11-26 13:02 | Oluwatomisin Ogunleye | 2025-11-26 13:00 | 2025-11-26 13:34 | 2078 | 2025-11-26 13:00 | 2025-11-26 13:34 | 0:35 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Outage Issue | 1 / 2 | MTN NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Grid to DG Synchronization failure due to Grid outage issue, DG powered manually.
NOCINC0006480366 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0997A | OY2854 | IBD | Ibadan | Oyo | 3 - Low | OY1101 | WEST |  | 2025-11-29 14:03 | Aishat Oyedeji | 2025-11-29 14:02 | 2025-11-29 14:37 | 2068 | 2025-11-29 14:02 | 2025-11-29 14:37 | 0:34 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Fan Belt | 2 / 2 | MTN NG, Airtel NG |  | Taiwo Abanikannda |  |  | Soye West | Ugwu Samuel Nnamdi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Cut fan belt was worked on | Cut fan belt was worked on
NOCINC0006478172 | Internal Reconciliation | Site Down | P3 | IHS_OND_0962A | OD2447 | IBD | Ibadan | Ondo | 3 - Low | ON0710 | WEST | Huawei 3G SiteDown@2025-11-29 09:06:44@UOD2447 | 2025-11-29 09:24 | System Administrator | 2025-11-29 09:08 | 2025-11-29 09:42 | 2065 | 2025-11-29 09:08 | 2025-11-29 09:42 | 0:34 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Solenoid Coil | 2 / 2 | MTN NG, Airtel NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty Solenoid Coil Bypassed
NOCINC0006444013 | External Reconciliation | Site Down | P4 | IHS_OYO_1353B | OY4327 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 21:26 | Damilola Paseda | 2025-11-24 21:26 | 2025-11-24 22:00 | 2064 | 2025-11-24 21:26 | 2025-11-24 22:00 | 0:34 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Taiwo Abanikannda |  |  | Soye West | Ugwu Samuel Nnamdi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting passive update from FSE. | Suspected passive issue, awaiting passive update from FSE.
NOCINC0006483954 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0738C | DL1027 | ASB | Asaba | Delta | 3 - Low | DL0732 | SOUTH SOUTH |  | 2025-11-30 00:22 | Bukola Olabanji | 2025-11-30 00:20 | 2025-11-30 00:55 | 2064 | 2025-11-30 00:20 | 2025-11-30 00:55 | 0:34 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | Airtel NG, MTN NG |  | Kevwe Oshoture |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG low frequency, governor was adjusted
NOCINC0006468245 | External Reconciliation | Site Down | P1 | IHS_ANA_1088A | AN0333 | ASB | Asaba | Anambra | 3 - Low | AN0701 | SOUTH EAST |  | 2025-11-27 22:00 | Oluwatoyin Fagite | 2025-11-27 21:56 | 2025-11-27 22:30 | 2058 | 2025-11-27 21:56 | 2025-11-27 22:30 | 0:34 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Aneke Christian | Habib Muhammed | Habib Muhammed | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | DG high engine temperature due to low coolant level, coolant was added (No diesel outage after validation) | DG high engine temperature due to low coolant level, coolant was added (No diesel outage after validation)
NOCINC0006488335 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1447B | - | - | Ibadan | Oyo | 3 - Low | OY1565 | WEST |  | 2025-11-30 16:35 | Victor Otugo | 2025-11-30 16:29 | 2025-11-30 17:03 | 2057 | 2025-11-30 16:29 | 2025-11-30 17:03 | 0:34 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Sensor Switch | 1 / 1 | Airtel NG |  | Mohammed Soliu |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | faulty oil switch was worked on
NOCINC0006481356 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0904A | T3561 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 16:27 | Aishat Oyedeji | 2025-11-29 16:27 | 2025-11-29 17:01 | 2049 | 2025-11-29 16:27 | 2025-11-29 17:01 | 0:34 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Voltage fluctuation due to no BUB, GG auto-restarted. | Voltage fluctuation due to no BUB, GG auto-restarted.
NOCINC0006486921 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0947A | T2279 | ASB | Asaba | Delta | 3 - Low | DL0251 | SOUTH SOUTH |  | 2025-11-30 13:03 | Ezinne Ubachukwu | 2025-11-30 13:03 | 2025-11-30 13:34 | 1868 | 2025-11-30 13:00 | 2025-11-30 13:34 | 0:34 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Interface Module Faulty | 2 / 2 | Airtel NG, MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty DG Module was worked on(No diesel outage after validation) | Faulty DG Module was worked on(No diesel outage after validation)
NOCINC0006463860 | External Reconciliation | Site Down | P1 | IHS_OND_0853A | T3443 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 10:52 | Iyesioluwa Ola | 2025-11-27 10:52 | 2025-11-27 11:26 | 2044 | 2025-11-27 10:52 | 2025-11-27 11:26 | 0:34 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 1 | MTN NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Faulty DG Governor Was Replaced
NOCINC0006474467 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0915A | T3858 | IBD | Ibadan | Oyo | 3 - Low | OY1032 | WEST |  | 2025-11-28 18:14 | Mutmainnah Saba | 2025-11-28 18:14 | 2025-11-28 18:48 | 2040 | 2025-11-28 18:14 | 2025-11-28 18:48 | 0:34 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | Airtel NG, MTN NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty radiator was worked on | Faulty radiator was worked on
NOCINC0006471959 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1051A | DL0091 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 11:56 | Uthman Akinola | 2025-11-28 11:51 | 2025-11-28 12:25 | 2040 | 2025-11-28 11:51 | 2025-11-28 12:25 | 0:34 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Failed rectifier module was reset (no diesel outage after validation)
NOCINC0006445630 | External Reconciliation | Site Down | P2 | IHS_DEL_1109A | DL0753 | ASB | Asaba | Delta | 3 - Low | DL1240 | SOUTH SOUTH |  | 2025-11-25 06:54 | Quadri Ogundare | 2025-11-25 06:52 | 2025-11-25 07:26 | 2036 | 2025-11-25 06:52 | 2025-11-25 07:26 | 0:34 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | HENRY OMELE |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | High engine temperature due to low coolant level, coolant was topped | High engine temperature due to low coolant level, coolant was topped
NOCINC0006468528 | External Reconciliation | Site Down | P3 | IHS_EDO_0008B | ED5007 | IBD | Asaba | Edo | 3 - Low | ED1032 | SOUTH SOUTH |  | 2025-11-27 22:52 | Patrick Okoro | 2025-11-27 22:51 | 2025-11-27 23:25 | 2036 | 2025-11-27 22:51 | 2025-11-27 23:25 | 0:34 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 2 | MTN NG |  | MICHAEL TONDO | Micheal Tondo | Micheal Tondo | Cornelius Yakubu | Elochukwu Umeohana |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Dg high temperature. Coolant was added | Dg high temperature. Coolant was added
NOCINC0006446928 | External Reconciliation | Site Down | P1 | IHS_WAR_0958B | DL3355 | ASB | Asaba | Delta | 3 - Low | DL0843 | SOUTH SOUTH |  | 2025-11-25 10:16 | Tracy Osarumwense | 2025-11-25 10:16 | 2025-11-25 10:50 | 2033 | 2025-11-25 10:16 | 2025-11-25 10:50 | 0:34 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Emergency Stop Switch | 2 / 2 | Airtel NG, MTN NG |  | Kenneth Oboniye |  |  | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty Emergency stop switch was bypassed | Faulty Emergency stop switch was bypassed (No diesel outage after validation)
NOCINC0006458734 | External Reconciliation | Site Down | P1 | IHS_KWA_0831A | KW3805 | IBD | Ibadan | Kwara | 3 - Low | KW0653 | WEST |  | 2025-11-26 15:37 | Oluwatomisin Ogunleye | 2025-11-26 15:37 | 2025-11-26 16:11 | 2033 | 2025-11-26 15:37 | 2025-11-26 16:11 | 0:34 | IPT | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 2 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Grid-DG synchronization failure due to unstable grid supply issue. DG was powered manually.
NOCINC0006463242 | External Reconciliation | Site Down | P1 | IHS_KWA_0831A | KW3805 | IBD | Ibadan | Kwara | 3 - Low | KW0653 | WEST |  | 2025-11-27 09:02 | Titus Tosin | 2025-11-27 09:02 | 2025-11-27 09:36 | 2029 | 2025-11-27 09:02 | 2025-11-27 09:36 | 0:34 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 1 / 2 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Faulty kick starter was worked on
NOCINC0006489151 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0852A | EK2232 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-30 18:56 | Oluwadara Bankole | 2025-11-30 18:52 | 2025-11-30 19:26 | 2028 | 2025-11-30 18:52 | 2025-11-30 19:26 | 0:34 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006471165 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0820A | T3238 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 10:05 | Azeezat Badmus | 2025-11-28 09:54 | 2025-11-28 10:28 | 2026 | 2025-11-28 09:54 | 2025-11-28 10:28 | 0:34 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Failed rectifier module was reset (No diesel outage after validation)
NOCINC0006472113 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0869A | T2762 | ASB | Asaba | Delta | 3 - Low | DL1171 | SOUTH SOUTH |  | 2025-11-28 12:21 | Uthman Akinola | 2025-11-28 12:21 | 2025-11-28 12:55 | 2021 | 2025-11-28 12:21 | 2025-11-28 12:55 | 0:34 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under frequency, governor was adjusted. (No diesel outage after validation) | DG under frequency, governor was adjusted. (No diesel outage after validation)
NOCINC0006483406 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0921B | EK6303 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 22:13 | Abisoye Olaleye | 2025-11-29 22:11 | 2025-11-29 22:45 | 2013 | 2025-11-29 22:11 | 2025-11-29 22:45 | 0:34 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | start failure due to weak crank battery
NOCINC0006466710 | External Reconciliation | Site Down | P1 | IHS_DEL_0811A | T2654 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 17:24 | Femi Olanipekun | 2025-11-27 17:24 | 2025-11-27 17:58 | 2007 | 2025-11-27 17:24 | 2025-11-27 17:58 | 0:33 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 1 / 1 | MTN NG |  | Dare Oguyemi | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 8 | faulty Water pump was replaced (no diesel outage after validation)
NOCINC0006460196 | External Reconciliation | Site Down | P1 | IHS_WAR_0738C | DL1027 | ASB | Asaba | Delta | 3 - Low | DL0732 | SOUTH SOUTH |  | 2025-11-26 19:56 | Oluwatobiloba Are | 2025-11-26 19:56 | 2025-11-26 20:29 | 2005 | 2025-11-26 19:56 | 2025-11-26 20:29 | 0:33 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Control Panel | 2 / 2 | Airtel NG, MTN NG |  | Kevwe Oshoture |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed to start Alarm was cleared to restore power to site. | Failed to start Alarm was cleared to restore power to site. (No diesel outage after validation).
NOCINC0006485695 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0929A | OS2725 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 09:41 | Victor Otugo | 2025-11-30 09:37 | 2025-11-30 10:10 | 2004 | 2025-11-30 09:37 | 2025-11-30 10:10 | 0:33 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Charging Alternator | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Failed charging alternator was excited
NOCINC0006463008 | External Reconciliation | Site Down | P2 | IHS_EDO_0810A | T3266 | IBD | Asaba | Edo | 3 - Low | ED0218 | SOUTH SOUTH |  | 2025-11-27 08:10 | Oluwatomisin Sogbesan | 2025-11-27 08:10 | 2025-11-27 08:38 | 1704 | 2025-11-27 08:10 | 2025-11-27 08:43 | 0:33 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Generator servicing was completed at site with ref: IHSREF/25110509204790712877 SARID0008708046 | Generator servicing was completed at site with ref: IHSREF/25110509204790712877 SARID0008708046
NOCINC0006439567 | External Reconciliation | Site Down | P4 | IHS_EDO_1240B | ED5542 | IBD | Asaba | Edo | 3 - Low | ED1126 | SOUTH SOUTH |  | 2025-11-24 11:35 | Ayomide Akindolie | 2025-11-24 11:35 | 2025-11-24 12:08 | 2003 | 2025-11-24 11:35 | 2025-11-24 12:08 | 0:33 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Jude Audu | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty Injector Pump was worked on. | Faulty Injector Pump was worked on. (No diesel outage after validation).
NOCINC0006472170 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 12:33 | Muhammed Hashirudeen | 2025-11-28 12:31 | 2025-11-28 13:04 | 2001 | 2025-11-28 12:31 | 2025-11-28 13:04 | 0:33 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is affected by ED4860. (No diesel outage after validation)
NOCINC0006459226 | External Reconciliation | Site Down | P1 | IHS_WAR_0886H | DL0377 | ASB | Asaba | Delta | 3 - Low | DL0738 | SOUTH SOUTH |  | 2025-11-26 17:01 | Patrick Okoro | 2025-11-26 17:01 | 2025-11-26 17:34 | 1999 | 2025-11-26 17:01 | 2025-11-26 17:34 | 0:33 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 3 / 3 | MTN NG, Airtel NG, INQ |  | Victor Ezeh |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Failed Charging alternator was excited (No diesel outage after validation) | Failed Charging alternator was excited (No diesel outage after validation)
NOCINC0006460513 | External Reconciliation | Site Down | P1 | IHS_DEL_0947A | T2279 | ASB | Asaba | Delta | 3 - Low | DL0251 | SOUTH SOUTH |  | 2025-11-26 20:37 | Ezinne Ubachukwu | 2025-11-26 20:33 | 2025-11-26 21:06 | 1997 | 2025-11-26 20:33 | 2025-11-26 21:06 | 0:33 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Faulty module was worked on (No diesel outage after validation) | Faulty module was worked on (No diesel outage after validation)
NOCINC0006482076 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0842A | EK2219 | IBD | Ibadan | Ekiti | 3 - Low | EK0564 | WEST |  | 2025-11-29 18:22 | Zainab Bello | 2025-11-29 18:20 | 2025-11-29 18:53 | 1997 | 2025-11-29 18:20 | 2025-11-29 18:53 | 0:33 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | Airtel NG, MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | under voltage alarm was cleared
NOCINC0006473686 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0042B | DL0624 | ASB | Asaba | Delta | 3 - Low | DL0809 | SOUTH SOUTH |  | 2025-11-28 16:22 | Bukola Olabanji | 2025-11-28 16:20 | 2025-11-28 16:53 | 1997 | 2025-11-28 16:20 | 2025-11-28 16:53 | 0:33 | BJ Bison NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization delay due to start fail alarm was cleared | Hybrid synchronization delay due to start fail alarm was cleared
NOCINC0006471405 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0892A | T3074 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 10:39 | Okusanya Joseph | 2025-11-28 10:38 | 2025-11-28 11:11 | 1996 | 2025-11-28 10:38 | 2025-11-28 11:11 | 0:33 | IPT | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 1 | MTN NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Grid-DG Synchronization Failure due to unstable grid supply, DG was powered manually
NOCINC0006481424 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0854A | T3316 | IBD | Asaba | Edo | 3 - Low | ED0398 | SOUTH SOUTH |  | 2025-11-29 16:35 | Evelyn Emagurehor | 2025-11-29 16:33 | 2025-11-29 17:06 | 1993 | 2025-11-29 16:33 | 2025-11-29 17:06 | 0:33 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | SAHEED SHONDE | Babatunde Olayiwola | Shonde Saheed | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | DG underfrequency was adjusted. (No diesel outage after validation). | DG underfrequency was adjusted. (No diesel outage after validation).
NOCINC0006463355 | External Reconciliation | Site Down | P3 | IHS_ANA_0966A | T4830 | ASB | Asaba | Anambra | 3 - Low | AN0833 | SOUTH EAST |  | 2025-11-27 09:30 | Femi Olanipekun | 2025-11-27 09:30 | 2025-11-27 10:03 | 1991 | 2025-11-27 09:30 | 2025-11-27 10:03 | 0:33 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Amadi Fabian | Tijani Haruna | Tijani Haruna | Henry Wanogho | Ifeanyi Chukusa |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 3 | Weak DG at site, MDG deployed and also installed to power the site (No diesel outage after validation) | Weak DG at site, MDG deployed and also installed to power the site (No diesel outage after validation)
NOCINC0006474203 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0915A | T3858 | IBD | Ibadan | Oyo | 3 - Low | OY1032 | WEST |  | 2025-11-28 17:34 | Damilola Paseda | 2025-11-28 17:34 | 2025-11-28 18:07 | 1988 | 2025-11-28 17:34 | 2025-11-28 18:07 | 0:33 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Radiator Leakage | 2 / 2 | MTN NG, Airtel NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | High DG temperature due to leaking radiator, radiator was worked on and DG was powered manually. | High DG temperature due to leaking radiator, radiator was worked on and DG was powered manually.
NOCINC0006475882 | Internal Reconciliation | Site Down | P2 | IHS_ANA_0989A | T4169 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 21:48 | Femi Olanipekun | 2025-11-28 21:46 | 2025-11-28 22:20 | 1987 | 2025-11-28 21:46 | 2025-11-28 22:20 | 0:33 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Filter | 1 / 1 | MTN NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 4 | Blocked fuel filter was flushed to restore the site (No diesel outage after validation) | Blocked fuel filter was flushed to restore the site (No diesel outage after validation)
NOCINC0006438122 | External Reconciliation | Site Down | P1 | IHS_OYO_0989A | OY2802 | IBD | Ibadan | Oyo | 3 - Low | OY0956 | WEST |  | 2025-11-24 06:36 | Mutmainnah Saba | 2025-11-24 06:33 | 2025-11-24 07:06 | 1986 | 2025-11-24 06:33 | 2025-11-24 07:06 | 0:33 | SPS | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006490173 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0734E | ED5189 | IBD | Asaba | Edo | 3 - Low | ED0645 | SOUTH SOUTH |  | 2025-11-30 22:36 | Azeezat Badmus | 2025-11-30 22:35 | 2025-11-30 23:08 | 1985 | 2025-11-30 22:35 | 2025-11-30 23:08 | 0:33 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty charging alternator was worked on (No diesel outage after validation)
NOCINC0006489787 | Internal Reconciliation | Site Down | P4 | IHS_BEN_0078C | ED5153 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 21:17 | Azeezat Badmus | 2025-11-30 21:15 | 2025-11-30 21:49 | 1983 | 2025-11-30 21:15 | 2025-11-30 21:49 | 0:33 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Top Gasket | 1 / 1 | MTN NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty top gasket was worked on (No diesel outage after validation)
NOCINC0006458340 | External Reconciliation | Site Down | P1 | IHS_OND_0853A | T3443 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 14:44 | Mary Elaigwu | 2025-11-26 14:44 | 2025-11-26 15:17 | 1980 | 2025-11-26 14:44 | 2025-11-26 15:17 | 0:33 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 1 | MTN NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Faulty Lift Pump Worked On
NOCINC0006442948 | External Reconciliation | Site Down | P3 | IHS_ANA_1041A | AN0028 | ASB | Asaba | Anambra | 3 - Low | AN0711 | SOUTH EAST |  | 2025-11-24 18:29 | Abundance Otunola | 2025-11-24 18:27 | 2025-11-24 19:00 | 1974 | 2025-11-24 18:27 | 2025-11-24 19:00 | 0:33 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Low voltage alarm, AVR was adjusted (No diesel outage after validation)
NOCINC0006473073 | Internal Reconciliation | Site Down | P4 | IHS_KWA_1024C | KW6468 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 14:55 | Samuel Omole | 2025-11-28 14:49 | 2025-11-28 15:22 | 1973 | 2025-11-28 14:49 | 2025-11-28 15:22 | 0:33 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting RCA from FSE
NOCINC0006488610 | Internal Reconciliation | Site Down | P1 | IHS_AWK_0016B | AN0088 | ASB | Asaba | Anambra | 3 - Low | AN0662 | SOUTH EAST |  | 2025-11-30 17:15 | Ezinne Ubachukwu | 2025-11-30 17:12 | 2025-11-30 17:45 | 1973 | 2025-11-30 17:12 | 2025-11-30 17:45 | 0:33 | BJ Bison NGA | Fuel Outage (Probable) | Passive | Diesel | Tank Sealing Issue - Water In The Fuel | 2 / 2 | MTN NG, Airtel NG |  | Egbujor Victor | Hillary Uduak | Hillary Uduak | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Water ingress was flushed. (No diesel outage after validation) | Water ingress was flushed. (No diesel outage after validation)
NOCINC0006476416 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0979A | ED2145 | IBD | Asaba | Edo | 3 - Low | ED0499 | SOUTH SOUTH |  | 2025-11-28 23:51 | Elizabeth Apata | 2025-11-28 23:51 | 2025-11-29 00:23 | 1969 | 2025-11-28 23:51 | 2025-11-29 00:23 | 0:33 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under voltage alarm was cleared and DG was powered manually (No diesel outage after validation)
NOCINC0006459148 | External Reconciliation | Site Down | P1 | IHS_ANA_0786A | T0285/T6512 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 16:44 | Patrick Okoro | 2025-11-26 16:43 | 2025-11-26 17:16 | 1968 | 2025-11-26 16:43 | 2025-11-26 17:16 | 0:33 | Huawei | Equipment Repair | Passive | Environmental | Aircon Compressor High Temp | 1 / 2 | MTN NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | High temperature due to faulty AC Compressor, Shelter Open and HVAC serviced | High temperature due to faulty AC Compressor, Shelter Open and HVAC serviced
NOCINC0006467023 | External Reconciliation | Site Down | P1 | IHS_ANA_1035A | AN0117 | ASB | Asaba | Anambra | 3 - Low | AN0601 | SOUTH EAST |  | 2025-11-27 18:16 | Femi Olanipekun | 2025-11-27 18:16 | 2025-11-27 18:49 | 1964 | 2025-11-27 18:16 | 2025-11-27 18:49 | 0:33 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG shut down on engine temperature, radiator flushed, water was added (No diesel outage after validation) | DG shut down on engine temperature, radiator flushed, water was added (No diesel outage after validation)
NOCINC0006472406 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0898A | KW4595 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 13:06 | Praise Okezie | 2025-11-28 13:03 | 2025-11-28 13:36 | 1963 | 2025-11-28 13:03 | 2025-11-28 13:36 | 0:33 | IPT | Fuel Outage (Probable) | Passive | DCDG Gen | DCDG - Fuel Pump | 1 / 1 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty fuel pump was replaced
NOCINC0006484252 | Internal Reconciliation | Site Down | P4 | IHS_ONT_0083B | AN0905 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 02:39 | Gbemisola Adedeji | 2025-11-30 02:35 | 2025-11-30 03:07 | 1955 | 2025-11-30 02:35 | 2025-11-30 03:07 | 0:33 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Ezimeruwe ANTHONY |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Tripped DG load breaker was enabled (No diesel outage after validation). | Tripped DG load breaker was enabled (No diesel outage after validation).
NOCINC0006436542 | External Reconciliation | Site Down | P2 | IHS_OND_0717E | OD2062 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-24 00:17 | Ayodele Oludare | 2025-11-24 00:15 | 2025-11-24 00:48 | 1953 | 2025-11-24 00:15 | 2025-11-24 00:48 | 0:33 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Module | 1 / 1 | MTN NG |  | John Kunamon |  |  | Ibrahim Akinpelu | John Kunamon |  | Fagbemi Solomon | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to failed hybrid module, modile was reset
NOCINC0006480995 | Internal Reconciliation | Site Down | P2 | IHS_BEN_0058B | ED5098 | IBD | Asaba | Edo | 3 - Low | ED0505 | SOUTH SOUTH |  | 2025-11-29 15:37 | Evelyn Emagurehor | 2025-11-29 15:37 | 2025-11-29 16:09 | 1952 | 2025-11-29 15:37 | 2025-11-29 16:09 | 0:33 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 2 | MTN NG |  | Edwin Emehian | Achebe Chigozie | Omoragbon Austin | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | High engine temperature due to low coolant level, coolant was added to restore the site. (No diesel outage after validation). | High engine temperature due to low coolant level, coolant was added to restore the site. (No diesel outage after validation).
NOCINC0006488880 | Internal Reconciliation | Site Down | P4 | IHS_OYO_0023B | OY4041 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 18:01 | Precious Attah | 2025-11-30 18:00 | 2025-11-30 18:33 | 1943 | 2025-11-30 18:00 | 2025-11-30 18:33 | 0:32 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG lost compression, Weak DG was primed to start
NOCINC0006467026 | External Reconciliation | Site Down | P2 | IHS_KWA_0791A | T3169 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 18:17 | Titus Tosin | 2025-11-27 18:16 | 2025-11-27 18:48 | 1942 | 2025-11-27 18:16 | 2025-11-27 18:48 | 0:32 | IPT | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | PPM (Generator servicing (PPM) was carried out) | PPM (Generator servicing (PPM) was carried out)
NOCINC0006448196 | External Reconciliation | Site Down | P4 | IHS_EDO_0994A | ED2090 | IBD | Asaba | Edo | 3 - Low | ED0970 | SOUTH SOUTH |  | 2025-11-25 12:40 | Emmanuel Faleti | 2025-11-25 12:40 | 2025-11-25 13:12 | 1942 | 2025-11-25 12:40 | 2025-11-25 13:12 | 0:32 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 1 / 2 | MTN NG |  | OMOKHAFE JULIUS | Julius Godwin | Julius Godwin | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low oil pressure, oil was added (No diesel outage after validation) | Low oil pressure, oil was added (No diesel outage after validation)
NOCINC0006440132 | External Reconciliation | Site Down | P3 | IHS_KWA_0926C | KW4755 | IBD | Ibadan | Kwara | 3 - Low | KW0526 | WEST |  | 2025-11-24 13:02 | Azeezat Adekunle | 2025-11-24 12:59 | 2025-11-24 13:31 | 1925 | 2025-11-24 12:59 | 2025-11-24 13:31 | 0:32 | IPT | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | David Oyebamiji |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out
NOCINC0006487664 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1270C | AN0063 | ASB | Asaba | Anambra | 3 - Low | AN0677 | SOUTH EAST |  | 2025-11-30 14:53 | Ezinne Ubachukwu | 2025-11-30 14:50 | 2025-11-30 15:22 | 1924 | 2025-11-30 14:50 | 2025-11-30 15:22 | 0:32 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 2 / 2 | MTN NG, Airtel NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Partial contact on solenoid switch was worked on. (No diesel outage after validation) | Partial contact on solenoid switch was worked on. (No diesel outage after validation)
NOCINC0006447754 | External Reconciliation | Site Down | P1 | IHS_KWA_0876A | KW2342 | IBD | Ibadan | Kwara | 3 - Low | KW0411 | WEST | Cascaded Incident from TTO6730815 - Cascade Removed From TTO6730815 | 2025-11-25 11:47 | Precious Attah | 2025-11-25 11:46 | 2025-11-25 12:18 | 1922 | 2025-11-25 11:46 | 2025-11-25 12:18 | 0:32 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 3 | faulty rectifier module was reset
NOCINC0006440323 | External Reconciliation | Site Down | P1 | IHS_OYO_0908A | T3862 | IBD | Ibadan | Oyo | 3 - Low | OY0975 | WEST |  | 2025-11-24 13:15 | Oluwatomisin Ogunleye | 2025-11-24 13:13 | 2025-11-24 13:45 | 1922 | 2025-11-24 13:13 | 2025-11-24 13:45 | 0:32 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Module | 2 / 2 | MTN NG, Airtel NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to failed csu, csu was reset
NOCINC0006484053 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0802A | T3257 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 01:12 | Bukola Olabanji | 2025-11-30 00:33 | 2025-11-30 01:05 | 1920 | 2025-11-30 00:33 | 2025-11-30 01:05 | 0:32 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Imomoh Sylvanus |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 2 | Flat DG battery, external battery was used to power site
NOCINC0006480735 | Internal Reconciliation | Site Down | P3 | IHS_EDO_1166H | ED4902 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 14:54 | Evelyn Emagurehor | 2025-11-29 14:53 | 2025-11-29 15:25 | 1916 | 2025-11-29 14:53 | 2025-11-29 15:25 | 0:32 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Smile |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG at site was primed to start to restore the site. (No diesel outage after validation). | Weak DG at site was primed to start to restore the site. (No diesel outage after validation).
NOCINC0006474914 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0881A | T3654 | IBD | Ibadan | Osun | 3 - Low | OS0853 | WEST | CSL Fault@2025-11-28 19:08:12@T3654_AshipaRdIpetuModu | 2025-11-28 19:21 | System Administrator | 2025-11-28 19:08 | 2025-11-28 19:40 | 1915 | 2025-11-28 19:08 | 2025-11-28 19:40 | 0:32 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Under voltage alarm was cleared and DG powered | Under voltage alarm was cleared and DG powered
NOCINC0006441638 | External Reconciliation | Site Down | P2 | IHS_IBA_0005B | OY2642 | IBD | Ibadan | Oyo | 3 - Low | OY0811 | WEST |  | 2025-11-24 16:05 | Aishat Oyedeji | 2025-11-24 16:05 | 2025-11-24 16:37 | 1914 | 2025-11-24 16:05 | 2025-11-24 16:37 | 0:32 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Failed Charging Alternator was excited | Failed Charging Alternator was excited
NOCINC0006472469 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0701E | OY4307 | IBD | Ibadan | Oyo | 3 - Low | OY0911 | WEST |  | 2025-11-28 13:16 | Damilola Paseda | 2025-11-28 13:15 | 2025-11-28 13:47 | 1913 | 2025-11-28 13:15 | 2025-11-28 13:47 | 0:32 | SPS | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | BASHIR ABDULRASAQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | PPM was carried out at the site with IHSREF/25112709361080621166 | PPM was carried out at the site with IHSREF/25112709361080621166
NOCINC0006462983 | External Reconciliation | Site Down | P3 | IHS_OSU_0893A | T3819 | IBD | Ibadan | Osun | 3 - Low | OS0654 | WEST |  | 2025-11-27 08:03 | Precious Attah | 2025-11-27 08:02 | 2025-11-27 08:34 | 1912 | 2025-11-27 08:02 | 2025-11-27 08:34 | 0:32 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006466904 | External Reconciliation | Site Down | P3 | IHS_DEL_0933A | T2785 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 17:57 | Uthman Akinola | 2025-11-27 17:56 | 2025-11-27 18:28 | 1911 | 2025-11-27 17:56 | 2025-11-27 18:28 | 0:32 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 4 | DG under frequency, governor was adjusted to restore the site (No diesel outage after validation) | DG under frequency, governor was adjusted to restore the site (No diesel outage after validation)
NOCINC0006446393 | External Reconciliation | Site Down | P1 | IHS_ANA_1421H | AN0442 | ASB | Asaba | Anambra | 3 - Low | AN0027 | SOUTH EAST |  | 2025-11-25 09:12 | Oluwatoyin Fagite | 2025-11-25 09:10 | 2025-11-25 09:42 | 1903 | 2025-11-25 09:10 | 2025-11-25 09:42 | 0:32 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Anwah Chike |  |  | Erik Nwodo | Nwigbo Chijioke |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Hybrid synchronization failure due to failed to start alarm, alarm was cleared and DG was powered manually (No diesel outage after validation) | Hybrid synchronization failure due to failed to start alarm, alarm was cleared and DG was powered manually (No diesel outage after validation)
NOCINC0006486147 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0832A | T3284 | IBD | Asaba | Edo | 3 - Low | ED0845 | SOUTH SOUTH |  | 2025-11-30 11:10 | Evelyn Emagurehor | 2025-11-30 11:10 | 2025-11-30 11:42 | 1898 | 2025-11-30 11:10 | 2025-11-30 11:42 | 0:32 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG at site was primed to start to restore the site. (No diesel outage after validation). | Weak DG at site was primed to start to restore the site. (No diesel outage after validation).
NOCINC0006462563 | External Reconciliation | Site Down | P1 | IHS_DEL_0811A | T2654 | ASB | Asaba | Delta | 3 - Low | - | - | NE Is Disconnected@2025-11-27 06:00:44@N2654 | 2025-11-27 06:14 | System Administrator | 2025-11-27 06:01 | 2025-11-27 06:32 | 1897 | 2025-11-27 06:01 | 2025-11-27 06:32 | 0:32 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 1 / 1 | MTN NG |  | Dare Oguyemi | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 7 | Faulty water pump was worked on (No diesel outage after validation) | Faulty water pump was worked on (No diesel outage after validation)
NOCINC0006480585 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0793A | T0246 | ASB | Asaba | Anambra | 3 - Low | AN0533 | SOUTH EAST |  | 2025-11-29 14:38 | Kehinde Akinbowale | 2025-11-29 14:35 | 2025-11-29 15:07 | 1897 | 2025-11-29 14:35 | 2025-11-29 15:07 | 0:32 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | Airtel NG, MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG high temperature due to low coolant level, Coolant was added(No diesel outage after validation) | DG high temperature due to low coolant level, Coolant was added(No diesel outage after validation)
NOCINC0006460312 | External Reconciliation | Site Down | P4 | IHS_ANA_1325B | AN3173 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 20:15 | Oluwatoyin Fagite | 2025-11-26 20:12 | 2025-11-26 20:44 | 1894 | 2025-11-26 20:12 | 2025-11-26 20:44 | 0:32 | BJ Bison NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Femi Balogun | Kenneth Nlerum | Kenneth Nlerum | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization delay. DG auto restart (No diesel outage after validation)
NOCINC0006474745 | Internal Reconciliation | Site Down | P1 | IHS_ILO_0043B | KW4687 | IBD | Ibadan | Kwara | 3 - Low | KW0372 | WEST |  | 2025-11-28 18:48 | Okusanya Joseph | 2025-11-28 18:48 | 2025-11-28 19:20 | 1889 | 2025-11-28 18:48 | 2025-11-28 19:20 | 0:31 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Hybrid synchronization failure due to DG failed to start alarm was cleared and DG was Powered manually
NOCINC0006485435 | Internal Reconciliation | Site Down | P2 | IHS_ANA_0831A | T4094 | ASB | Asaba | Anambra | 3 - Low | AN0929 | SOUTH EAST |  | 2025-11-30 08:49 | Ezinne Ubachukwu | 2025-11-30 08:47 | 2025-11-30 09:18 | 1886 | 2025-11-30 08:47 | 2025-11-30 09:18 | 0:31 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Generator servicing was done on site. (No diesel outage after validation) | Generator servicing was done on site. (No diesel outage after validation)
NOCINC0006448997 | External Reconciliation | Site Down | P4 | IHS_DEL_1205B | DL4069 | ASB | Asaba | Delta | 3 - Low | DL1001 | SOUTH SOUTH |  | 2025-11-25 14:15 | Patrick Okoro | 2025-11-25 14:10 | 2025-11-25 14:33 | 1403 | 2025-11-25 14:02 | 2025-11-25 14:33 | 0:31 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG high temperature, Coolant was added (No diesel outage after validation) | DG high temperature, Coolant was added (No diesel outage after validation)
NOCINC0006438847 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST |  | 2025-11-24 09:22 | Aishat Oyedeji | 2025-11-24 09:18 | 2025-11-24 09:50 | 1880 | 2025-11-24 09:18 | 2025-11-24 09:50 | 0:31 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen CSU, CSU was reset | Hybrid synchronization failure due to frozen CSU, CSU was reset
NOCINC0006475429 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0901A | KW4588 | IBD | Ibadan | Kwara | 3 - Low | KW0466 | WEST |  | 2025-11-28 20:47 | Titus Tosin | 2025-11-28 20:45 | 2025-11-28 21:17 | 1880 | 2025-11-28 20:45 | 2025-11-28 21:17 | 0:31 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Tripped load breaker was enabled.
NOCINC0006484707 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1086C | ED5375 | IBD | Asaba | Edo | 3 - Low | ED1056 | SOUTH SOUTH |  | 2025-11-30 05:31 | Bukola Olabanji | 2025-11-30 05:29 | 2025-11-30 06:01 | 1875 | 2025-11-30 05:29 | 2025-11-30 06:01 | 0:31 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Imomoh Sylvanus |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG under frequency, Governor was adjusted
NOCINC0006457842 | External Reconciliation | Site Down | P1 | IHS_OND_0853A | T3443 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 13:26 | Mary Elaigwu | 2025-11-26 13:26 | 2025-11-26 13:57 | 1865 | 2025-11-26 13:26 | 2025-11-26 13:57 | 0:31 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 1 / 1 | MTN NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Faulty Hand Primer Was Worked On
NOCINC0006484121 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0804A | T3230 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 01:58 | Muhammed Hashirudeen | 2025-11-30 01:58 | 2025-11-30 02:29 | 1863 | 2025-11-30 01:58 | 2025-11-30 02:29 | 0:31 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Burnt DC breaker was replaced (No diesel outage after validation)
NOCINC0006475890 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-28 21:49 | Ihuoma Opurum | 2025-11-28 21:49 | 2025-11-28 22:19 | 1856 | 2025-11-28 21:49 | 2025-11-28 22:19 | 0:31 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 2 / 2 | MTN NG, Airtel NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Suspected passive issue at site. Awaiting RCA from FSE.
NOCINC0006443750 | External Reconciliation | Site Down | P1 | IHS_ILO_0704E | KW4598 | IBD | Ibadan | Kwara | 3 - Low | KW0360 | WEST | 4G ZTE Sitedown@2025-11-24 20:35:59@KW0360(40360) | 2025-11-24 20:49 | System Administrator | 2025-11-24 20:36 | 2025-11-24 21:07 | 1856 | 2025-11-24 20:36 | 2025-11-24 21:07 | 0:31 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Outage Issue | 1 / 1 | Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to grid outage issue. DG was powered manually.
NOCINC0006449717 | External Reconciliation | Site Down | P4 | IHS_ANA_1071A | AN0307 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 15:53 | Oluwatoyin Fagite | 2025-11-25 15:51 | 2025-11-25 16:22 | 1855 | 2025-11-25 15:51 | 2025-11-25 16:22 | 0:31 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006450179 | External Reconciliation | Site Down | P3 | IHS_DEL_0728E | DL5201 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 16:47 | Ezinne Ubachukwu | 2025-11-25 16:44 | 2025-11-25 17:15 | 1844 | 2025-11-25 16:44 | 2025-11-25 17:15 | 0:31 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG Under voltage alarm was cleared. (No diesel outage after validation) | DG Under voltage alarm was cleared. (No diesel outage after validation)
NOCINC0006445064 | External Reconciliation | Site Down | P2 | IHS_KWA_0889A | KW4597 | IBD | Ibadan | Kwara | 3 - Low | KW0508 | WEST |  | 2025-11-25 02:45 | Praise Okezie | 2025-11-25 02:42 | 2025-11-25 03:13 | 1840 | 2025-11-25 02:42 | 2025-11-25 03:13 | 0:31 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Afolabi Ganiyyu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006472224 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0997C | OS4740 | IBD | Ibadan | Osun | 3 - Low | OS0721 | WEST |  | 2025-11-28 12:39 | Valentine Adinnu | 2025-11-28 12:38 | 2025-11-28 13:09 | 1840 | 2025-11-28 12:38 | 2025-11-28 13:09 | 0:31 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - RPM - Gas Flow | 2 / 2 | MTN NG, Airtel NG |  | Ben Johnson-Nsikan |  |  | Abiola Adegbiji | Babalola Babajide |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty solenoid was worked on | Faulty solenoid was worked on
NOCINC0006472521 | Internal Reconciliation | Site Down | P1 | IHS_OND_0789A | T3408 | IBD | Ibadan | Ondo | 3 - Low | ON0576 | WEST |  | 2025-11-28 13:26 | Maureen Uchehorke | 2025-11-28 13:26 | 2025-11-28 13:56 | 1835 | 2025-11-28 13:26 | 2025-11-28 13:56 | 0:31 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | MTN NG, Airtel NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Grid synchronization failure due to Grid incomplete phase, DG was powered manually
NOCINC0006443160 | External Reconciliation | Site Down | P1 | IHS_OYO_0034B | OY4245 | IBD | Ibadan | Kwara | 3 - Low | KW0313 | WEST |  | 2025-11-24 19:05 | Victor Otugo | 2025-11-24 19:03 | 2025-11-24 19:33 | 1833 | 2025-11-24 19:03 | 2025-11-24 19:33 | 0:31 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Emergency Stop Switch | 2 / 2 | Airtel NG, MTN NG |  | Mohammed Soliu |  | Abdulraman Odunola | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | DG failed to start alarm was cleared, DG power manually
NOCINC0006476505 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1126A | AN0439 | ASB | Asaba | Anambra | 3 - Low | AN0667 | SOUTH EAST |  | 2025-11-29 00:22 | Femi Olanipekun | 2025-11-29 00:22 | 2025-11-29 00:53 | 1828 | 2025-11-29 00:22 | 2025-11-29 00:53 | 0:30 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Clogged Radiator | 2 / 2 | MTN NG, Airtel NG |  | Amadi Fabian | Tijani Haruna | Tijani Haruna | Henry Wanogho | Ifeanyi Chukusa |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | High DG temperature, clogged radiator was flushed to power the site (No diesel outage after validation) | High DG temperature, clogged radiator was flushed to power the site (No diesel outage after validation)
NOCINC0006470277 | External Reconciliation | Site Down | P2 | IHS_BEN_0042B | ED2012 | IBD | Asaba | Edo | 3 - Low | ED1091 | SOUTH SOUTH |  | 2025-11-28 07:19 | Emmanuel Faleti | 2025-11-28 07:19 | 2025-11-28 07:49 | 1824 | 2025-11-28 07:19 | 2025-11-28 07:49 | 0:30 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 3 / 3 | Airtel NG, MTN NG, Smile |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | DG servicing was completed at site
NOCINC0006477765 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0049B | OS2681 | IBD | Ibadan | Osun | 3 - Low | OS0831 | WEST |  | 2025-11-29 08:04 | Titus Tosin | 2025-11-29 08:01 | 2025-11-29 08:31 | 1816 | 2025-11-29 08:01 | 2025-11-29 08:31 | 0:30 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Actuator | 2 / 2 | MTN NG, Airtel NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hooked actuator string was released
NOCINC0006462958 | External Reconciliation | Site Down | P4 | IHS_OND_0868A | T3871 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 07:55 | Yewande Adeagbo | 2025-11-27 07:53 | 2025-11-27 08:23 | 1811 | 2025-11-27 07:53 | 2025-11-27 08:23 | 0:30 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | Benjamin Onwu |  |  | Ibrahim Akinpelu | Benjamin Onwu |  | Victor Adeoye | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG undervoltage alarm was cleared
NOCINC0006442634 | External Reconciliation | Site Down | P4 | IHS_DEL_0878A | T2722 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 17:49 | Ezinne Ubachukwu | 2025-11-24 17:39 | 2025-11-24 18:09 | 1807 | 2025-11-24 17:39 | 2025-11-24 18:09 | 0:30 | Tyllium NGA | Equipment Repair | Passive | Hybrid | Hybrid Module | 1 / 1 | MTN NG |  | Monday Agha | Igwe Samuel | Igwe Samuel | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure, DG powered manually. ( No diesel outage after validation) | Hybrid synchronization failure, DG powered manually. ( No diesel outage after validation)
NOCINC0006479027 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-29 11:25 | Quadri Ogundare | 2025-11-29 11:24 | 2025-11-29 11:54 | 1803 | 2025-11-29 11:24 | 2025-11-29 11:54 | 0:30 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected passive, awaiting update
NOCINC0006459106 | External Reconciliation | Site Down | P2 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 16:38 | Azeezat Badmus | 2025-11-26 16:36 | 2025-11-26 17:06 | 1802 | 2025-11-26 16:36 | 2025-11-26 17:06 | 0:30 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is powered from ED4860. (No diesel outage after validation)
NOCINC0006439647 | External Reconciliation | Site Down | P2 | IHS_OSU_0042B | OS4285 | IBD | Ibadan | Osun | 3 - Low | OS0738 | WEST |  | 2025-11-24 11:52 | Azeezat Adekunle | 2025-11-24 11:48 | 2025-11-24 12:18 | 1802 | 2025-11-24 11:48 | 2025-11-24 12:18 | 0:30 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 2 / 2 | MTN NG, Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty solenoid coil was worked on
NOCINC0006461924 | External Reconciliation | Site Down | P4 | IHS_EDO_0836A | T3260 | IBD | Asaba | Edo | 3 - Low | ED1055 | SOUTH SOUTH |  | 2025-11-27 01:47 | Oluwatomisin Sogbesan | 2025-11-27 01:45 | 2025-11-27 02:15 | 1797 | 2025-11-27 01:45 | 2025-11-27 02:15 | 0:30 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low oil pressure alarm was cleared (No diesel outage after validation) | Low oil pressure alarm was cleared (No diesel outage after validation)
NOCINC0006464443 | External Reconciliation | Site Down | P2 | IHS_OND_0023B | OD4718 | IBD | Ibadan | Ondo | 3 - Low | ON0521 | WEST |  | 2025-11-27 12:09 | Iyesioluwa Ola | 2025-11-27 12:07 | 2025-11-27 12:37 | 1794 | 2025-11-27 12:07 | 2025-11-27 12:37 | 0:30 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Sanusi Idowu | Isah Ahmed |  | Soye West | Goddey Nwokedigbo Peter |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | hybrid synchronization failure due to frozen orion was reser
NOCINC0006490282 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0955A | T3674 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 23:01 | Damilola Paseda | 2025-11-30 23:00 | 2025-11-30 23:30 | 1793 | 2025-11-30 23:00 | 2025-11-30 23:30 | 0:30 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen SMU, SMU was reset | Hybrid synchronization failure due to frozen SMU, SMU was reset
NOCINC0006437373 | External Reconciliation | Site Down | P1 | IHS_OND_0847A | T3840 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 01:37 | Abisoye Olaleye | 2025-11-24 01:35 | 2025-11-24 02:05 | 1790 | 2025-11-24 01:35 | 2025-11-24 02:05 | 0:30 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Emmanuel Aja |  |  | Ibrahim Akinpelu | Emmanuel Aja |  | Oluwafemi Iyiola | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 4 | Hybrid synchronisation failure due to frozen smu,smu was reset and power was restored
NOCINC0006451921 | External Reconciliation | Site Down | P4 | IHS_OND_0044B | OD2575 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-25 21:08 | Ihuoma Opurum | 2025-11-25 21:07 | 2025-11-25 21:37 | 1788 | 2025-11-25 21:07 | 2025-11-25 21:37 | 0:30 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Module | 1 / 1 | MTN NG |  | Usman Hammed |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Grid-DG synchronization failure due to faulty DG module. DG was powered manually.
NOCINC0006467167 | External Reconciliation | Site Down | P4 | IHS_DEL_1196B | DL4059 | ASB | Asaba | Delta | 3 - Low | DL1139 | SOUTH SOUTH |  | 2025-11-27 18:42 | Uthman Akinola | 2025-11-27 18:39 | 2025-11-27 19:08 | 1786 | 2025-11-27 18:39 | 2025-11-27 19:08 | 0:30 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 3 / 3 | MTN NG, Airtel NG, Smile |  | Gabriel Akhamiogu |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled (No diesel outage after validation) | Tripped load breaker was enabled (No diesel outage after validation)
NOCINC0006473015 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1049A | AN0103 | ASB | Asaba | Anambra | 3 - Low | AN0526 | SOUTH EAST |  | 2025-11-28 14:49 | Gbemisola Adedeji | 2025-11-28 14:47 | 2025-11-28 15:17 | 1784 | 2025-11-28 14:47 | 2025-11-28 15:17 | 0:30 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Femi Balogun | Femi Balogun | Femi Balogun | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Weak DG was primed to start(No diesel outage after validation) | Weak DG was primed to start(No diesel outage after validation)
NOCINC0006480107 | Internal Reconciliation | Site Down | P2 | IHS_OND_0036B | OD4707 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 13:35 | Testimony Akinyemi | 2025-11-29 13:32 | 2025-11-29 14:02 | 1781 | 2025-11-29 13:32 | 2025-11-29 14:02 | 0:30 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Faulty Rectifier Modules was Reset
NOCINC0006449955 | External Reconciliation | Site Down | P2 | IHS_ANA_1397H | AN0372 | ASB | Asaba | Anambra | 3 - Low | AN0118 | SOUTH EAST |  | 2025-11-25 16:28 | Ezinne Ubachukwu | 2025-11-25 16:26 | 2025-11-25 16:55 | 1778 | 2025-11-25 16:26 | 2025-11-25 16:55 | 0:30 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | MTN NG, Airtel NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | frozen CSU was reset | frozen CSU was rest
NOCINC0006457808 | External Reconciliation | Site Down | P1 | IHS_OND_0804A | T3437 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 13:19 | Iyesioluwa Ola | 2025-11-26 13:19 | 2025-11-26 13:49 | 1776 | 2025-11-26 13:19 | 2025-11-26 13:49 | 0:30 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 4 | start failure alarm was cleared and GG restarted
NOCINC0006443949 | External Reconciliation | Site Down | P4 | IHS_OYO_1066A | OY4077 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 21:19 | Valentine Adinnu | 2025-11-24 21:17 | 2025-11-24 21:47 | 1776 | 2025-11-24 21:17 | 2025-11-24 21:47 | 0:30 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen SMU, SMU was reset | Hybrid synchronization failure due to frozen SMU, SMU was reset
NOCINC0006488213 | Internal Reconciliation | Site Down | P3 | IHS_EDO_1026A | ED2161 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 16:15 | Evelyn Emagurehor | 2025-11-30 16:13 | 2025-11-30 16:43 | 1770 | 2025-11-30 16:13 | 2025-11-30 16:43 | 0:30 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 2 | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006445487 | External Reconciliation | Site Down | P3 | IHS_ANA_0709E | AN1044 | ASB | Asaba | Anambra | 3 - Low | AN0674 | SOUTH EAST |  | 2025-11-25 06:01 | Solomon Bankole | 2025-11-25 06:00 | 2025-11-25 06:30 | 1764 | 2025-11-25 06:00 | 2025-11-25 06:30 | 0:29 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | Airtel NG |  | Idowu Dare |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG under frequency alarm cleared, Governor was adjusted ( No diesel outage after validation) | DG under frequency alarm cleared, Governor was adjusted ( No diesel outage after validation)
NOCINC0006445594 | External Reconciliation | Site Down | P2 | IHS_DEL_1114A | DL0709 | ASB | Asaba | Delta | 3 - Low | DL1018 | SOUTH SOUTH |  | 2025-11-25 06:44 | Solomon Bankole | 2025-11-25 06:43 | 2025-11-25 07:12 | 1763 | 2025-11-25 06:43 | 2025-11-25 07:12 | 0:29 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Failed charging Alternator was excited
NOCINC0006459947 | External Reconciliation | Site Down | P1 | IHS_KWA_0831A | KW3805 | IBD | Ibadan | Kwara | 3 - Low | KW0653 | WEST |  | 2025-11-26 19:05 | Titus Tosin | 2025-11-26 19:04 | 2025-11-26 19:34 | 1761 | 2025-11-26 19:04 | 2025-11-26 19:34 | 0:29 | IPT | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 1 / 2 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Grid to DG synchronization failure due to incomplete phase, DG was powered manually.
NOCINC0006477573 | Internal Reconciliation | Site Down | P4 | IHS_IBA_0706E | OY4354 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 07:17 | Bosede Kutelu | 2025-11-29 07:15 | 2025-11-29 07:45 | 1760 | 2025-11-29 07:15 | 2025-11-29 07:45 | 0:29 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Over Frequency | 1 / 1 | MTN NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG over frequency was adjusted
NOCINC0006445123 | External Reconciliation | Site Down | P3 | IHS_OSU_0800A | T3086 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 03:03 | Valentine Adinnu | 2025-11-25 02:55 | 2025-11-25 03:24 | 1760 | 2025-11-25 02:55 | 2025-11-25 03:24 | 0:29 | IPT | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 1 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Grid to DG synchronisation failure due to unstable grid supply, DG was powered manually | Grid to DG synchronisation failure due to unstable grid supply, DG was powered manually
NOCINC0006451125 | External Reconciliation | Site Down | P3 | IHS_OYO_1321B | OY1102 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 19:13 | Mutmainnah Saba | 2025-11-25 19:10 | 2025-11-25 19:39 | 1759 | 2025-11-25 19:10 | 2025-11-25 19:39 | 0:29 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Oremade Yusuf |  |  | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG underfrequency alarm was adjusted
NOCINC0006487694 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1105A | DL0505 | ASB | Asaba | Delta | 3 - Low | DL0678 | SOUTH SOUTH |  | 2025-11-30 14:56 | Ayomide Akindolie | 2025-11-30 14:56 | 2025-11-30 15:25 | 1759 | 2025-11-30 14:56 | 2025-11-30 15:25 | 0:29 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Insufficient rectifier module, module was added (No diesel outage after validation) | Insufficient rectifier module, module was added (No diesel outage after validation)
NOCINC0006478897 | Internal Reconciliation | Site Down | P1 | IHS_OND_0829A | T3950 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 11:08 | System Administrator | 2025-11-29 10:55 | 2025-11-29 11:01 | 361 | 2025-11-29 10:54 | 2025-11-29 11:23 | 0:29 | IPT | Equipment Repair | Passive | Rectifier | Rectifier - Phase Controller | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty Rectifier Phase Controller Worked On
NOCINC0006443031 | External Reconciliation | Site Down | P3 | IHS_KWA_0939C | KW6391 | IBD | Ibadan | Kwara | 3 - Low | KW0598 | WEST |  | 2025-11-24 18:40 | Precious Attah | 2025-11-24 18:39 | 2025-11-24 19:08 | 1755 | 2025-11-24 18:39 | 2025-11-24 19:08 | 0:29 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG under voltage alarm was cleared
NOCINC0006455706 | External Reconciliation | Site Down | P3 | IHS_KWA_0875A | KW2314 | IBD | Ibadan | Kwara | 3 - Low | KW0446 | WEST |  | 2025-11-26 07:36 | Azeezat Adekunle | 2025-11-26 07:34 | 2025-11-26 08:03 | 1751 | 2025-11-26 07:34 | 2025-11-26 08:03 | 0:29 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | David Oyebamiji |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed rectifier module was reset
NOCINC0006443966 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-24 21:22 | Kehinde Akinbowale | 2025-11-24 21:15 | 2025-11-24 21:44 | 1746 | 2025-11-24 21:15 | 2025-11-24 21:44 | 0:29 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Weak DG was primed to start(No diesel outage after validation) | Weak DG was primed to start(No diesel outage after validation)
NOCINC0006472404 | Internal Reconciliation | Site Down | P3 | IHS_OND_0058B | OD4813 | IBD | Ibadan | Ondo | 3 - Low | ON0686 | WEST |  | 2025-11-28 13:06 | Testimony Akinyemi | 2025-11-28 13:03 | 2025-11-28 13:32 | 1742 | 2025-11-28 13:03 | 2025-11-28 13:32 | 0:29 | IPT | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 2 / 2 | MTN NG, Airtel NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Panned Activity Passive with access ref: IHSREF/25112713532667734298 was carried out
NOCINC0006448799 | External Reconciliation | Site Down | P1 | IHS_ANA_1095A | AN0423 | ASB | Asaba | Anambra | 3 - Low | AN0573 | SOUTH EAST |  | 2025-11-25 13:48 | Aderonke Olowojoba | 2025-11-25 13:45 | 2025-11-25 14:14 | 1740 | 2025-11-25 13:45 | 2025-11-25 14:14 | 0:29 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 2 / 2 | MTN NG, Airtel NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty solenoid cable was re-terminated (No diesel outage after validation) | Faulty solenoid cable was re-terminated (No diesel outage after validation)
NOCINC0006483590 | Internal Reconciliation | Site Down | P4 | IHS_OND_0976A | OD2556 | IBD | Ibadan | Edo | 3 - Low | - | - |  | 2025-11-29 22:48 | Abisoye Olaleye | 2025-11-29 22:47 | 2025-11-29 23:16 | 1739 | 2025-11-29 22:47 | 2025-11-29 23:16 | 0:29 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | MTN NG |  | Benjamin Onwu |  |  | Ibrahim Akinpelu | Benjamin Onwu |  | Victor Adeoye | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | undervoltage alarm was cleared
NOCINC0006462994 | External Reconciliation | Site Down | P4 | IHS_EDO_0836A | T3260 | IBD | Asaba | Edo | 3 - Low | ED1055 | SOUTH SOUTH |  | 2025-11-27 08:07 | Oluwatomisin Sogbesan | 2025-11-27 08:06 | 2025-11-27 08:35 | 1735 | 2025-11-27 08:06 | 2025-11-27 08:35 | 0:29 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | Airtel NG, MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on (No diesel outage after validation) | Faulty ATS contactor was worked on
NOCINC0006490114 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0996A | ED4860 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 22:20 | Azeezat Badmus | 2025-11-30 22:19 | 2025-11-30 22:48 | 1734 | 2025-11-30 22:19 | 2025-11-30 22:48 | 0:29 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006484329 | Internal Reconciliation | Site Down | P4 | IHS_OND_0044B | OD2575 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 03:10 | Abisoye Olaleye | 2025-11-30 03:08 | 2025-11-30 03:37 | 1734 | 2025-11-30 03:08 | 2025-11-30 03:37 | 0:29 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Usman Hammed |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to dg delay to start. DG was powered manually.
NOCINC0006468207 | External Reconciliation | Site Down | P4 | IHS_OYO_1447B | - | - | Ibadan | Oyo | 3 - Low | OY1565 | WEST |  | 2025-11-27 21:55 | Ifechi Ugwueze | 2025-11-27 21:49 | 2025-11-27 22:18 | 1734 | 2025-11-27 21:49 | 2025-11-27 22:18 | 0:29 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | Airtel NG |  | Mohammed Soliu |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | ACDG Load breaker was replaced
NOCINC0006466603 | External Reconciliation | Site Down | P1 | IHS_DEL_1032A | DL0344 | ASB | Asaba | Delta | 3 - Low | DL1259 | SOUTH SOUTH |  | 2025-11-27 17:06 | Bukola Olabanji | 2025-11-27 17:03 | 2025-11-27 17:32 | 1726 | 2025-11-27 17:03 | 2025-11-27 17:32 | 0:29 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed rectifier module was replaced (no diesel outage after validation).
NOCINC0006485132 | Internal Reconciliation | Site Down | P3 | IHS_DEL_0798A | T2622 | ASB | Asaba | Delta | 3 - Low | DL0802 | SOUTH SOUTH |  | 2025-11-30 07:41 | Uthman Akinola | 2025-11-30 07:40 | 2025-11-30 08:09 | 1723 | 2025-11-30 07:40 | 2025-11-30 08:09 | 0:29 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | tripped DG load breaker due to partial contact of cables, breaker was tighten and DG powered (No diesel outage after validation) | tripped DG load breaker due to partial contact of cables, breaker was tighten and DG powered (No diesel outage after validation)
NOCINC0006467187 | External Reconciliation | Site Down | P2 | IHS_OSU_0876A | T3672 | IBD | Ibadan | Osun | 3 - Low | OS0670 | WEST |  | 2025-11-27 18:46 | Titus Tosin | 2025-11-27 18:46 | 2025-11-27 19:14 | 1720 | 2025-11-27 18:46 | 2025-11-27 19:14 | 0:29 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | DG under frequency alarm was cleared and DG was powered manually
NOCINC0006465252 | External Reconciliation | Site Down | P4 | IHS_ANA_1119A | AN0681 | ASB | Asaba | Anambra | 3 - Low | AN0854 | SOUTH EAST |  | 2025-11-27 13:55 | Gbemisola Adedeji | 2025-11-27 13:52 | 2025-11-27 14:20 | 1712 | 2025-11-27 13:52 | 2025-11-27 14:20 | 0:29 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | ThankGod Amadi | Femi Balogun | Femi Balogun | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG under voltage, AVR was adjusted (No diesel outage after validation). | DG under voltage, AVR was adjusted (No diesel outage after validation).
NOCINC0006443914 | External Reconciliation | Site Down | P2 | IHS_DEL_0731E | DL1019 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-24 21:00:45@DL1019_Magnes Onyibe Street | 2025-11-24 21:14 | System Administrator | 2025-11-24 21:07 | 2025-11-24 21:36 | 1710 | 2025-11-24 21:07 | 2025-11-24 21:36 | 0:29 | Tyllium NGA | Equipment Repair | Passive | Hybrid | Hybrid Module | 1 / 1 | MTN NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization failure. Dg was powered manually ( No diesel outage after validation) | Hybrid synchronization failure. Dg was powered manually ( No diesel outage after validation)
NOCINC0006440926 | External Reconciliation | Site Down | P2 | IHS_IBA_0112C | OY4360 | IBD | Ibadan | Oyo | 3 - Low | OY1631 | WEST |  | 2025-11-24 14:29 | Aishat Oyedeji | 2025-11-24 14:27 | 2025-11-24 14:56 | 1709 | 2025-11-24 14:27 | 2025-11-24 14:56 | 0:28 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | failed charging alternator was excited | failed charging alternator was excited
NOCINC0006473214 | Internal Reconciliation | Site Down | P3 | IHS_BOM_0002B | DL0769 | ASB | Asaba | Delta | 3 - Low | DL0803 | SOUTH SOUTH |  | 2025-11-28 15:14 | Bukola Olabanji | 2025-11-28 15:10 | 2025-11-28 15:39 | 1708 | 2025-11-28 15:10 | 2025-11-28 15:39 | 0:28 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 2 / 2 | MTN NG, Airtel NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty solenoid coil was worked on (no diesel outage after validation).
NOCINC0006456410 | External Reconciliation | Site Down | P3 | IHS_EDO_0906A | T3377 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 09:58 | Emmanuel Faleti | 2025-11-26 09:56 | 2025-11-26 10:24 | 1708 | 2025-11-26 09:56 | 2025-11-26 10:24 | 0:28 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Hybrid system was reset due to synchronization failure (No diesel outage after validation) | Hybrid system was reset due to synchronization failure (No diesel outage after validation)
NOCINC0006487274 | Internal Reconciliation | Site Down | P1 | IHS_OND_0764A | T3400 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 13:43 | Ihuoma Opurum | 2025-11-30 13:42 | 2025-11-30 14:10 | 1699 | 2025-11-30 13:42 | 2025-11-30 14:10 | 0:28 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 1 / 1 | MTN NG |  | Mercy Oni |  | Ojadua Olusegun | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Grid to DG synchronization failure due to incomplete phase from Grid. DG was powered manually
NOCINC0006482269 | Internal Reconciliation | Site Down | P1 | IHS_OND_0970A | OD4722 | IBD | Ibadan | Ondo | 3 - Low | ON0627 | WEST |  | 2025-11-29 19:00 | Maureen Uchehorke | 2025-11-29 19:00 | 2025-11-29 19:28 | 1696 | 2025-11-29 19:00 | 2025-11-29 19:28 | 0:28 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | hybrid synchronization failure due to frozen CSU, CSU was reset
NOCINC0006475638 | Internal Reconciliation | Site Down | P4 | IHS_BEN_0078C | ED5153 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 21:08 | Elizabeth Apata | 2025-11-28 21:04 | 2025-11-28 21:32 | 1686 | 2025-11-28 21:04 | 2025-11-28 21:32 | 0:28 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | High DG temperature Coolant was added (No diesel outage after validation)
NOCINC0006488800 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0708E | OY4493 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 17:51 | Precious Attah | 2025-11-30 17:49 | 2025-11-30 18:17 | 1682 | 2025-11-30 17:49 | 2025-11-30 18:17 | 0:28 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | DG lost compression, Weak DG was primed to start
NOCINC0006441693 | External Reconciliation | Site Down | P4 | IHS_OSU_0873A | T3665 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 16:13 | Hardy Oko | 2025-11-24 16:11 | 2025-11-24 16:39 | 1680 | 2025-11-24 16:11 | 2025-11-24 16:39 | 0:28 | IPT | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization delay. DG was powered manually
NOCINC0006482093 | Internal Reconciliation | Site Down | P4 | IHS_OND_0945A | OD2568 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 18:26 | System Administrator | 2025-11-29 18:11 | 2025-11-29 18:39 | 1680 | 2025-11-29 18:11 | 2025-11-29 18:39 | 0:28 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Failed Rectifier Module Reset
NOCINC0006484786 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1208A | AN0578 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 06:04 | Gbemisola Adedeji | 2025-11-30 06:00 | 2025-11-30 06:28 | 1679 | 2025-11-30 06:00 | 2025-11-30 06:28 | 0:28 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Madu Modestus | Madu Modestus | Madu Modestus | Fady Safwat | Aliyu Garuba |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | DG under frequency, governor was adjusted (No diesel outage after validation). | DG under frequency, governor was adjusted (No diesel outage after validation).
NOCINC0006471824 | Internal Reconciliation | Site Down | P3 | IHS_OSU_1046B | OS4748 | IBD | Ibadan | Osun | 3 - Low | OS0760 | WEST |  | 2025-11-28 11:32 | Oluwatomisin Ogunleye | 2025-11-28 11:31 | 2025-11-28 11:59 | 1678 | 2025-11-28 11:31 | 2025-11-28 11:59 | 0:28 | IPT | Fuel Outage (Probable) | Passive | Diesel | Diesel Top-Up | 2 / 2 | MTN NG, Airtel NG |  | Odufu Friday |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Low diesel pressure, diesel was topped | Low diesel pressure, diesel was topped
NOCINC0006439911 | External Reconciliation | Site Down | P2 | IHS_OYO_1071A | OY2862 | IBD | Ibadan | Oyo | 3 - Low | OY1052 | WEST |  | 2025-11-24 12:51 | Hardy Oko | 2025-11-24 12:50 | 2025-11-24 13:18 | 1677 | 2025-11-24 12:50 | 2025-11-24 13:18 | 0:28 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 2 | MTN NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Hybrid synchronisation failure due to failed SMU ,SMU was reset
NOCINC0006437702 | External Reconciliation | Site Down | P1 | IHS_DEL_0765A | T0154 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 04:25 | Bukola Olabanji | 2025-11-24 04:16 | 2025-11-24 04:43 | 1676 | 2025-11-24 04:16 | 2025-11-24 04:43 | 0:28 | BJ Bison NGA | Equipment Repair | Passive | Environmental | Aircon Switch Faulty | 1 / 1 | MTN NG |  | Babatunde Jimoh� |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty aircon switch was worked on
NOCINC0006457774 | External Reconciliation | Site Down | P2 | IHS_EDO_0966A | ED2023 | IBD | Asaba | Edo | 3 - Low | ED0641 | SOUTH SOUTH |  | 2025-11-26 13:12 | Azeezat Badmus | 2025-11-26 13:11 | 2025-11-26 13:39 | 1676 | 2025-11-26 13:11 | 2025-11-26 13:39 | 0:28 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Olusoji Megbodofo |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty charging alternator was worked on (No diesel outage after validation) | Faulty charging alternator was worked on (No diesel outage after validation)
NOCINC0006465923 | External Reconciliation | Site Down | P1 | IHS_DEL_0896A | T2777 | ASB | Asaba | Delta | 3 - Low | DL0250 | SOUTH SOUTH |  | 2025-11-27 15:26 | Uthman Akinola | 2025-11-27 15:26 | 2025-11-27 15:54 | 1669 | 2025-11-27 15:26 | 2025-11-27 15:54 | 0:28 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Tripped dg load breaker due to over load (no diesel outage after validation)
NOCINC0006474678 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-28 18:39 | Kehinde Akinbowale | 2025-11-28 18:37 | 2025-11-28 19:05 | 1668 | 2025-11-28 18:37 | 2025-11-28 19:05 | 0:28 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | Airtel NG, MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under voltage alarm was cleared(No diesel outage after validation) | DG under voltage alarm was cleared(No diesel outage after validation)
NOCINC0006451137 | External Reconciliation | Site Down | P3 | IHS_KWA_0939C | KW6391 | IBD | Ibadan | Kwara | 3 - Low | KW0598 | WEST |  | 2025-11-25 19:17 | Precious Attah | 2025-11-25 19:16 | 2025-11-25 19:44 | 1667 | 2025-11-25 19:16 | 2025-11-25 19:44 | 0:28 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG under voltage alarm was cleared
NOCINC0006481304 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1185A | DL0719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-29 16:06:01@DL0719_NO 6 Old Warri Road Okuvweri | 2025-11-29 16:18 | System Administrator | 2025-11-29 16:13 | 2025-11-29 16:28 | 930 | 2025-11-29 16:13 | 2025-11-29 16:40 | 0:27 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 1 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | IHSREF/25112817313968548478 SARID0009102597 IHS_DEL_1185A ‎Name: Daniel Asuquo Usunginwang ‎Phone number: 09169270067 ‎Company: Uziben ‎Purpose: RMS snag clearance ‎Date: 29/11/2025 ‎ ‎ | IHSREF/25112817313968548478 SARID0009102597 IHS_DEL_1185A ‎Name: Daniel Asuquo Usunginwang ‎Phone number: 09169270067 ‎Company: Uziben ‎Purpose: RMS snag clearance ‎Date: 29/11/2025 ‎
NOCINC0006473252 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1164A | DL0626 | ASB | Asaba | Delta | 3 - Low | DL0600 | SOUTH SOUTH |  | 2025-11-28 15:22 | Bukola Olabanji | 2025-11-28 15:21 | 2025-11-28 15:48 | 1649 | 2025-11-28 15:21 | 2025-11-28 15:48 | 0:27 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | Airtel NG, MTN NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Low coolant level, coolant was added (no diesel outage after validation).
NOCINC0006452913 | External Reconciliation | Site Down | P1 | IHS_DEL_1040A | DL0093 | ASB | Asaba | Delta | 3 - Low | DL0621 | SOUTH SOUTH |  | 2025-11-26 00:22 | Ayomide Akindolie | 2025-11-26 00:21 | 2025-11-26 00:48 | 1646 | 2025-11-26 00:21 | 2025-11-26 00:48 | 0:27 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was worked on (No diesel outage after validation)
NOCINC0006471987 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0753A | T3114 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 11:59 | Praise Okezie | 2025-11-28 11:53 | 2025-11-28 12:20 | 1645 | 2025-11-28 11:53 | 2025-11-28 12:20 | 0:27 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Bello Saheed |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out on site
NOCINC0006449205 | External Reconciliation | Site Down | P4 | IHS_EKI_0013B | EK2273 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-25 14:42 | Tunji Adejumo | 2025-11-25 14:41 | 2025-11-25 15:08 | 1645 | 2025-11-25 14:41 | 2025-11-25 15:08 | 0:27 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid Synchronisation failure due to over voltage discharge alarm was cleared
NOCINC0006470233 | External Reconciliation | Site Down | P3 | IHS_OSU_0919A | OS3637 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 07:06 | Marvellous Emecheta | 2025-11-28 07:00 | 2025-11-28 07:28 | 1645 | 2025-11-28 07:00 | 2025-11-28 07:28 | 0:27 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | MTN NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Suspected passive issue at site awaiting RCA from FSE
NOCINC0006485766 | Internal Reconciliation | Site Down | P2 | IHS_OND_0838A | T3930 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 09:58 | Ihuoma Opurum | 2025-11-30 09:58 | 2025-11-30 10:25 | 1644 | 2025-11-30 09:58 | 2025-11-30 10:25 | 0:27 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - High Rectifier Temp | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 3 | High rectifier temperature due to faulty sensor. Rectifier temperature sensor was worked on.
NOCINC0006441728 | External Reconciliation | Site Down | P1 | IHS_WAR_0879H | T2907 | ASB | Asaba | Delta | 3 - Low | DL0635 | SOUTH SOUTH |  | 2025-11-24 16:19 | Ayomide Akindolie | 2025-11-24 16:19 | 2025-11-24 16:46 | 1643 | 2025-11-24 16:19 | 2025-11-24 16:46 | 0:27 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on | Faulty injector pump was worked on (No diesel outage after validation).
NOCINC0006457680 | External Reconciliation | Site Down | P2 | IHS_OSU_0929A | OS2725 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 12:54 | Ifechi Ugwueze | 2025-11-26 12:51 | 2025-11-26 13:18 | 1640 | 2025-11-26 12:51 | 2025-11-26 13:18 | 0:27 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Low Oil Pressure | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Low oil Pressure, oil was added
NOCINC0006474449 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-28 18:11 | Kehinde Akinbowale | 2025-11-28 18:07 | 2025-11-28 18:34 | 1634 | 2025-11-28 18:07 | 2025-11-28 18:34 | 0:27 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Over Voltage | 2 / 2 | Airtel NG, MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG over voltage alarm, AVR was adjusted(No diesel outage after validation) | DG over voltage alarm, AVR was adjusted(No diesel outage after validation)
NOCINC0006460438 | External Reconciliation | Site Down | P1 | IHS_EDO_0993A | ED2116 | IBD | Asaba | Edo | 3 - Low | ED0800 | SOUTH SOUTH |  | 2025-11-26 20:26 | Azeezat Badmus | 2025-11-26 20:19 | 2025-11-26 20:46 | 1633 | 2025-11-26 20:19 | 2025-11-26 20:46 | 0:27 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | EKPU SUNDAY | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on to restore power on site (No diesel outage after validation) | Faulty injector pump was worked on to restore power on site (No diesel outage after validation)
NOCINC0006445689 | External Reconciliation | Site Down | P2 | IHS_OSU_0892A | T3074 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 07:13 | Praise Okezie | 2025-11-25 07:11 | 2025-11-25 07:38 | 1631 | 2025-11-25 07:11 | 2025-11-25 07:38 | 0:27 | IPT | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 1 | MTN NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to Unstable Grid Supply Issue, DG powered manually.
NOCINC0006462314 | External Reconciliation | Site Down | P2 | IHS_EDO_0017B | ED5089 | IBD | Asaba | Edo | 3 - Low | ED0663 | SOUTH SOUTH |  | 2025-11-27 05:04 | Oluwatomisin Sogbesan | 2025-11-27 05:02 | 2025-11-27 05:29 | 1630 | 2025-11-27 05:02 | 2025-11-27 05:29 | 0:27 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was replaced (No diesel outage after validation) | Failed charging alternator was replaced (No diesel outage after validation)
NOCINC0006465099 | External Reconciliation | Site Down | P4 | IHS_OSU_0875A | OS3995 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 13:29 | Okusanya Joseph | 2025-11-27 13:27 | 2025-11-27 13:54 | 1623 | 2025-11-27 13:27 | 2025-11-27 13:54 | 0:27 | IPT | Equipment Repair | Passive | ACDG Gen | Gen Temp High | 1 / 1 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | High engine temperature due to blocked radiator, coolant was added and radiator was flushed.
NOCINC0006487232 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1259B | ED1180 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 13:34 | Oluwatomisin Sogbesan | 2025-11-30 13:32 | 2025-11-30 13:59 | 1622 | 2025-11-30 13:32 | 2025-11-30 13:59 | 0:27 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Lifting Pump Faulty | 1 / 1 | MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty hand primer was replaced to restore the site. (No diesel outage after validation). | Faulty hand primer was replaced to restore the site. (No diesel outage after validation).
NOCINC0006439505 | External Reconciliation | Site Down | P1 | IHS_ANA_0793A | T0246 | ASB | Asaba | Anambra | 3 - Low | AN0533 | SOUTH EAST |  | 2025-11-24 11:21 | Aderonke Olowojoba | 2025-11-24 11:18 | 2025-11-24 11:45 | 1621 | 2025-11-24 11:18 | 2025-11-24 11:45 | 0:27 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low oil pressure, oil added. (No diesel outage after validation) | Low oil pressure, oil added. (No diesel outage after validation)
NOCINC0006487723 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0826A | KW2302 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-30 14:59 | Ihuoma Opurum | 2025-11-30 14:57 | 2025-11-30 15:24 | 1614 | 2025-11-30 14:57 | 2025-11-30 15:24 | 0:27 | IPT | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Enorch Dauda |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify | 2 | Hybrid synchronization delay. DG was powered manually
NOCINC0006462828 | External Reconciliation | Site Down | P3 | IHS_ILO_0031B | KW4580 | IBD | Ibadan | Kwara | 3 - Low | KW0666 | West |  | 2025-11-27 07:24 | Precious Attah | 2025-11-27 07:22 | 2025-11-27 07:49 | 1614 | 2025-11-27 07:22 | 2025-11-27 07:49 | 0:27 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Olapade Babatunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Tripped load breaker enabled
NOCINC0006442885 | External Reconciliation | Site Down | P1 | IHS_KWA_0759A | T3136 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 18:21 | Azeezat Adekunle | 2025-11-24 18:10 | 2025-11-24 18:37 | 1614 | 2025-11-24 18:10 | 2025-11-24 18:37 | 0:27 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | faulty injector pump was worked on
NOCINC0006490382 | Resolved | Site Down | P1 | IHS_EDO_0996A | ED4860 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 23:36 | Azeezat Badmus | 2025-11-30 23:33 | 2025-12-01 00:21 | 2887 | 2025-11-30 23:33 | 2025-12-01 | 0:27 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006439278 | External Reconciliation | Site Down | P1 | IHS_EDO_0755A | T0230 | IBD | Asaba | Edo | 3 - Low | ED0450 | SOUTH SOUTH |  | 2025-11-24 10:36 | Oluwatomisin Sogbesan | 2025-11-24 10:35 | 2025-11-24 11:02 | 1610 | 2025-11-24 10:35 | 2025-11-24 11:02 | 0:27 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 3 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Faulty ATS contactor was worked on (No diesel outage after validation) | Faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006490160 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1063A | OY2926 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 22:32 | Valentine Adinnu | 2025-11-30 22:31 | 2025-11-30 22:58 | 1610 | 2025-11-30 22:31 | 2025-11-30 22:58 | 0:27 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Effiong Asukwo |  |  | Paul Akpomie | Effiong Asukwo |  | Victor Olanrewaju | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen SMU, SMU was reset | Hybrid synchronization failure due to frozen SMU, SMU was reset
NOCINC0006448275 | External Reconciliation | Site Down | P4 | IHS_EDO_1045C | ED6119 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 12:53 | Emmanuel Faleti | 2025-11-25 12:52 | 2025-11-25 13:19 | 1602 | 2025-11-25 12:52 | 2025-11-25 13:19 | 0:27 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Priming Motor Faulty | 1 / 1 | MTN NG |  | Kazeem Ajiboye |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty hand primer pump was serviced to restore power on site (No diesel outage after validation) | Faulty hand primer pump was serviced to restore power on site (No diesel outage after validation)
NOCINC0006482795 | Internal Reconciliation | Site Down | P2 | IHS_AWK_0002B | AN3769 | ASB | Asaba | Anambra | 3 - Low | AN0451 | SOUTH EAST |  | 2025-11-29 20:40 | Gbemisola Adedeji | 2025-11-29 20:38 | 2025-11-29 21:04 | 1601 | 2025-11-29 20:38 | 2025-11-29 21:04 | 0:27 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ugwuja Chinonso |  |  | Erik Nwodo | Nwigbo Chijioke |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | DG under voltage, AVR was adjusted (No diesel outage after validation). | DG under voltage, AVR was adjusted (No diesel outage after validation).
NOCINC0006483692 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0726E | ED6177 | IBD | Asaba | Edo | 3 - Low | ED0473 | SOUTH SOUTH |  | 2025-11-29 23:08 | Muhammed Hashirudeen | 2025-11-29 23:07 | 2025-11-29 23:33 | 1577 | 2025-11-29 23:07 | 2025-11-29 23:33 | 0:27 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Interface Module Faulty | 3 / 3 | Airtel NG, MTN NG, Smile |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Fraulty DG module was worked on (No diesel outage after validation)
NOCINC0006488272 | Internal Reconciliation | Site Down | P1 | IHS_AWK_0016B | AN0088 | ASB | Asaba | Anambra | 3 - Low | AN0662 | SOUTH EAST |  | 2025-11-30 16:21 | Ayokunle Samuel | 2025-11-30 16:20 | 2025-11-30 16:30 | 553 | 2025-11-30 16:19 | 2025-11-30 16:46 | 0:27 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Air Intake | 2 / 2 | MTN NG, Airtel NG |  | Egbujor Victor | Hillary Uduak | Hillary Uduak | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Air intake was flushed out. (No diesel outage after validation) | Air intake was flushed out. (No diesel outage after validation)
NOCINC0006463195 | External Reconciliation | Site Down | P3 | IHS_OSU_0058B | OS4265 | IBD | Ibadan | Osun | 3 - Low | OS0701 | WEST |  | 2025-11-27 08:54 | Mutmainnah Saba | 2025-11-27 08:49 | 2025-11-27 09:16 | 1587 | 2025-11-27 08:49 | 2025-11-27 09:16 | 0:26 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on
NOCINC0006448554 | External Reconciliation | Site Down | P3 | IHS_ANA_1005A | T4856 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 13:30 | Ezinne Ubachukwu | 2025-11-25 13:25 | 2025-11-25 13:52 | 1586 | 2025-11-25 13:25 | 2025-11-25 13:52 | 0:26 | BJ Bison NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Emmanuel Emmanuel | Henry Ubawuchi | Henry Ubawuchi | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Hybrid Synchronization failure, DG powered manually (No diesel outage after validation) | Hybrid Synchronization failure, DG powered manually (No diesel outage after validation)
NOCINC0006490278 | Resolved | Site Down | P1 | IHS_EDO_0996A | ED4860 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 22:59 | Azeezat Badmus | 2025-11-30 22:56 | 2025-11-30 23:23 | 1582 | 2025-11-30 22:56 | 2025-11-30 23:23 | 0:26 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006459383 | External Reconciliation | Site Down | P3 | IHS_EDO_1091C | ED6182 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 17:26 | Emmanuel Faleti | 2025-11-26 17:25 | 2025-11-26 17:52 | 1580 | 2025-11-26 17:25 | 2025-11-26 17:52 | 0:26 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 1 / 1 | MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty kick starter was worked on. (No diesel outage after validation) | Faulty kick starter was worked on. (No diesel outage after validation)
NOCINC0006458662 | External Reconciliation | Site Down | P3 | IHS_KWA_0835A | KW3151 | IBD | Ibadan | Kwara | 3 - Low | KW0376 | WEST |  | 2025-11-26 15:29 | Titus Tosin | 2025-11-26 15:28 | 2025-11-26 15:54 | 1577 | 2025-11-26 15:28 | 2025-11-26 15:54 | 0:26 | IPT | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Olapade Babatunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronisation failure due to dg failed to start alarm was cleared and powered manually
NOCINC0006465281 | External Reconciliation | Site Down | P1 | IHS_DEL_0896A | T2777 | ASB | Asaba | Delta | 3 - Low | DL0250 | SOUTH SOUTH |  | 2025-11-27 13:58 | Uthman Akinola | 2025-11-27 13:58 | 2025-11-27 14:24 | 1576 | 2025-11-27 13:58 | 2025-11-27 14:24 | 0:26 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Tripped DG load breaker was enabled (No diesel outage after validation) | Tripped DG load breaker was enabled (No diesel outage after validation)
NOCINC0006485792 | Internal Reconciliation | Site Down | P4 | IHS_OND_0048B | OD2585 | IBD | Ibadan | Edo | 3 - Low | - | - |  | 2025-11-30 10:04 | Yewande Adeagbo | 2025-11-30 10:03 | 2025-11-30 10:29 | 1571 | 2025-11-30 10:03 | 2025-11-30 10:29 | 0:26 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG Was Primed To Start
NOCINC0006464733 | External Reconciliation | Site Down | P4 | IHS_ANA_1028A | AN0022 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 12:35 | Femi Olanipekun | 2025-11-27 12:33 | 2025-11-27 12:59 | 1569 | 2025-11-27 12:33 | 2025-11-27 12:59 | 0:26 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Team confirmed high DG temperature, coolant was added to power the site (No diesel outage after validation) | Team confirmed high DG temperature, coolant was added to power the site (No diesel outage after validation)
NOCINC0006444265 | External Reconciliation | Site Down | P3 | IHS_EDO_0906A | T3377 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 22:14 | Azeezat Badmus | 2025-11-24 22:11 | 2025-11-24 22:37 | 1566 | 2025-11-24 22:11 | 2025-11-24 22:37 | 0:26 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Module | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure,Dg powered manually (No diesel outage after validation)
NOCINC0006484990 | Internal Reconciliation | Site Down | P1 | IHS_NNE_0002B | AN0055 | ASB | Asaba | Anambra | 3 - Low | AN0436 | SOUTH EAST |  | 2025-11-30 07:07 | Gbemisola Adedeji | 2025-11-30 07:06 | 2025-11-30 07:32 | 1566 | 2025-11-30 07:06 | 2025-11-30 07:32 | 0:26 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Ukanwa Reginald | Ukanwa Karachi | Ukanwa Karachi | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation). | Failed charging alternator was excited (No diesel outage after validation).
NOCINC0006451010 | External Reconciliation | Site Down | P4 | IHS_EDO_1048C | ED6125 | IBD | Asaba | Edo | 3 - Low | - | - | CSL Fault@2025-11-25 18:48:26@ED6125_ADESUWA GRAMMAR SCHL | 2025-11-25 19:02 | System Administrator | 2025-11-25 18:48 | 2025-11-25 19:15 | 1565 | 2025-11-25 18:48 | 2025-11-25 19:15 | 0:26 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006439642 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-24 11:51 | Ayomide Akindolie | 2025-11-24 11:51 | 2025-11-24 12:17 | 1565 | 2025-11-24 11:51 | 2025-11-24 12:17 | 0:26 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty AVR was worked on (No diesel outage after validation)
NOCINC0006458863 | External Reconciliation | Site Down | P1 | IHS_DEL_1104A | DL0752 | ASB | Asaba | Delta | 3 - Low | DL0704 | SOUTH SOUTH |  | 2025-11-26 15:55 | Femi Olanipekun | 2025-11-26 15:55 | 2025-11-26 16:21 | 1565 | 2025-11-26 15:55 | 2025-11-26 16:21 | 0:26 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under frequency, governor was adjusted to restore the site (No diesel outage after validation) | DG under frequency, governor was adjusted to restore the site (No diesel outage after validation)
NOCINC0006448523 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-25 13:25 | Emmanuel Faleti | 2025-11-25 13:24 | 2025-11-25 13:50 | 1564 | 2025-11-25 13:24 | 2025-11-25 13:50 | 0:26 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty Radiator was worked on. (No diesel outage after validation) | Faulty Radiator was worked on. (No diesel outage after validation)
NOCINC0006470689 | External Reconciliation | Site Down | P2 | IHS_ILO_0065C | KW4737 | IBD | Ibadan | Kwara | 3 - Low | KW0486 | WEST |  | 2025-11-28 08:56 | Okusanya Joseph | 2025-11-28 08:55 | 2025-11-28 09:21 | 1563 | 2025-11-28 08:55 | 2025-11-28 09:21 | 0:26 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | DG undervoltage alarm, AVR was adjusted
NOCINC0006470464 | External Reconciliation | Site Down | P1 | IHS_EKI_0731A | T3052 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-28 08:07 | Mary Elaigwu | 2025-11-28 08:06 | 2025-11-28 08:32 | 1558 | 2025-11-28 08:06 | 2025-11-28 08:32 | 0:26 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | DG crank battery, external battery was used to start the GG
NOCINC0006485225 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1105A | DL0505 | ASB | Asaba | Delta | 3 - Low | DL0678 | SOUTH SOUTH |  | 2025-11-30 08:13 | Tracy Osarumwense | 2025-11-30 08:13 | 2025-11-30 08:39 | 1556 | 2025-11-30 08:13 | 2025-11-30 08:39 | 0:26 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty Rectifier Module was replaced. | Faulty Rectifier Module was replaced. (No diesel outage after validation).
NOCINC0006459468 | External Reconciliation | Site Down | P1 | IHS_KWA_0831A | KW3805 | IBD | Ibadan | Kwara | 3 - Low | KW0653 | WEST |  | 2025-11-26 17:42 | Titus Tosin | 2025-11-26 17:39 | 2025-11-26 18:05 | 1552 | 2025-11-26 17:39 | 2025-11-26 18:05 | 0:26 | IPT | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 2 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Grid-DG synchronization failure due to unstable grid supply issue. DG was powered manually.
NOCINC0006473758 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0047B | OS4256 | IBD | Ibadan | Osun | 3 - Low | OS0904 | WEST |  | 2025-11-28 16:32 | Valentine Adinnu | 2025-11-28 16:23 | 2025-11-28 16:44 | 1259 | 2025-11-28 16:23 | 2025-11-28 16:49 | 0:26 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Adejumobi Tunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out at site | PPM (Generator servicing) was carried out at site
NOCINC0006472273 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0781A | T0280 | ASB | Asaba | Delta | 3 - Low | DL1032 | SOUTH SOUTH |  | 2025-11-28 12:47 | Abundance Otunola | 2025-11-28 12:45 | 2025-11-28 13:11 | 1549 | 2025-11-28 12:45 | 2025-11-28 13:11 | 0:26 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier - Circuit Breaker | 2 / 2 | MTN NG, Airtel NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 8 | Faulty rectifier contactor was engaged. (No diesel outage after validation) | Faulty rectifier contactor was engaged. (No diesel outage after validation)
NOCINC0006459044 | External Reconciliation | Site Down | P1 | IHS_KWA_0844A | KW5691 | IBD | Ibadan | Kwara | 3 - Low | KW0433 | WEST |  | 2025-11-26 16:26 | Titus Tosin | 2025-11-26 16:25 | 2025-11-26 16:51 | 1548 | 2025-11-26 16:25 | 2025-11-26 16:51 | 0:26 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was completed at site
NOCINC0006462619 | External Reconciliation | Site Down | P1 | IHS_DEL_0929A | T2950 | ASB | Asaba | Delta | 3 - Low | DL0580 | SOUTH SOUTH |  | 2025-11-27 06:27 | Ezinne Ubachukwu | 2025-11-27 06:26 | 2025-11-27 06:52 | 1545 | 2025-11-27 06:26 | 2025-11-27 06:52 | 0:26 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Over Frequency | 2 / 2 | Airtel NG, MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Over frequency, frequency was adjusted (No diesel outage after validation) | Over frequency, frequency was adjusted (No diesel outage after validation)
NOCINC0006450715 | External Reconciliation | Site Down | P2 | IHS_OYO_1251H | OY4116 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 18:08 | Mutmainnah Saba | 2025-11-25 18:05 | 2025-11-25 18:31 | 1545 | 2025-11-25 18:05 | 2025-11-25 18:31 | 0:26 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Over Voltage | 2 / 2 | MTN NG, Dimension Data Limited |  | BANKOLE SODIQ |  | Filani Oluwatobi | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Over voltage alarm was cleared, DG was powered manually
NOCINC0006468687 | External Reconciliation | Site Down | P2 | IHS_WAR_0879H | T2907 | ASB | Asaba | Delta | 3 - Low | DL0635 | SOUTH SOUTH |  | 2025-11-27 23:45 | Oluwatobiloba Are | 2025-11-27 23:42 | 2025-11-28 00:08 | 1544 | 2025-11-27 23:42 | 2025-11-28 00:08 | 0:26 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled
NOCINC0006472600 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0049C | EK4524 | IBD | Ibadan | Ekiti | 3 - Low | EK0428 | WEST |  | 2025-11-28 13:42 | Testimony Akinyemi | 2025-11-28 13:41 | 2025-11-28 14:07 | 1544 | 2025-11-28 13:41 | 2025-11-28 14:07 | 0:26 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Ajao Oyekunle |  |  | Soye West | Ugwu Samuel Nnamdi |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | PPM (Generator Servicing) was done without access ref
NOCINC0006474278 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-28 17:42 | Gbemisola Adedeji | 2025-11-28 17:38 | 2025-11-28 18:04 | 1543 | 2025-11-28 17:38 | 2025-11-28 18:04 | 0:26 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled(No diesel outage after validation) | Tripped load breaker was enabled(No diesel outage after validation)
NOCINC0006439803 | External Reconciliation | Site Down | P2 | IHS_OYO_1251H | OY4116 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 12:33 | Aishat Oyedeji | 2025-11-24 12:27 | 2025-11-24 12:53 | 1535 | 2025-11-24 12:27 | 2025-11-24 12:53 | 0:26 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Over Frequency | 1 / 2 | MTN NG |  | BANKOLE SODIQ |  | Filani Oluwatobi | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | DG over voltage alarm was cleared, DG was powered manually | DG over voltage alarm was cleared, DG was powered manually
NOCINC0006462549 | External Reconciliation | Site Down | P1 | IHS_OND_0828A | T3847 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 06:09 | Oluwadara Bankole | 2025-11-27 06:05 | 2025-11-27 06:30 | 1531 | 2025-11-27 06:05 | 2025-11-27 06:30 | 0:26 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 1 / 1 | MTN NG |  | Okewusi Eyitayo Okewusi |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on
NOCINC0006484013 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0964B | DL4012 | ASB | Asaba | Delta | 3 - Low | DL1306 | SOUTH SOUTH |  | 2025-11-30 00:48 | Uthman Akinola | 2025-11-30 00:48 | 2025-11-30 01:12 | 1410 | 2025-11-30 00:46 | 2025-11-30 01:12 | 0:25 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Monday Agha | Igwe Samuel | Igwe Samuel | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed charging alternator was excited(no diesel outage after validation)
NOCINC0006456150 | External Reconciliation | Site Down | P3 | IHS_KWA_0914A | KW4594 | IBD | Ibadan | Kwara | 3 - Low | KW0418 | WEST |  | 2025-11-26 09:12 | Titus Tosin | 2025-11-26 09:12 | 2025-11-26 09:38 | 1529 | 2025-11-26 09:12 | 2025-11-26 09:38 | 0:25 | IPT | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to DG failed to start alarm was cleared and DG was Powered manually
NOCINC0006470399 | External Reconciliation | Site Down | P4 | IHS_BEN_0063B | ED5104 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 07:55 | Emmanuel Faleti | 2025-11-28 07:53 | 2025-11-28 08:18 | 1527 | 2025-11-28 07:53 | 2025-11-28 08:18 | 0:25 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Flat DG Battery, external battery was used to restore site (No diesel outage after validation)
NOCINC0006439058 | External Reconciliation | Site Down | P1 | IHS_SAP_0005B | DL0717 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 09:47 | Ayomide Akindolie | 2025-11-24 09:47 | 2025-11-24 10:12 | 1524 | 2025-11-24 09:47 | 2025-11-24 10:12 | 0:25 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006444386 | External Reconciliation | Site Down | P2 | IHS_OSU_0867A | T3649 | IBD | Ibadan | Osun | 3 - Low | OS0666 | WEST |  | 2025-11-24 22:33 | Damilola Paseda | 2025-11-24 22:31 | 2025-11-24 22:56 | 1524 | 2025-11-24 22:31 | 2025-11-24 22:56 | 0:25 | IPT | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Faulty ATS contactor was worked on | Faulty ATS contactor was worked on
NOCINC0006470264 | External Reconciliation | Site Down | P1 | IHS_BEN_0075C | ED5148 | IBD | Asaba | Edo | 3 - Low | ED0665 | SOUTH SOUTH |  | 2025-11-28 07:16 | Emmanuel Faleti | 2025-11-28 07:16 | 2025-11-28 07:41 | 1523 | 2025-11-28 07:16 | 2025-11-28 07:41 | 0:25 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 3 / 3 | Airtel NG, MTN NG, Smile |  | KAZEEM AJIBOYE |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG servicing was completed at site
NOCINC0006474870 | Internal Reconciliation | Site Down | P1 | IHS_IBA_0099C | OY4157 | IBD | Ibadan | Oyo | 3 - Low | OY1034 | WEST | Cascaded Incident from TTO6760739 - Cascade Removed From TTO6760739 | 2025-11-28 19:14 | Mutmainnah Saba | 2025-11-28 19:10 | 2025-11-28 19:35 | 1516 | 2025-11-28 19:10 | 2025-11-28 19:35 | 0:25 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen CSU, CSU was reset | Hybrid synchronization failure due to frozen CSU, CSU was reset
NOCINC0006472286 | Internal Reconciliation | Site Down | P2 | IHS_EDO_1179H | ED5348 | IBD | Asaba | Edo | 3 - Low | ED1137 | SOUTH SOUTH |  | 2025-11-28 12:50 | Muhammed Hashirudeen | 2025-11-28 12:50 | 2025-11-28 13:15 | 1514 | 2025-11-28 12:50 | 2025-11-28 13:15 | 0:25 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 4 / 4 | MTN NG, Airtel NG, Smile, INQ |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Weak DG was worked on (No diesel outage after validatio
NOCINC0006479525 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1198B | DL4061 | ASB | Asaba | Delta | 3 - Low | DL0878 | SOUTH SOUTH |  | 2025-11-29 12:18 | Ayokunle Samuel | 2025-11-29 12:18 | 2025-11-29 12:37 | 1184 | 2025-11-29 12:14 | 2025-11-29 12:39 | 0:25 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | Airtel NG, MTN NG |  | Adedeji Olusegun |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 5 | Hybrid synchronization failure due to flat cracking Battery. DG was powered manually. (No diesel outage after validation) | Hybrid synchronization failure due to flat cracking Battery. DG was powered manually. (No diesel outage after validation)
NOCINC0006480909 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0001B | OY2931 | IBD | Ibadan | Oyo | 3 - Low | OY0906 | WEST |  | 2025-11-29 15:23 | Aishat Oyedeji | 2025-11-29 15:23 | 2025-11-29 15:48 | 1513 | 2025-11-29 15:23 | 2025-11-29 15:48 | 0:25 | SPS | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 5 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to incomplete grid phase, DG powered manually | Grid to DG synchronization failure due to incomplete grid phase, DG powered manually
NOCINC0006438514 | External Reconciliation | Site Down | P3 | IHS_OSU_0110C | OS4664 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 08:32 | Precious Attah | 2025-11-24 08:31 | 2025-11-24 08:56 | 1511 | 2025-11-24 08:31 | 2025-11-24 08:56 | 0:25 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty fuel pump was replaced
NOCINC0006468685 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-27 23:44 | Emmanuel Faleti | 2025-11-27 23:44 | 2025-11-28 00:09 | 1507 | 2025-11-27 23:44 | 2025-11-28 00:09 | 0:25 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on. (No diesel outage after validation) | Faulty injector pump was worked on. (No diesel outage after validation)
NOCINC0006486562 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0963C | DL4026 | ASB | Asaba | Delta | 3 - Low | DL0975 | SOUTH SOUTH | Cascaded Incident from TTO6773831 - Cascade Removed From TTO6773831 | 2025-11-30 12:14 | Tracy Osarumwense | 2025-11-30 12:12 | 2025-11-30 12:37 | 1505 | 2025-11-30 12:12 | 2025-11-30 12:37 | 0:25 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Overload | 2 / 2 | MTN NG, Airtel NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 5 | DG unexpected shutdown due to overload, alarm was cleared and DG Powered Manually. (No diesel outage after validation) | DG unexpected shutdown due to overload, alarm was cleared and DG Powered Manually. (No diesel outage after validation).
NOCINC0006443781 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST | Cascaded Incident from TTO6726419 - Cascade Removed From TTO6726419 | 2025-11-24 20:54 | Kehinde Akinbowale | 2025-11-24 20:50 | 2025-11-24 21:15 | 1505 | 2025-11-24 20:50 | 2025-11-24 21:15 | 0:25 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 2 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start(No diesel outage after validation) | Weak DG was primed to start(No diesel outage after validation)
NOCINC0006471928 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0863A | T4130 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 11:52 | Kehinde Akinbowale | 2025-11-28 11:49 | 2025-11-28 12:14 | 1505 | 2025-11-28 11:49 | 2025-11-28 12:14 | 0:25 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Failed charging alternator was excited(No diesel outage after validation) | Failed charging alternator was excited(No diesel outage after validation)
NOCINC0006488118 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0042B | OS4285 | IBD | Ibadan | Osun | 3 - Low | OS0738 | WEST |  | 2025-11-30 16:03 | Precious Attah | 2025-11-30 16:02 | 2025-11-30 16:27 | 1502 | 2025-11-30 16:02 | 2025-11-30 16:27 | 0:25 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | low oil pressure, oil was added
NOCINC0006487251 | Internal Reconciliation | Site Down | P3 | IHS_OND_0002B | - | - | Ibadan | Osun | 3 - Low | ON0518 | WEST |  | 2025-11-30 13:38 | Ihuoma Opurum | 2025-11-30 13:35 | 2025-11-30 14:00 | 1500 | 2025-11-30 13:35 | 2025-11-30 14:00 | 0:25 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | Airtel NG |  | Olatunde Babatunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled
NOCINC0006488261 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0861A | T3322 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 16:19 | Oluwatomisin Sogbesan | 2025-11-30 16:17 | 2025-11-30 16:42 | 1499 | 2025-11-30 16:17 | 2025-11-30 16:42 | 0:25 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Adeoti Ogunbiyi |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited
NOCINC0006446841 | External Reconciliation | Site Down | P1 | IHS_OND_0789A | T3408 | IBD | Ibadan | Ondo | 3 - Low | ON0576 | WEST |  | 2025-11-25 10:09 | Mary Elaigwu | 2025-11-25 10:08 | 2025-11-25 10:33 | 1495 | 2025-11-25 10:08 | 2025-11-25 10:33 | 0:25 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 2 / 2 | MTN NG, Airtel NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty kick starter, Generator was powered manually
NOCINC0006478686 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0876A | T3517 | IBD | Ibadan | Oyo | 3 - Low | OY0739 | WEST |  | 2025-11-29 10:43 | Aishat Oyedeji | 2025-11-29 10:43 | 2025-11-29 11:08 | 1494 | 2025-11-29 10:43 | 2025-11-29 11:08 | 0:25 | Biswal | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Enoch Fidelis |  |  | Abiola Adegbiji | Habeeb Adepoju |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 6 | PPM (Generator servicing) was carried out with with ref IHSREF/25110413473185419467 | PPM (Generator servicing) was carried out with with ref IHSREF/25110413473185419467
NOCINC0006474462 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0842A | EK2219 | IBD | Ibadan | Ekiti | 3 - Low | EK0564 | WEST |  | 2025-11-28 18:13 | Zainab Bello | 2025-11-28 18:11 | 2025-11-28 18:36 | 1494 | 2025-11-28 18:11 | 2025-11-28 18:36 | 0:25 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | Airtel NG, MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Under voltage alarm was cleared
NOCINC0006482139 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1088A | AN0333 | ASB | Asaba | Anambra | 3 - Low | AN0701 | SOUTH EAST |  | 2025-11-29 18:32 | Abundance Otunola | 2025-11-29 18:28 | 2025-11-29 18:53 | 1488 | 2025-11-29 18:28 | 2025-11-29 18:53 | 0:25 | Tyllium NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Aneke Christian | Habib Muhammed | Habib Muhammed | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Hybrid synchronization failure, DG was powered manually(No diesel outage after validation) | Hybrid synchronization failure, DG was powered manually(No diesel outage after validation)
NOCINC0006465053 | External Reconciliation | Site Down | P2 | IHS_OSU_0953A | OS4274 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 13:24 | Mutmainnah Saba | 2025-11-27 13:22 | 2025-11-27 13:46 | 1477 | 2025-11-27 13:22 | 2025-11-27 13:46 | 0:25 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006465640 | External Reconciliation | Site Down | P3 | IHS_BOM_0002B | DL0769 | ASB | Asaba | Delta | 3 - Low | DL0803 | SOUTH SOUTH |  | 2025-11-27 14:47 | Mary Odefemi | 2025-11-27 14:46 | 2025-11-27 15:11 | 1477 | 2025-11-27 14:46 | 2025-11-27 15:11 | 0:25 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006449546 | External Reconciliation | Site Down | P2 | IHS_EDO_0879A | T3332 | IBD | Asaba | Edo | 3 - Low | ED0563 | SOUTH SOUTH |  | 2025-11-25 15:30 | Emmanuel Faleti | 2025-11-25 15:28 | 2025-11-25 15:53 | 1476 | 2025-11-25 15:28 | 2025-11-25 15:53 | 0:25 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 3 / 3 | MTN NG, Airtel NG, Smile |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Generator Servicing (PPM) was completed at site (No diesel outage after validation) | Generator Servicing (PPM) was completed at site (No diesel outage after validation)
NOCINC0006488431 | Internal Reconciliation | Site Down | P2 | IHS_BEN_0079C | ED5154 | IBD | Asaba | Edo | 3 - Low | ED0465 | SOUTH SOUTH |  | 2025-11-30 16:50 | Evelyn Emagurehor | 2025-11-30 16:43 | 2025-11-30 17:07 | 1472 | 2025-11-30 16:43 | 2025-11-30 17:07 | 0:25 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Failed DG charging alternator was excited to restore power to the site. (No diesel outage after validation). | Failed DG charging alternator was excited to restore power to the site. (No diesel outage after validation).
NOCINC0006449765 | External Reconciliation | Site Down | P2 | IHS_KWA_0790A | T3171 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 15:59 | Oluwatomisin Ogunleye | 2025-11-25 15:57 | 2025-11-25 16:21 | 1468 | 2025-11-25 15:57 | 2025-11-25 16:21 | 0:24 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Emergency Stop | 1 / 1 | MTN NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | faulty emergency stop was worked on
NOCINC0006440137 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-24 13:03 | Tracy Osarumwense | 2025-11-24 13:03 | 2025-11-24 13:28 | 1465 | 2025-11-24 13:03 | 2025-11-24 13:28 | 0:24 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty AVR was worked on (No diesel outage after validation)
NOCINC0006472612 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1242C | AN0957 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 13:45 | Kehinde Akinbowale | 2025-11-28 13:42 | 2025-11-28 14:07 | 1465 | 2025-11-28 13:42 | 2025-11-28 14:07 | 0:24 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled (No diesel outage after validation). | Tripped load breaker was enabled (No diesel outage after validation).
NOCINC0006446716 | External Reconciliation | Site Down | P2 | IHS_OYO_0950A | T3694 | IBD | Ibadan | Oyo | 3 - Low | OY1012 | WEST |  | 2025-11-25 09:50 | Victor Otugo | 2025-11-25 09:50 | 2025-11-25 10:14 | 1462 | 2025-11-25 09:50 | 2025-11-25 10:14 | 0:24 | IPT | Fuel Outage (Probable) | Passive | Diesel | Fuel Line Issue | 2 / 2 | Airtel NG, MTN NG |  | Imoleayo Amoo | Olalekan Ajibola | Olalekan Ajibola | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | blocked fuel line was worked on
NOCINC0006473814 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 16:40 | Azeezat Badmus | 2025-11-28 16:39 | 2025-11-28 17:03 | 1457 | 2025-11-28 16:39 | 2025-11-28 17:03 | 0:24 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is affected by ED4860. (No diesel outage after validation)
NOCINC0006466037 | External Reconciliation | Site Down | P3 | IHS_OSU_0895A | T3488 | IBD | Ibadan | Osun | 3 - Low | OS0732 | WEST |  | 2025-11-27 15:40 | Sheriff Salami | 2025-11-27 15:37 | 2025-11-27 16:01 | 1453 | 2025-11-27 15:37 | 2025-11-27 16:01 | 0:24 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Load Breaker | 1 / 2 | MTN NG |  | Zechariah Akinbulejo | Opeyemi Ajibola | Opeyemi Ajibola | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled
NOCINC0006472710 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0766A | T3144 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 14:03 | Praise Okezie | 2025-11-28 13:59 | 2025-11-28 14:23 | 1449 | 2025-11-28 13:59 | 2025-11-28 14:23 | 0:24 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Generator (PPM) servicing was carried out on site without ref
NOCINC0006449603 | External Reconciliation | Site Down | P4 | IHS_OYO_1242H | OY4479 | IBD | Ibadan | Oyo | 3 - Low | OY1532 | WEST |  | 2025-11-25 15:38 | Victor Otugo | 2025-11-25 15:38 | 2025-11-25 16:02 | 1447 | 2025-11-25 15:38 | 2025-11-25 16:02 | 0:24 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | hybrid failure due to loss Communication, DG was powered manually
NOCINC0006441330 | External Reconciliation | Site Down | P4 | IHS_EDO_1256B | ED5547 | IBD | Asaba | Edo | 3 - Low | ED0973 | SOUTH SOUTH |  | 2025-11-24 15:09 | Evelyn Emagurehor | 2025-11-24 15:05 | 2025-11-24 15:29 | 1442 | 2025-11-24 15:05 | 2025-11-24 15:29 | 0:24 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on to restore power to the site. (No diesel outage after validation). | Faulty injector pump was worked on to restore power to the site. (No diesel outage after validation).
NOCINC0006444036 | External Reconciliation | Site Down | P1 | IHS_KWA_0733A | T3103 | IBD | Ibadan | Kwara | 3 - Low | KW0368 | WEST |  | 2025-11-24 21:29 | Praise Okezie | 2025-11-24 21:27 | 2025-11-24 21:51 | 1440 | 2025-11-24 21:27 | 2025-11-24 21:51 | 0:24 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Outage Issue | 1 / 2 | MTN NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Grid to DG synchronization failure due to grid outage issue. DG was auto restarted
NOCINC0006466179 | External Reconciliation | Site Down | P1 | IHS_OND_0853A | T3443 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 15:59 | Iyesioluwa Ola | 2025-11-27 15:59 | 2025-11-27 16:23 | 1433 | 2025-11-27 15:59 | 2025-11-27 16:23 | 0:24 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | MTN NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Faulty AVR was worked on
NOCINC0006438235 | External Reconciliation | Site Down | P4 | IHS_ANA_1040A | AN0030 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 07:17 | Uthman Akinola | 2025-11-24 07:17 | 2025-11-24 07:41 | 1433 | 2025-11-24 07:17 | 2025-11-24 07:41 | 0:24 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 1 / 1 | MTN NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | frozen rectifier CSU was reset(no diesel outage after validation)
NOCINC0006462680 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-27 06:45 | Precious Attah | 2025-11-27 06:43 | 2025-11-27 07:07 | 1432 | 2025-11-27 06:43 | 2025-11-27 07:07 | 0:24 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 2 / 2 | Airtel NG, MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006448322 | External Reconciliation | Site Down | P1 | IHS_KWA_0739A | T3106 | IBD | Ibadan | Kwara | 3 - Low | KW0452 | WEST |  | 2025-11-25 12:58 | Oluwatomisin Ogunleye | 2025-11-25 12:58 | 2025-11-25 13:22 | 1429 | 2025-11-25 12:58 | 2025-11-25 13:22 | 0:24 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | GRID-DG synchronization failure due to unstable grid supply. DG was powered manually.
NOCINC0006472874 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1095A | AN0423 | ASB | Asaba | Anambra | 3 - Low | AN0573 | SOUTH EAST |  | 2025-11-28 14:26 | Gbemisola Adedeji | 2025-11-28 14:25 | 2025-11-28 14:48 | 1427 | 2025-11-28 14:25 | 2025-11-28 14:48 | 0:24 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Sensor Switch | 2 / 2 | MTN NG, Airtel NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty oil switch alarm was cleared(No diesel outage after validation) | Faulty oil switch alarm was cleared(No diesel outage after validation)
NOCINC0006472104 | Internal Reconciliation | Site Down | P4 | IHS_OND_0866A | T3841 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 12:20 | Muhammed Hashirudeen | 2025-11-28 12:20 | 2025-11-28 12:43 | 1426 | 2025-11-28 12:20 | 2025-11-28 12:43 | 0:24 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Module | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure. DG powered manually (No diesel outage after validation)
NOCINC0006463888 | External Reconciliation | Site Down | P1 | IHS_KWA_0849A | T3394 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 10:58 | Titus Tosin | 2025-11-27 10:56 | 2025-11-27 11:20 | 1421 | 2025-11-27 10:56 | 2025-11-27 11:20 | 0:24 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Oyenini Olalekan |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | PPM (Generator servicing ) was carried out on site
NOCINC0006489457 | Internal Reconciliation | Site Down | P2 | IHS_OND_0936A | OD2572 | IBD | Ibadan | Ondo | 3 - Low | ON0591 | WEST |  | 2025-11-30 20:07 | Yewande Adeagbo | 2025-11-30 20:07 | 2025-11-30 20:30 | 1421 | 2025-11-30 20:07 | 2025-11-30 20:30 | 0:24 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Adetutu Adedipupo |  |  | Soye West | Goddey Nwokedigbo Peter |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | High DG Temperature, Coolant Was Added
NOCINC0006437615 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST |  | 2025-11-24 03:51 | Gbemisola Adedeji | 2025-11-24 03:49 | 2025-11-24 04:12 | 1420 | 2025-11-24 03:49 | 2025-11-24 04:12 | 0:24 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation). | Weak DG was primed to start (No diesel outage after validation).
NOCINC0006485021 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1248B | - | - | Asaba | Delta | 3 - Low | DL0960 | SOUTH SOUTH |  | 2025-11-30 07:17 | Bukola Olabanji | 2025-11-30 07:14 | 2025-11-30 07:38 | 1414 | 2025-11-30 07:14 | 2025-11-30 07:38 | 0:24 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | Airtel NG |  | David Uja |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | PPM was completed at site valid IHS ref - IHSREF/25112511260574718213 (No diesel outage after validation)
NOCINC0006458991 | External Reconciliation | Site Down | P3 | IHS_ILO_0058C | KW4689 | IBD | Ibadan | Kwara | 3 - Low | KW0514 | WEST |  | 2025-11-26 16:12 | Oluwatomisin Ogunleye | 2025-11-26 16:09 | 2025-11-26 16:32 | 1409 | 2025-11-26 16:09 | 2025-11-26 16:32 | 0:23 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled.
NOCINC0006465473 | External Reconciliation | Site Down | P4 | IHS_ANA_1185A | AN0665 | ASB | Asaba | Anambra | 3 - Low | AN1133 | SOUTH EAST |  | 2025-11-27 14:22 | Akachukwu Ugwu | 2025-11-27 14:19 | 2025-11-27 14:43 | 1405 | 2025-11-27 14:19 | 2025-11-27 14:43 | 0:23 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Filter | 2 / 2 | Airtel NG, MTN NG |  | Ezimeruwe ANTHONY |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty fuel filter housing was replaced (No diesel outage after validation) | Faulty fuel filter housing was replaced (No diesel outage after validation)
NOCINC0006475974 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1147A | AN0687 | ASB | Asaba | Anambra | 3 - Low | AN0580 | SOUTH EAST |  | 2025-11-28 22:00 | Akachukwu Ugwu | 2025-11-28 21:57 | 2025-11-28 22:21 | 1403 | 2025-11-28 21:57 | 2025-11-28 22:21 | 0:23 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | DG under frequency, Governor adjusted (No diesel outage after validation). | DG under frequency, Governor adjusted (No diesel outage after validation).
NOCINC0006477639 | Internal Reconciliation | Site Down | P2 | IHS_EDO_1179H | ED5348 | IBD | Asaba | Edo | 3 - Low | ED1137 | SOUTH SOUTH |  | 2025-11-29 07:31 | Elizabeth Apata | 2025-11-29 07:28 | 2025-11-29 07:52 | 1402 | 2025-11-29 07:28 | 2025-11-29 07:52 | 0:23 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 4 / 4 | MTN NG, Airtel NG, Smile, INQ |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006484469 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1147A | AN0687 | ASB | Asaba | Anambra | 3 - Low | AN0580 | SOUTH EAST |  | 2025-11-30 04:08 | Gbemisola Adedeji | 2025-11-30 04:07 | 2025-11-30 04:31 | 1400 | 2025-11-30 04:07 | 2025-11-30 04:31 | 0:23 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Over Frequency | 2 / 2 | MTN NG, Airtel NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | High DG frequency, governor was adjusted (No diesel outage after validation). | High DG frequency, governor was adjusted (No diesel outage after validation).
NOCINC0006483955 | Internal Reconciliation | Site Down | P4 | IHS_OND_0033B | OD2599 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 00:24 | Abisoye Olaleye | 2025-11-30 00:19 | 2025-11-30 00:43 | 1398 | 2025-11-30 00:19 | 2025-11-30 00:43 | 0:23 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG Was Primed To Start.
NOCINC0006467888 | External Reconciliation | Site Down | P4 | IHS_OND_0044B | OD2575 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 20:53 | Mary Elaigwu | 2025-11-27 20:53 | 2025-11-27 21:16 | 1397 | 2025-11-27 20:53 | 2025-11-27 21:16 | 0:23 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Usman Hammed |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to DG failed to start, DG was powered manually
NOCINC0006456122 | External Reconciliation | Site Down | P2 | IHS_OYO_1251H | OY4116 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 09:03 | Ifechi Ugwueze | 2025-11-26 09:02 | 2025-11-26 09:25 | 1396 | 2025-11-26 09:02 | 2025-11-26 09:25 | 0:23 | SPS | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 2 / 2 | MTN NG, Dimension Data Limited |  | BANKOLE SODIQ |  | Filani Oluwatobi | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty Rectifier DC Cable was terminated
NOCINC0006472774 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0921B | EK6303 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-28 14:12 | Maureen Uchehorke | 2025-11-28 14:10 | 2025-11-28 14:33 | 1396 | 2025-11-28 14:10 | 2025-11-28 14:33 | 0:23 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Engine Temp - Faulty Water Pump | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | faulty water pump was work on
NOCINC0006477460 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 06:45 | Akachukwu Ugwu | 2025-11-29 06:40 | 2025-11-29 07:03 | 1390 | 2025-11-29 06:40 | 2025-11-29 07:03 | 0:23 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under voltage alarm. AVR adjusted (No diesel outage after validation). | DG under voltage alarm. AVR adjusted (No diesel outage after validation).
NOCINC0006465946 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-27 15:29 | Muhammed Hashirudeen | 2025-11-27 15:28 | 2025-11-27 15:51 | 1387 | 2025-11-27 15:28 | 2025-11-27 15:51 | 0:23 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006466553 | External Reconciliation | Site Down | P3 | IHS_OYO_1110C | OY4442 | IBD | Ibadan | Oyo | 3 - Low | OY1187 | WEST |  | 2025-11-27 16:55 | Kandervil Uwah | 2025-11-27 16:53 | 2025-11-27 17:16 | 1385 | 2025-11-27 16:53 | 2025-11-27 17:16 | 0:23 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Over Voltage | 2 / 2 | MTN NG, Airtel NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG Over voltage alarm was cleared
NOCINC0006448468 | External Reconciliation | Site Down | P2 | IHS_KWA_0790A | T3171 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 13:16 | Oluwatomisin Ogunleye | 2025-11-25 13:13 | 2025-11-25 13:36 | 1384 | 2025-11-25 13:13 | 2025-11-25 13:36 | 0:23 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 1 | MTN NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Grid to DG synchronization failure due to Unstable Grid Supply Issue, DG powered manually.
NOCINC0006461908 | External Reconciliation | Site Down | P4 | IHS_ANA_1124A | AN0530 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 01:32 | Aderonke Olowojoba | 2025-11-27 01:30 | 2025-11-27 01:53 | 1381 | 2025-11-27 01:30 | 2025-11-27 01:53 | 0:23 | BJ Bison NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Augustine Okoro | Ademola Adekunle | Ademola Adekunle | Henry Wanogho | Ifeanyi Chukusa |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure, DG was powered manually (No diesel outage after validation) | Hybrid synchronization failure, DG was powered manually (No diesel outage after validation)
NOCINC0006488518 | Internal Reconciliation | Site Down | P4 | IHS_ANA_0854A | T4118 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 17:05 | Aderonke Olowojoba | 2025-11-30 17:01 | 2025-11-30 17:24 | 1380 | 2025-11-30 17:01 | 2025-11-30 17:24 | 0:23 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 1 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted(No diesel outage after validation) | Low DG frequency, Governor was adjusted(No diesel outage after validation)
NOCINC0006462807 | External Reconciliation | Site Down | P2 | IHS_ILO_0726E | KW6399 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 07:18 | Precious Attah | 2025-11-27 07:15 | 2025-11-27 07:38 | 1378 | 2025-11-27 07:15 | 2025-11-27 07:38 | 0:23 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out
NOCINC0006476462 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0017B | ED5089 | IBD | Asaba | Edo | 3 - Low | ED0663 | SOUTH SOUTH |  | 2025-11-29 00:10 | Elizabeth Apata | 2025-11-29 00:09 | 2025-11-29 00:32 | 1368 | 2025-11-29 00:09 | 2025-11-29 00:32 | 0:23 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | Airtel NG, MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Flat DG crank battery, external battery was used to power site (no diesel outage after validation)
NOCINC0006458873 | External Reconciliation | Site Down | P1 | IHS_SAP_0008B | DL0851 | ASB | Asaba | Delta | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-26 15:41:27@DL0851_2 | 2025-11-26 15:57 | System Administrator | 2025-11-26 15:45 | 2025-11-26 16:08 | 1362 | 2025-11-26 15:45 | 2025-11-26 16:08 | 0:23 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Low DG frequency, govvernor was adjusted (No diesel outage after validation)
NOCINC0006448082 | External Reconciliation | Site Down | P3 | IHS_EDO_0978A | ED2153 | IBD | Asaba | Edo | 3 - Low | ED0709 | SOUTH SOUTH |  | 2025-11-25 12:27 | Oluwatomisin Sogbesan | 2025-11-25 12:26 | 2025-11-25 12:49 | 1360 | 2025-11-25 12:26 | 2025-11-25 12:49 | 0:23 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | Airtel NG, MTN NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 2 | DG high temperature due to low coolant level, coolant was added (No diesel outage after validation) | DG high temperature due to low coolant level, coolant was added (No diesel outage after validation)
NOCINC0006438343 | External Reconciliation | Site Down | P4 | IHS_OYO_0917A | T3524 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 07:47 | Osarieme Charles | 2025-11-24 07:40 | 2025-11-24 08:02 | 1360 | 2025-11-24 07:40 | 2025-11-24 08:02 | 0:23 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG governor was adjusted
NOCINC0006469516 | External Reconciliation | Site Down | P2 | IHS_EDO_0918A | T3320 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 02:40 | Oluwatobiloba Are | 2025-11-28 02:39 | 2025-11-28 03:01 | 1357 | 2025-11-28 02:39 | 2025-11-28 03:01 | 0:23 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 1 / 1 | MTN NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Hybrid to Gen synchronization failure due to weak ACDG - Generator Battery. RES: An external battery was used to power the Gen manually to restore power to the site. (No diesel outage after validation) | Hybrid to Gen synchronization failure due to weak ACDG - Generator Battery. RES: An external battery was used to power the Gen manually to restore power to the site. (No diesel outage after validation)
NOCINC0006470449 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1018A | T4896 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 08:04 | Oluwatoyin Fagite | 2025-11-28 08:00 | 2025-11-28 08:23 | 1352 | 2025-11-28 08:00 | 2025-11-28 08:23 | 0:23 | Tyllium NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Moses Kenechukwu | Kenneth Ogbodo | Kenneth Ogbodo | Fady Safwat | Aliyu Garuba |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | PPM(Generator Servicing) was completed at site | PPM(Generator Servicing) was completed at site
NOCINC0006444112 | External Reconciliation | Site Down | P1 | IHS_ANA_0834A | T4103 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 21:45 | Solomon Bankole | 2025-11-24 21:43 | 2025-11-24 22:06 | 1351 | 2025-11-24 21:43 | 2025-11-24 22:06 | 0:23 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty Lift pump was replaced ( No diesel outage after validation) | Faulty Lift pump was replaced ( No diesel outage after validation)
NOCINC0006459247 | External Reconciliation | Site Down | P1 | IHS_ANA_1001A | T4870 | ASB | Asaba | Anambra | 3 - Low | AN0530 | SOUTH EAST |  | 2025-11-26 17:04 | Patrick Okoro | 2025-11-26 17:04 | 2025-11-26 17:27 | 1346 | 2025-11-26 17:04 | 2025-11-26 17:27 | 0:22 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG over frequency, governor was adjusted to restore the site (No diesel outage after validation) | DG over frequency, governor was adjusted to restore the site (No diesel outage after validation)
NOCINC0006471998 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0809A | T3917 | IBD | Ibadan | Ekiti | 3 - Low | EK0500 | WEST |  | 2025-11-28 12:00 | Maureen Uchehorke | 2025-11-28 12:00 | 2025-11-28 12:23 | 1342 | 2025-11-28 12:00 | 2025-11-28 12:23 | 0:22 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - RPM - Gas Flow | 2 / 2 | Airtel NG, MTN NG |  | Akinboyewa Akinola |  |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Frozen gas line was worked on
NOCINC0006485583 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0893A | T3819 | IBD | Ibadan | Osun | 3 - Low | OS0654 | WEST |  | 2025-11-30 09:23 | Precious Attah | 2025-11-30 09:21 | 2025-11-30 09:44 | 1341 | 2025-11-30 09:21 | 2025-11-30 09:44 | 0:22 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out
NOCINC0006456467 | External Reconciliation | Site Down | P3 | IHS_EDO_0749A | T0218 | IBD | Asaba | Edo | 3 - Low | ED0700 | SOUTH SOUTH |  | 2025-11-26 10:08 | Emmanuel Faleti | 2025-11-26 10:07 | 2025-11-26 10:30 | 1339 | 2025-11-26 10:07 | 2025-11-26 10:30 | 0:22 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Outage Issue | 2 / 2 | Airtel NG, MTN NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Synchronization due to grid outage, DG was powered manually. (No diesel outage after validation) | Synchronization due to grid outage, DG was powered manually. (No diesel outage after validation)
NOCINC0006443757 | External Reconciliation | Site Down | P3 | IHS_OSU_0094C | OS4338 | IBD | Ibadan | Osun | 3 - Low | OS0629 | WEST | Huawei 2G SiteDown@2025-11-24 20:34:09@OS4338_Oke | 2025-11-24 20:50 | System Administrator | 2025-11-24 20:40 | 2025-11-24 21:02 | 1337 | 2025-11-24 20:40 | 2025-11-24 21:02 | 0:22 | IPT | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 2 | MTN NG |  | Tobiloba Oladejo |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid-DG synchronization failure due to unstable grid supply issue. DG was powered manually.
NOCINC0006444708 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-25 | Kehinde Akinbowale | 2025-11-24 23:58 | 2025-11-25 00:20 | 1329 | 2025-11-24 23:58 | 2025-11-25 00:20 | 0:22 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Weak DG was primed to start(No diesel outage after validation) | Weak DG was primed to start(No diesel outage after validation)
NOCINC0006456899 | External Reconciliation | Site Down | P3 | IHS_EDO_1184H | ED2105 | IBD | Asaba | Edo | 3 - Low | ED0862 | SOUTH SOUTH |  | 2025-11-26 11:24 | Azeezat Badmus | 2025-11-26 11:22 | 2025-11-26 11:45 | 1326 | 2025-11-26 11:22 | 2025-11-26 11:45 | 0:22 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Generator servicing was completed at site (No diesel outage after validation) | Generator servicing was completed at site (No diesel outage after validation)
NOCINC0006471560 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1362B | OY1006 | IBD | Ibadan | Oyo | 3 - Low | OY1690 | WEST |  | 2025-11-28 10:57 | Damilola Paseda | 2025-11-28 10:56 | 2025-11-28 11:18 | 1318 | 2025-11-28 10:56 | 2025-11-28 11:18 | 0:22 | SPS | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | PPM was carried out at the site with IHSREF/25111412140326243735 | PPM was carried out at the site with IHSREF/25111412140326243735
NOCINC0006457501 | External Reconciliation | Site Down | P1 | IHS_OND_0789A | T3408 | IBD | Ibadan | Ondo | 3 - Low | ON0576 | WEST |  | 2025-11-26 12:34 | Iyesioluwa Ola | 2025-11-26 12:33 | 2025-11-26 12:55 | 1313 | 2025-11-26 12:33 | 2025-11-26 12:55 | 0:22 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | Airtel NG, MTN NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG-Grid synchronisation failure due to unstable grid supply, DG powered manually
NOCINC0006488671 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0014V | - | - | Asaba | Edo | 3 - Low | ED0016 | SOUTH SOUTH |  | 2025-11-30 17:25 | Evelyn Emagurehor | 2025-11-30 17:24 | 2025-11-30 17:46 | 1312 | 2025-11-30 17:24 | 2025-11-30 17:46 | 0:22 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 1 / 1 | Airtel NG |  | SIMON SUNDAY | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty ACDG Radiator was worked on to restore power to the site. (No diesel outage after validation) | Faulty ACDG Radiator was worked on to restore power to the site. (No diesel outage after validation)
NOCINC0006479281 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1048A | AN0024 | ASB | Asaba | Anambra | 3 - Low | AN0523 | SOUTH EAST |  | 2025-11-29 11:56 | Kehinde Akinbowale | 2025-11-29 11:52 | 2025-11-29 12:14 | 1311 | 2025-11-29 11:52 | 2025-11-29 12:14 | 0:22 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Ugochuku Agbamuche | Ugo Agamuche | Ugo Agamuche | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled(No diesel outage after validation) | Tripped load breaker was enabled(No diesel outage after validation)
NOCINC0006486884 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0799A | T0279 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 12:57 | Aderonke Olowojoba | 2025-11-30 12:54 | 2025-11-30 13:16 | 1310 | 2025-11-30 12:54 | 2025-11-30 13:16 | 0:22 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Ugwuja Chinonso |  |  | Erik Nwodo | Nwigbo Chijioke |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 8 | Hybrid synchronization failure. DG powered manually. (No diesel outage after validation) | Hybrid synchronization failure. DG powered manually. (No diesel outage after validation)
NOCINC0006450919 | External Reconciliation | Site Down | P4 | IHS_OYO_1121C | OY6542 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 18:46 | Marvellous Emecheta | 2025-11-25 18:44 | 2025-11-25 19:06 | 1307 | 2025-11-25 18:44 | 2025-11-25 19:06 | 0:22 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to failed SMU, SMU was reset
NOCINC0006477545 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0879H | T2907 | ASB | Asaba | Delta | 3 - Low | DL0635 | SOUTH SOUTH |  | 2025-11-29 07:07 | Mary Odefemi | 2025-11-29 07:07 | 2025-11-29 07:29 | 1300 | 2025-11-29 07:07 | 2025-11-29 07:29 | 0:22 | BJ Bison NGA | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | Airtel NG, MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006469199 | External Reconciliation | Site Down | P1 | IHS_OSU_0781A | T3091 | IBD | Ibadan | Osun | 3 - Low | OS0661 | WEST |  | 2025-11-28 00:52 | Ifechi Ugwueze | 2025-11-28 00:48 | 2025-11-28 01:10 | 1297 | 2025-11-28 00:48 | 2025-11-28 01:10 | 0:22 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006472544 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0766A | T3144 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 13:31 | Okusanya Joseph | 2025-11-28 13:29 | 2025-11-28 13:51 | 1294 | 2025-11-28 13:29 | 2025-11-28 13:51 | 0:22 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Generator (PPM) servicing was carried out on site without ref
NOCINC0006465980 | External Reconciliation | Site Down | P1 | IHS_EKI_0853A | EK2244 | IBD | Ibadan | Ekiti | 3 - Low | EK0373 | WEST |  | 2025-11-27 15:31 | Abisoye Olaleye | 2025-11-27 15:28 | 2025-11-27 15:50 | 1290 | 2025-11-27 15:28 | 2025-11-27 15:50 | 0:22 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | High engine temperature due to low coolant level, coolant was added
NOCINC0006480468 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0820A | T3187 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-29 14:20 | Ayodele Oludare | 2025-11-29 14:15 | 2025-11-29 14:36 | 1286 | 2025-11-29 14:15 | 2025-11-29 14:36 | 0:21 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 1 / 1 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | low oil pressure, oil was added
NOCINC0006477749 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0768A | T3220 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 08:00 | Mary Odefemi | 2025-11-29 07:55 | 2025-11-29 08:17 | 1285 | 2025-11-29 07:55 | 2025-11-29 08:17 | 0:21 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 2 | MTN NG |  | Imomoh Sylvanus |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | PPM was carried out on site (No diesel outage after validation) | PPM was carried out on site (No diesel outage after validation)
NOCINC0006446389 | External Reconciliation | Site Down | P4 | IHS_WAR_0956B | DL3350 | ASB | Asaba | Delta | 3 - Low | DL1149 | SOUTH SOUTH |  | 2025-11-25 09:12 | Tracy Osarumwense | 2025-11-25 09:12 | 2025-11-25 09:33 | 1282 | 2025-11-25 09:12 | 2025-11-25 09:33 | 0:21 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | David Uja |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Generator Servicing was completed at site | Generator Servicing was completed at site. (No diesel outage after validation).
NOCINC0006484054 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0736A | T3105 | IBD | Ibadan | Kwara | 3 - Low | KW0352 | WEST |  | 2025-11-30 01:12 | Okusanya Joseph | 2025-11-30 01:12 | 2025-11-30 01:33 | 1279 | 2025-11-30 01:12 | 2025-11-30 01:33 | 0:21 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Circuit Breaker | 1 / 2 | Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Faulty circuit breaker replaced
NOCINC0006463753 | External Reconciliation | Site Down | P4 | IHS_DEL_1118A | DL0580 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 10:38 | Bukola Olabanji | 2025-11-27 10:36 | 2025-11-27 10:57 | 1273 | 2025-11-27 10:36 | 2025-11-27 10:57 | 0:21 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 1 / 1 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump rack was worked on (no diesel outage after validation).
NOCINC0006471381 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1240B | ED5542 | IBD | Asaba | Edo | 3 - Low | ED1126 | SOUTH SOUTH |  | 2025-11-28 10:35 | Bukola Olabanji | 2025-11-28 10:34 | 2025-11-28 10:55 | 1268 | 2025-11-28 10:34 | 2025-11-28 10:55 | 0:21 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Jude Audu | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on (No diesel outage after validation) | Faulty injector pump was worked on (No diesel outage after validation)
NOCINC0006439839 | External Reconciliation | Site Down | P3 | IHS_KWA_0926C | KW4755 | IBD | Ibadan | Kwara | 3 - Low | KW0526 | WEST |  | 2025-11-24 12:40 | Azeezat Adekunle | 2025-11-24 12:36 | 2025-11-24 12:57 | 1266 | 2025-11-24 12:36 | 2025-11-24 12:57 | 0:21 | IPT | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | David Oyebamiji |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out
NOCINC0006464263 | External Reconciliation | Site Down | P1 | IHS_OND_0853A | T3443 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 11:38 | Iyesioluwa Ola | 2025-11-27 11:36 | 2025-11-27 11:57 | 1261 | 2025-11-27 11:36 | 2025-11-27 11:57 | 0:21 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 1 | MTN NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Faulty DG Governor Was Replaced
NOCINC0006440667 | External Reconciliation | Site Down | P1 | IHS_DEL_1144A | DL0757 | ASB | Asaba | Delta | 3 - Low | DL0648 | SOUTH SOUTH |  | 2025-11-24 13:56 | Ayokunle Samuel | 2025-11-24 13:56 | 2025-11-24 14:17 | 1260 | 2025-11-24 13:56 | 2025-11-24 14:17 | 0:21 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty charging alternator was worked on to restore the site. (No diesel outage after validation)
NOCINC0006449063 | External Reconciliation | Site Down | P4 | IHS_IBA_0086B | OY4185 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 14:28 | Mutmainnah Saba | 2025-11-25 14:24 | 2025-11-25 14:45 | 1258 | 2025-11-25 14:24 | 2025-11-25 14:45 | 0:21 | SPS | Equipment Repair | Passive | Infrastructure | Armoured Cable | 1 / 1 | MTN NG |  | Oremade Yusuf |  | Iyiola Azeez | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | burnt DC load cable was worked on
NOCINC0006470373 | External Reconciliation | Site Down | P3 | IHS_WAR_0922B | DL3276 | ASB | Asaba | Delta | 3 - Low | DL0934 | SOUTH SOUTH |  | 2025-11-28 07:49 | Oluwatobiloba Are | 2025-11-28 07:49 | 2025-11-28 08:10 | 1258 | 2025-11-28 07:49 | 2025-11-28 08:10 | 0:21 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Low oil pressure, Oil was topped up (No diesel outage after validation) | Low oil pressure, Oil was topped up (No diesel outage after validation)
NOCINC0006486048 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0800A | T3057 | IBD | Ibadan | Oyo | 3 - Low | OY1106 | WEST |  | 2025-11-30 11:00 | Aishat Oyedeji | 2025-11-30 10:59 | 2025-11-30 11:18 | 1150 | 2025-11-30 10:57 | 2025-11-30 11:18 | 0:21 | Biswal | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 7 | PPM (Generator servicing) was carried out on site with IHSREF/25110413472536457057 | PPM (Generator servicing) was carried out on site with IHSREF/25110413472536457057
NOCINC0006466547 | External Reconciliation | Site Down | P4 | IHS_OYO_0978A | T3866 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 16:53 | Titus Tosin | 2025-11-27 16:52 | 2025-11-27 17:13 | 1253 | 2025-11-27 16:52 | 2025-11-27 17:13 | 0:21 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | faulty solenoid was worked on
NOCINC0006476014 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1118A | DL0580 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 22:08 | Mary Odefemi | 2025-11-28 22:05 | 2025-11-28 22:26 | 1248 | 2025-11-28 22:05 | 2025-11-28 22:26 | 0:21 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Main Alternator | 1 / 1 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty main alternator was worked on (No diesel outage after validation)
NOCINC0006440999 | External Reconciliation | Site Down | P1 | IHS_WAR_0879H | T2907 | ASB | Asaba | Delta | 3 - Low | DL0635 | SOUTH SOUTH |  | 2025-11-24 14:41 | Tracy Osarumwense | 2025-11-24 14:41 | 2025-11-24 15:02 | 1246 | 2025-11-24 14:41 | 2025-11-24 15:02 | 0:21 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 5 | Faulty Injector Pump was worked on. | Faulty Injector Pump was worked on.(No diesel outage after validation).
NOCINC0006443537 | External Reconciliation | Site Down | P3 | IHS_EDO_0749A | T0218 | IBD | Asaba | Edo | 3 - Low | ED0700 | SOUTH SOUTH |  | 2025-11-24 20:08 | Evelyn Emagurehor | 2025-11-24 20:08 | 2025-11-24 20:29 | 1245 | 2025-11-24 20:08 | 2025-11-24 20:29 | 0:21 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006446047 | External Reconciliation | Site Down | P3 | IHS_EDO_1336B | ED1703 | IBD | Asaba | Edo | 3 - Low | ED0783 | SOUTH SOUTH |  | 2025-11-25 08:45 | Tracy Osarumwense | 2025-11-25 08:45 | 2025-11-25 09:05 | 1241 | 2025-11-25 08:45 | 2025-11-25 09:05 | 0:21 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Emmanuel Omakoji | Lasisi Sulaimon | Lasisi Sulaimon | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Generator Servicing was completed at site | Generator Servicing was completed at site. (No diesel outage after validation).
NOCINC0006452619 | External Reconciliation | Site Down | P4 | IHS_OYO_1085K | OY4080 | IBD | Ibadan | Osun | 3 - Low | - | - | OML Fault@2025-11-25 22:44:13@OY4080_Ode-ote Village Ibadan | 2025-11-25 22:58 | System Administrator | 2025-11-25 22:44 | 2025-11-25 23:05 | 1239 | 2025-11-25 22:44 | 2025-11-25 23:05 | 0:21 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Bayo Nathaniel |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting passive update from Fse. | Suspected passive issue, awaiting passive update from Fse.
NOCINC0006440810 | External Reconciliation | Site Down | P4 | IHS_OND_0063B | OD4807 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-24 14:08 | Ihuoma Opurum | 2025-11-24 14:07 | 2025-11-24 14:28 | 1238 | 2025-11-24 14:07 | 2025-11-24 14:28 | 0:21 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Usman Hammed |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | failed rectifier module was reset
NOCINC0006483284 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0014V | - | - | Asaba | Edo | 3 - Low | ED0016 | SOUTH SOUTH |  | 2025-11-29 21:52 | Muhammed Hashirudeen | 2025-11-29 21:51 | 2025-11-29 22:12 | 1237 | 2025-11-29 21:51 | 2025-11-29 22:12 | 0:21 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 1 / 1 | Airtel NG |  | SIMON SUNDAY | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty water pump was worked on (No diesel outage after validation)
NOCINC0006457289 | External Reconciliation | Site Down | P1 | IHS_DEL_1000A | DL0101 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 12:02 | Patrick Okoro | 2025-11-26 12:00 | 2025-11-26 12:21 | 1236 | 2025-11-26 12:00 | 2025-11-26 12:21 | 0:21 | Tyllium NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start
NOCINC0006439257 | External Reconciliation | Site Down | P1 | IHS_IBA_0074B | OY4200 | IBD | Ibadan | Oyo | 3 - Low | OY1031 | WEST |  | 2025-11-24 10:32 | Aishat Oyedeji | 2025-11-24 10:32 | 2025-11-24 10:52 | 1236 | 2025-11-24 10:32 | 2025-11-24 10:52 | 0:21 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | Airtel NG |  | SUNDAY MOSES |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG lost compression, site restored on solar
NOCINC0006476167 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0032B | OS4262 | IBD | Ibadan | Osun | 3 - Low | OS0700 | WEST |  | 2025-11-28 22:39 | Sheriff Salami | 2025-11-28 22:28 | 2025-11-28 22:49 | 1235 | 2025-11-28 22:28 | 2025-11-28 22:49 | 0:21 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | Airtel NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed Rectifier Module was reset
NOCINC0006474329 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0059B | OS2661 | IBD | Ibadan | Osun | 3 - Low | OS0684 | WEST |  | 2025-11-28 17:52 | Praise Okezie | 2025-11-28 17:49 | 2025-11-28 18:09 | 1229 | 2025-11-28 17:49 | 2025-11-28 18:09 | 0:20 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 2 | MTN NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid-DG synchronization failure due to unstable grid supply issue. DG was powered manually.
NOCINC0006477625 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 07:27 | Akachukwu Ugwu | 2025-11-29 07:25 | 2025-11-29 07:45 | 1223 | 2025-11-29 07:25 | 2025-11-29 07:45 | 0:20 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under voltage alarm. AVR adjusted (No diesel outage after validation). | DG under voltage alarm. AVR adjusted (No diesel outage after validation).
NOCINC0006483001 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1473B | AN3657 | ASB | Asaba | Anambra | 3 - Low | AN0878 | SOUTH EAST |  | 2025-11-29 21:14 | Gbemisola Adedeji | 2025-11-29 21:10 | 2025-11-29 21:30 | 1219 | 2025-11-29 21:10 | 2025-11-29 21:30 | 0:20 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | NNADOZIE CASMIR |  |  | Erik Nwodo | Nwigbo Chijioke |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | High DG temperature alarm was cleared, coolant was added (No diesel outage after validation) | High DG temperature alarm was cleared, coolant was added (No diesel outage after validation)
NOCINC0006446513 | External Reconciliation | Site Down | P3 | IHS_EDO_1250B | ED5532 | IBD | Asaba | Edo | 3 - Low | ED0936 | SOUTH SOUTH |  | 2025-11-25 09:19 | Tracy Osarumwense | 2025-11-25 09:19 | 2025-11-25 09:39 | 1216 | 2025-11-25 09:19 | 2025-11-25 09:39 | 0:20 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Alade Olufemi Olufem | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Generator Servicing was completed at site | Generator Servicing was completed at site. (No diesel outage after validation).
NOCINC0006473498 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1291B | OY1070 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 16:01 | Damilola Paseda | 2025-11-28 16:00 | 2025-11-28 16:20 | 1214 | 2025-11-28 16:00 | 2025-11-28 16:20 | 0:20 | Biswal | Equipment Repair | Passive | DCGG CB | DCGG - Faulty/Burnt Breaker | 1 / 1 | MTN NG |  | Lukman Mohammed | Habeeb Adepoju |  | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Burnt load breaker was replaced | Burnt load breaker was replaced
NOCINC0006437543 | External Reconciliation | Site Down | P4 | IHS_OND_1016C | OD6214 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-24 02:59 | Ayodele Oludare | 2025-11-24 02:59 | 2025-11-24 03:19 | 1214 | 2025-11-24 02:59 | 2025-11-24 03:19 | 0:20 | Inhouse | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Obuseh Williams |  |  | Ibrahim Akinpelu | Obuseh Williams |  | Lukman Amusat | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | failed rectifer module was reset
NOCINC0006463003 | External Reconciliation | Site Down | P1 | IHS_OND_0872A | T3454 | IBD | Ibadan | Ondo | 3 - Low | ON0607 | WEST |  | 2025-11-27 08:09 | Yewande Adeagbo | 2025-11-27 08:08 | 2025-11-27 08:28 | 1209 | 2025-11-27 08:08 | 2025-11-27 08:28 | 0:20 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | Mercy Oni |  | Ojadua Olusegun | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Faulty radiator was worked on
NOCINC0006489563 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0763A | T4402 | ASB | Asaba | Delta | 3 - Low | DL0798 | SOUTH SOUTH |  | 2025-11-30 20:30 | Solomon Bankole | 2025-11-30 20:29 | 2025-11-30 20:49 | 1202 | 2025-11-30 20:29 | 2025-11-30 20:49 | 0:20 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled ( No diesel outage after validation) | Tripped load breaker was enabled ( No diesel outage after validation)
NOCINC0006470424 | External Reconciliation | Site Down | P1 | IHS_OND_0823A | T3902 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 07:58 | Mary Elaigwu | 2025-11-28 07:58 | 2025-11-28 08:18 | 1201 | 2025-11-28 07:58 | 2025-11-28 08:18 | 0:20 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 1 / 1 | MTN NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Gid synchronization failure due to grid incomplete phase, DG was powered manually
NOCINC0006467494 | External Reconciliation | Site Down | P2 | IHS_OSU_0886A | T3047 | IBD | Ibadan | Osun | 3 - Low | OS0658 | WEST |  | 2025-11-27 19:46 | Bosede Kutelu | 2025-11-27 19:44 | 2025-11-27 20:04 | 1191 | 2025-11-27 19:44 | 2025-11-27 20:04 | 0:20 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 9 | Faulty fuel pump was worked on
NOCINC0006438377 | External Reconciliation | Site Down | P2 | IHS_OND_1000A | OD4809 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-24 07:54 | Abisoye Olaleye | 2025-11-24 07:50 | 2025-11-24 08:10 | 1191 | 2025-11-24 07:50 | 2025-11-24 08:10 | 0:20 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Benjamin Onwu |  |  | Ibrahim Akinpelu | Benjamin Onwu |  | Victor Adeoye | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Hybrid synchronization failure due to frozen SMU was reset.
NOCINC0006479471 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0796A | T2635 | ASB | Asaba | Delta | 3 - Low | DL0985 | SOUTH SOUTH |  | 2025-11-29 12:11 | Ayokunle Samuel | 2025-11-29 12:09 | 2025-11-29 12:24 | 929 | 2025-11-29 12:05 | 2025-11-29 12:24 | 0:19 | Tyllium NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 3 / 3 | Airtel NG, MTN NG, Smile |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Weak DG was primed to start. (No diesel outage after validation) | Weak DG was primed to start. (No diesel outage after validation)
NOCINC0006465776 | External Reconciliation | Site Down | P1 | IHS_DEL_0938A | T2914 | ASB | Asaba | Delta | 3 - Low | DL0644 | SOUTH SOUTH |  | 2025-11-27 15:09 | Mary Odefemi | 2025-11-27 15:06 | 2025-11-27 15:26 | 1169 | 2025-11-27 15:06 | 2025-11-27 15:26 | 0:19 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 2 / 2 | Airtel NG, MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | RMS snag clearance was completed at site with ref (IHSREF/25112605472637484237 SARID0009051195)
NOCINC0006438386 | External Reconciliation | Site Down | P1 | IHS_OYO_0908A | T3862 | IBD | Ibadan | Oyo | 3 - Low | OY0975 | WEST |  | 2025-11-24 07:56 | Osarieme Charles | 2025-11-24 07:56 | 2025-11-24 08:15 | 1128 | 2025-11-24 07:55 | 2025-11-24 08:15 | 0:19 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Hybrid Synchronization Failure due to frozen smu, smu was reset
NOCINC0006447846 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-25 11:56 | Emmanuel Faleti | 2025-11-25 11:56 | 2025-11-25 12:15 | 1163 | 2025-11-25 11:56 | 2025-11-25 12:15 | 0:19 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty Radiator was worked on (No diesel outage after validation) | Faulty Radiator was worked on (No diesel outage after validation)
NOCINC0006462839 | External Reconciliation | Site Down | P3 | IHS_OSU_0070B | OS4343 | IBD | Ibadan | Osun | 3 - Low | OS0735 | WEST |  | 2025-11-27 07:26 | Precious Attah | 2025-11-27 07:26 | 2025-11-27 07:45 | 1161 | 2025-11-27 07:26 | 2025-11-27 07:45 | 0:19 | IPT | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | MTN NG, Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to incomplete phase, DG was powered manually.
NOCINC0006438789 | External Reconciliation | Site Down | P4 | IHS_DEL_0955A | T2713 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 09:06 | Tracy Osarumwense | 2025-11-24 09:06 | 2025-11-24 09:25 | 1148 | 2025-11-24 09:06 | 2025-11-24 09:25 | 0:19 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | KELECHI LEWIS |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG High Temperature due to low Coolant level, Coolant was added. | DG High Temperature due to low Coolant level, Coolant was added. (No diesel outage after validation).
NOCINC0006441187 | External Reconciliation | Site Down | P3 | IHS_EDO_0987A | ED2044 | IBD | Asaba | Edo | 3 - Low | ED0551 | SOUTH SOUTH |  | 2025-11-24 15:00 | Evelyn Emagurehor | 2025-11-24 14:53 | 2025-11-24 15:12 | 1146 | 2025-11-24 14:53 | 2025-11-24 15:12 | 0:19 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 2 | Airtel NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak Refurbished DG was primed to start to restore power to the site. (No diesel outage after validation). | Weak Refurbished DG was primed to start to restore power to the site. (No diesel outage after validation).
NOCINC0006459328 | External Reconciliation | Site Down | P1 | IHS_DEL_0855A | T2737 | ASB | Asaba | Delta | 3 - Low | DL0243 | SOUTH SOUTH |  | 2025-11-26 17:18 | Mary Odefemi | 2025-11-26 17:18 | 2025-11-26 17:37 | 1143 | 2025-11-26 17:18 | 2025-11-26 17:37 | 0:19 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Kick Starter | 2 / 2 | Airtel NG, MTN NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty kick starter was worked on (No diesel outage after validation)
NOCINC0006446974 | External Reconciliation | Site Down | P1 | IHS_WAR_0875H | T2874 | ASB | Asaba | Delta | 3 - Low | DL0400 | SOUTH SOUTH |  | 2025-11-25 10:24 | Tracy Osarumwense | 2025-11-25 10:24 | 2025-11-25 10:43 | 1143 | 2025-11-25 10:24 | 2025-11-25 10:43 | 0:19 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | Stanley Odira |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low Oil Pressure, Oil was added. | Low Oil Pressure, Oil was added. (No diesel outage after validation).
NOCINC0006458282 | External Reconciliation | Site Down | P1 | IHS_BOM_0002B | DL0769 | ASB | Asaba | Delta | 3 - Low | DL0803 | SOUTH SOUTH |  | 2025-11-26 14:34 | Mary Odefemi | 2025-11-26 14:33 | 2025-11-26 14:52 | 1142 | 2025-11-26 14:33 | 2025-11-26 14:52 | 0:19 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset (No diesel outage after validation)
NOCINC0006472675 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0911A | T2775 | ASB | Asaba | Delta | 3 - Low | DL0560 | SOUTH SOUTH |  | 2025-11-28 13:59 | Bukola Olabanji | 2025-11-28 13:59 | 2025-11-28 14:18 | 1140 | 2025-11-28 13:59 | 2025-11-28 14:18 | 0:19 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 2 / 2 | Airtel NG, MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Faulty water pump was worked on
NOCINC0006486490 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0892A | T3074 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 12:04 | Precious Attah | 2025-11-30 12:03 | 2025-11-30 12:22 | 1135 | 2025-11-30 12:03 | 2025-11-30 12:22 | 0:19 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | MTN NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Low DG Frequency, AVR was Adjusted
NOCINC0006450551 | External Reconciliation | Site Down | P2 | IHS_OND_0838A | T3930 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-25 17:35 | Yewande Adeagbo | 2025-11-25 17:33 | 2025-11-25 17:52 | 1135 | 2025-11-25 17:33 | 2025-11-25 17:52 | 0:19 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gas Flow | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 3 | Freeze gas line was worked on
NOCINC0006459651 | External Reconciliation | Site Down | P3 | IHS_OSU_0070B | OS4343 | IBD | Ibadan | Osun | 3 - Low | OS0735 | WEST |  | 2025-11-26 18:19 | Titus Tosin | 2025-11-26 18:17 | 2025-11-26 18:36 | 1133 | 2025-11-26 18:17 | 2025-11-26 18:36 | 0:19 | IPT | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | MTN NG, Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to incomplete phase, DG was powered manually.
NOCINC0006486655 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0100C | OS2665 | IBD | Ibadan | Osun | 3 - Low | OS0846 | WEST |  | 2025-11-30 12:29 | Aishat Oyedeji | 2025-11-30 12:28 | 2025-11-30 12:47 | 1129 | 2025-11-30 12:28 | 2025-11-30 12:47 | 0:19 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out on site with IHSREF/25112307465844946037 | PPM (Generator servicing) was carried out on site with IHSREF/25112307465844946037
NOCINC0006478620 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0046B | DL0738 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 10:36 | Ayomide Akindolie | 2025-11-29 10:30 | 2025-11-29 10:49 | 1125 | 2025-11-29 10:30 | 2025-11-29 10:49 | 0:19 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Planned activity - RMS snag clearance with valid ref IHSREF/25112817413594336284
NOCINC0006477607 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0801A | T2658 | ASB | Asaba | Delta | 3 - Low | DL0797 | SOUTH SOUTH |  | 2025-11-29 07:25 | Mary Odefemi | 2025-11-29 07:25 | 2025-11-29 07:43 | 1123 | 2025-11-29 07:25 | 2025-11-29 07:43 | 0:19 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 2 / 2 | Airtel NG, MTN NG |  | Stanley Odira |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Faulty thermostat was isolated (No diesel outage after validation)
NOCINC0006487471 | Internal Reconciliation | Site Down | P2 | IHS_IBA_0720E | OY4036 | IBD | Ibadan | Oyo | 3 - Low | OY0910 | WEST |  | 2025-11-30 14:19 | Aishat Oyedeji | 2025-11-30 14:19 | 2025-11-30 14:37 | 1120 | 2025-11-30 14:19 | 2025-11-30 14:37 | 0:19 | SPS | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | BASHIR ABDULRASAQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | PPM (Generator serving) was carried out on site with Ref IHSREF/25112709360721582354 | PPM (Generator serving) was carried out on site with Ref IHSREF/25112709360721582354
NOCINC0006463176 | External Reconciliation | Site Down | P4 | IHS_EDO_1240B | ED5542 | IBD | Asaba | Edo | 3 - Low | ED1126 | SOUTH SOUTH |  | 2025-11-27 08:49 | Bukola Olabanji | 2025-11-27 08:48 | 2025-11-27 09:07 | 1116 | 2025-11-27 08:48 | 2025-11-27 09:07 | 0:19 | MPI NGA | Fuel Outage (Probable) | Passive | Diesel | Diesel Top-Up | 2 / 2 | MTN NG, Airtel NG |  | Jude Audu | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Diesel top-up was done on site (initial 1,343.7 before top-up).
NOCINC0006481217 | Internal Reconciliation | Site Down | P1 | IHS_OND_0895A | OD3381 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 16:06 | Testimony Akinyemi | 2025-11-29 16:05 | 2025-11-29 16:24 | 1114 | 2025-11-29 16:05 | 2025-11-29 16:24 | 0:19 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Battery | 2 / 2 | MTN NG, Airtel NG |  | Mercy Oni |  | Ojadua Olusegun | Soye West | Ugwu Samuel Nnamdi |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 6 | Rectifier battery overdischarge alarm was cleared
NOCINC0006473063 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1020A | OY3854 | IBD | Ibadan | Oyo | 3 - Low | OY1418 | WEST |  | 2025-11-28 14:53 | Oluwatomisin Ogunleye | 2025-11-28 14:51 | 2025-11-28 15:09 | 1111 | 2025-11-28 14:51 | 2025-11-28 15:09 | 0:19 | Inhouse | 3RD Party Power Failure | Passive | Power Provided By 3RD Party | Power Provided By 3RD Party | 2 / 2 | MTN NG, Airtel NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Power provided by 3rd party, power restored at IITA | Power provided by 3rd party, power restored at IITA
NOCINC0006467337 | External Reconciliation | Site Down | P3 | IHS_ILO_0027B | KW4596 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 19:11 | Okusanya Joseph | 2025-11-27 19:10 | 2025-11-27 19:29 | 1108 | 2025-11-27 19:10 | 2025-11-27 19:29 | 0:18 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Air Intake | 1 / 1 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | blocked fuel line was flushed
NOCINC0006469570 | External Reconciliation | Site Down | P2 | IHS_ANA_1404H | AN0523 | ASB | Asaba | Anambra | 3 - Low | AN0851 | SOUTH EAST |  | 2025-11-28 03:03 | Oluwatoyin Fagite | 2025-11-28 02:54 | 2025-11-28 03:13 | 1107 | 2025-11-28 02:54 | 2025-11-28 03:13 | 0:18 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 3 | Hybrid synchronization failure due to failed to start alarm alarm was cleared and DG powered manually (No diesel outage after validation) | Hybrid synchronization failure due to failed to start alarm alarm was cleared and DG powered manually (No diesel outage after validation)
NOCINC0006442223 | External Reconciliation | Site Down | P3 | IHS_OSU_0110C | OS4664 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 16:49 | Precious Attah | 2025-11-24 16:49 | 2025-11-24 17:06 | 977 | 2025-11-24 16:47 | 2025-11-24 17:06 | 0:18 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on
NOCINC0006470360 | External Reconciliation | Site Down | P1 | IHS_ILO_0733E | KW4627 | IBD | Ibadan | Kwara | 3 - Low | KW0363 | WEST |  | 2025-11-28 07:46 | Osarieme Charles | 2025-11-28 07:44 | 2025-11-28 08:02 | 1103 | 2025-11-28 07:44 | 2025-11-28 08:02 | 0:18 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | PPM was done on site without IHSREF 25112412165952680866.
NOCINC0006466871 | External Reconciliation | Site Down | P2 | IHS_WAR_0886H | DL0377 | ASB | Asaba | Delta | 3 - Low | DL0738 | SOUTH SOUTH |  | 2025-11-27 17:50 | Uthman Akinola | 2025-11-27 17:46 | 2025-11-27 18:04 | 1101 | 2025-11-27 17:46 | 2025-11-27 18:04 | 0:18 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 3 | MTN NG, Airtel NG |  | Victor Ezeh |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006476825 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0871A | T3283 | IBD | Asaba | Edo | 3 - Low | ED0451 | SOUTH SOUTH |  | 2025-11-29 02:50 | Elizabeth Apata | 2025-11-29 02:49 | 2025-11-29 03:08 | 1100 | 2025-11-29 02:49 | 2025-11-29 03:08 | 0:18 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen CSU. Frozen CSU was reset. (No diesel outage after validation)
NOCINC0006462987 | External Reconciliation | Site Down | P3 | IHS_EDO_1184H | ED2105 | IBD | Asaba | Edo | 3 - Low | ED0862 | SOUTH SOUTH | CSL Fault@2025-11-27 07:52:02@ED2105_IYI OBA HTN COLO_ BENIN | 2025-11-27 08:04 | System Administrator | 2025-11-27 07:59 | 2025-11-27 08:18 | 1098 | 2025-11-27 07:59 | 2025-11-27 08:18 | 0:18 | Huawei | Equipment Repair | Passive | Infrastructure | Armoured Cable | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Burnt load cable was worked on and re-terminated (No diesel outage after validation)
NOCINC0006457718 | External Reconciliation | Site Down | P2 | IHS_EDO_0747A | T0161 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 13:02 | Azeezat Badmus | 2025-11-26 12:59 | 2025-11-26 13:18 | 1089 | 2025-11-26 12:59 | 2025-11-26 13:18 | 0:18 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty load breaker was replaced (No diesel outage after validation)
NOCINC0006486259 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0757C | DL1099 | ASB | Asaba | Delta | 3 - Low | DL0709 | SOUTH SOUTH |  | 2025-11-30 11:33 | Tracy Osarumwense | 2025-11-30 11:33 | 2025-11-30 11:51 | 1089 | 2025-11-30 11:33 | 2025-11-30 11:51 | 0:18 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 1 / 1 | Airtel NG |  | Kehinde Adekanbi |  |  | Erik Nwodo | John Wekpe |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG under voltage, Under voltage alarm was cleared (No diesel outage after validation) | DG under voltage, Under voltage alarm was cleared (No diesel outage after validation)
NOCINC0006449574 | External Reconciliation | Site Down | P3 | IHS_EDO_0978A | ED2153 | IBD | Asaba | Edo | 3 - Low | ED0709 | SOUTH SOUTH |  | 2025-11-25 15:33 | Emmanuel Faleti | 2025-11-25 15:32 | 2025-11-25 15:50 | 1089 | 2025-11-25 15:32 | 2025-11-25 15:50 | 0:18 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 2 / 2 | MTN NG, Airtel NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 2 | Faulty temperature sensor switch was worked on (No diesel outage after validation) | Faulty temperature sensor switch was worked on (No diesel outage after validation)
NOCINC0006473459 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0080C | ED5167 | IBD | Asaba | Edo | 3 - Low | ED0815 | SOUTH SOUTH |  | 2025-11-28 15:53 | Muhammed Hashirudeen | 2025-11-28 15:49 | 2025-11-28 16:07 | 1086 | 2025-11-28 15:49 | 2025-11-28 16:07 | 0:18 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | MTN NG |  | EKPU SUNDAY |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Tripped lad breaker was enabled. (No diesel outage after validation)
NOCINC0006463450 | External Reconciliation | Site Down | P4 | IHS_KWA_0773A | T3148 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 09:46 | Okusanya Joseph | 2025-11-27 09:45 | 2025-11-27 10:03 | 1083 | 2025-11-27 09:45 | 2025-11-27 10:03 | 0:18 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Oyenini Olalekan |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | PPM (Generator servicing ) was carried out on site
NOCINC0006463866 | External Reconciliation | Site Down | P3 | IHS_OSU_0073B | OS4386 | IBD | Ibadan | Osun | 3 - Low | OS0712 | WEST |  | 2025-11-27 10:53 | Okusanya Joseph | 2025-11-27 10:52 | 2025-11-27 11:10 | 1081 | 2025-11-27 10:52 | 2025-11-27 11:10 | 0:18 | IPT | Fuel Outage (Probable) | Passive | Diesel | Diesel Top-Up | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Low diesel level, diesel was topped up
NOCINC0006441462 | External Reconciliation | Site Down | P1 | IHS_OYO_1031A | OY2893 | IBD | Ibadan | Oyo | 3 - Low | OY0970 | WEST |  | 2025-11-24 15:31 | Azeezat Adekunle | 2025-11-24 15:29 | 2025-11-24 15:47 | 1080 | 2025-11-24 15:29 | 2025-11-24 15:47 | 0:18 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | MTN NG |  | Olapo Adebunmi |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 4 | Suspected passive Issue on site, Awaiting update from FSE
NOCINC0006464616 | External Reconciliation | Site Down | P4 | IHS_OSU_0875A | OS3995 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 12:21 | Okusanya Joseph | 2025-11-27 12:21 | 2025-11-27 12:39 | 1078 | 2025-11-27 12:21 | 2025-11-27 12:39 | 0:18 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 1 / 1 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty thermostat was worked on
NOCINC0006473134 | Internal Reconciliation | Site Down | P1 | IHS_OND_0775A | T3404 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 15:04 | Testimony Akinyemi | 2025-11-28 15:02 | 2025-11-28 15:20 | 1076 | 2025-11-28 15:02 | 2025-11-28 15:20 | 0:18 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 2 / 2 | Airtel NG, MTN NG |  | Mercy Oni |  | Ojadua Olusegun | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | faulty water pump worked on
NOCINC0006472396 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0915A | T3858 | IBD | Ibadan | Oyo | 3 - Low | OY1032 | WEST |  | 2025-11-28 13:04 | Mutmainnah Saba | 2025-11-28 13:02 | 2025-11-28 13:20 | 1070 | 2025-11-28 13:02 | 2025-11-28 13:20 | 0:18 | SPS | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | OLAMILEKAN SOYEBO |  | Olumide Adebayo | Ridwan Adepoju | Olufemi Akinlusi |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty Injector Pump was Worked On
NOCINC0006474974 | Internal Reconciliation | Site Down | P3 | IHS_KWA_1057B | - | - | Ibadan | Kwara | 3 - Low | KW0600 | WEST |  | 2025-11-28 19:31 | Okusanya Joseph | 2025-11-28 19:30 | 2025-11-28 19:48 | 1069 | 2025-11-28 19:30 | 2025-11-28 19:48 | 0:18 | Energy Vision Nigeria | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | Airtel NG |  | Omotayo Makusota |  |  | Nosakhare Imade | Sani Nasir |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to DG failed to start alarm was cleared and DG was Powered manually
NOCINC0006482230 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0970A | T3827 | IBD | Ibadan | Oyo | 3 - Low | OY1352 | WEST |  | 2025-11-29 18:51 | Valentine Adinnu | 2025-11-29 18:49 | 2025-11-29 19:07 | 1069 | 2025-11-29 18:49 | 2025-11-29 19:07 | 0:18 | Inhouse | Equipment Repair | Passive | Rectifier | Rectifier - Phase Controller | 2 / 2 | Airtel NG, MTN NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty rectifier phase controller was bypassed | Faulty rectifier phase controller was bypassed
NOCINC0006470860 | External Reconciliation | Site Down | P2 | IHS_KWA_0737A | T3110 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 09:17 | Praise Okezie | 2025-11-28 09:15 | 2025-11-28 09:33 | 1069 | 2025-11-28 09:15 | 2025-11-28 09:33 | 0:18 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | PPM done (Generator servicing) without Access Ref
NOCINC0006485345 | Internal Reconciliation | Site Down | P1 | IHS_OYO_1080K | OY2999 | IBD | Ibadan | Oyo | 3 - Low | OY1055 | WEST |  | 2025-11-30 08:38 | Aishat Oyedeji | 2025-11-30 08:38 | 2025-11-30 08:56 | 1068 | 2025-11-30 08:38 | 2025-11-30 08:56 | 0:18 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 2 / 2 | MTN NG, Airtel NG |  | Lukman Mohammed | Habeeb Adepoju |  | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Voltage fluctuation due to weak BUB, GG auto-restarted. | Voltage fluctuation due to weak BUB, GG auto-restarted.
NOCINC0006467413 | External Reconciliation | Site Down | P4 | IHS_EDO_1234B | ED5514 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 19:29 | Muhammed Hashirudeen | 2025-11-27 19:29 | 2025-11-27 19:46 | 1067 | 2025-11-27 19:29 | 2025-11-27 19:46 | 0:18 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 1 / 1 | MTN NG |  | Christopher Aiyenale |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed rectifier CSU was reset (No diesel outage after validation) | Failed rectifier CSU was reset (No diesel outage after validation)
NOCINC0006467624 | External Reconciliation | Site Down | P3 | IHS_OND_0058B | OD4813 | IBD | Ibadan | Ondo | 3 - Low | ON0686 | WEST |  | 2025-11-27 20:06 | Abisoye Olaleye | 2025-11-27 20:04 | 2025-11-27 20:21 | 1066 | 2025-11-27 20:04 | 2025-11-27 20:21 | 0:18 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Tripped DG Load Breaker Was Enabled.
NOCINC0006484450 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1115A | DL0492 | ASB | Asaba | Delta | 3 - Low | DL0920 | SOUTH SOUTH |  | 2025-11-30 03:57 | Bukola Olabanji | 2025-11-30 03:56 | 2025-11-30 04:14 | 1065 | 2025-11-30 03:56 | 2025-11-30 04:14 | 0:18 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | MTN NG, Airtel NG |  | David Uja |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Flat DG battery, external battery was used to power site
NOCINC0006443945 | External Reconciliation | Site Down | P4 | IHS_BEN_0032V | ED5182 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 21:19 | Solomon Bankole | 2025-11-24 21:17 | 2025-11-24 21:35 | 1064 | 2025-11-24 21:17 | 2025-11-24 21:35 | 0:18 | MPI NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | SAMUEL ASUKWO |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to start fail alarm. RES: Alarm was cleared and Gen powered manually | Hybrid synchronization failure due to start fail alarm. RES: Alarm was cleared and Gen powered manually
NOCINC0006443404 | External Reconciliation | Site Down | P1 | IHS_ANA_0786A | T0285/T6512 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 19:48 | Ayokunle Samuel | 2025-11-24 19:43 | 2025-11-24 20:00 | 1064 | 2025-11-24 19:43 | 2025-11-24 20:00 | 0:18 | Huawei | Grid Supply | Passive | Grid | National Grid - Low Current Supply | 1 / 2 | MTN NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Hybrid failure due to low voltage, DG powered manually to restore site. (No diesel outage after validation) | Hybrid failure due to low voltage, DG powered manually to restore site. (No diesel outage after validation)
NOCINC0006449479 | External Reconciliation | Site Down | P1 | IHS_OYO_0998A | OY2821 | IBD | Ibadan | Oyo | 3 - Low | - | - | Cascaded Incident from TTO6732699 - Cascade Removed From TTO6732699 | 2025-11-25 15:18 | Mutmainnah Saba | 2025-11-25 15:15 | 2025-11-25 15:33 | 1064 | 2025-11-25 15:15 | 2025-11-25 15:33 | 0:18 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Lukman Mohammed |  |  | Abiola Adegbiji | Habeeb Adepoju |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | high temperature alarm was cleared, coolant was added
NOCINC0006472476 | Internal Reconciliation | Site Down | P2 | IHS_OND_0839A | T3924 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 13:18 | Maureen Uchehorke | 2025-11-28 13:18 | 2025-11-28 13:36 | 1063 | 2025-11-28 13:18 | 2025-11-28 13:36 | 0:18 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | failed charging alternator was excited
NOCINC0006470940 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0774A | T0090 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 09:30 | Damilola Paseda | 2025-11-28 09:28 | 2025-11-28 09:46 | 1060 | 2025-11-28 09:28 | 2025-11-28 09:46 | 0:18 | SPS | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 3 | MTN NG |  | BASHIR ABDULRASAQ | Yusuf Gyang |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | PPM was carried out at the site with IHSREF/25112709360827320807 | PPM was carried out at the site with IHSREF/25112709360827320807
NOCINC0006486631 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0936A | T2991 | ASB | Asaba | Delta | 3 - Low | DL0750 | SOUTH SOUTH |  | 2025-11-30 12:24 | Ayomide Akindolie | 2025-11-30 12:22 | 2025-11-30 12:39 | 1060 | 2025-11-30 12:22 | 2025-11-30 12:39 | 0:18 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 1 / 2 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Low Oil Pressure, Oil was added. | Low Oil Pressure, Oil was added. (No diesel outage after validation).
NOCINC0006478327 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0736A | T3105 | IBD | Ibadan | Kwara | 3 - Low | KW0352 | WEST |  | 2025-11-29 09:44 | Azeezat Adekunle | 2025-11-29 09:42 | 2025-11-29 09:59 | 1053 | 2025-11-29 09:42 | 2025-11-29 09:59 | 0:18 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Suspected passive Issue on site, Awaiting update from FSE
NOCINC0006467372 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-27 19:19 | Akachukwu Ugwu | 2025-11-27 19:15 | 2025-11-27 19:33 | 1052 | 2025-11-27 19:15 | 2025-11-27 19:33 | 0:18 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty AVR was worked on (No diesel outage after validation) | Faulty AVR was worked on (No diesel outage after validation)
NOCINC0006440544 | External Reconciliation | Site Down | P1 | IHS_DEL_0779A | T0283 | ASB | Asaba | Delta | 3 - Low | DL1038 | SOUTH SOUTH |  | 2025-11-24 13:33 | Ezinne Ubachukwu | 2025-11-24 13:32 | 2025-11-24 13:50 | 1050 | 2025-11-24 13:32 | 2025-11-24 13:50 | 0:18 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Adedeji Olusegun |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Under frequency., Governor was adjusted (No diesel outage after validation) | Under frequency., Governor was adjusted (No diesel outage after validation)
NOCINC0006484728 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0764A | T0150/T2992 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 05:38 | Bukola Olabanji | 2025-11-30 05:37 | 2025-11-30 05:54 | 1044 | 2025-11-30 05:37 | 2025-11-30 05:54 | 0:17 | BJ Bison NGA | Equipment Repair | Passive | Control Panel | Faulty Circuit Breaker | 1 / 1 | MTN NG |  | KELECHI LEWIS |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty DG load breaker was replaced
NOCINC0006486327 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1142A | DL0762 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 11:41 | Ayokunle Samuel | 2025-11-30 11:26 | 2025-11-30 11:44 | 1044 | 2025-11-30 11:26 | 2025-11-30 11:44 | 0:17 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | Gen Temp High | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG high temperature, Coolant was added. (No diesel outage after validation) | DG high temperature, Coolant was added. (No diesel outage after validation)
NOCINC0006442697 | External Reconciliation | Site Down | P3 | IHS_OSU_0869A | T3670 | IBD | Ibadan | Osun | 3 - Low | OS0668 | WEST |  | 2025-11-24 18:00 | Victor Otugo | 2025-11-24 18:00 | 2025-11-24 18:15 | 921 | 2025-11-24 17:58 | 2025-11-24 18:15 | 0:17 | IPT | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid DG synchronisation delay due to unstable grid supply issue, DG powered manually
NOCINC0006441649 | External Reconciliation | Site Down | P1 | IHS_OND_0789A | T3408 | IBD | Ibadan | Ondo | 3 - Low | ON0576 | WEST |  | 2025-11-24 16:06 | Yewande Adeagbo | 2025-11-24 16:04 | 2025-11-24 16:22 | 1042 | 2025-11-24 16:04 | 2025-11-24 16:22 | 0:17 | Huawei | Grid Supply | Passive | Grid | National Grid - Circuit Breaker | 2 / 2 | MTN NG, Airtel NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Grid-DG synchronization failure due to faulty grid circuit breaker was worked on.
NOCINC0006489273 | Internal Reconciliation | Site Down | P1 | IHS_AWK_0016B | AN0088 | ASB | Asaba | Anambra | 3 - Low | AN0662 | SOUTH EAST |  | 2025-11-30 19:18 | Ezinne Ubachukwu | 2025-11-30 19:13 | 2025-11-30 19:31 | 1041 | 2025-11-30 19:13 | 2025-11-30 19:31 | 0:17 | BJ Bison NGA | Fuel Outage (Probable) | Passive | Diesel | Water Separator Blockage | 2 / 2 | MTN NG, Airtel NG |  | Egbujor Victor | Hillary Uduak | Hillary Uduak | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | choked water separator was serviced (No diesel outage after validation) | choked water separator was serviced (No diesel outage after validation)
NOCINC0006465553 | External Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-27 14:34 | Bukola Olabanji | 2025-11-27 14:31 | 2025-11-27 14:48 | 1041 | 2025-11-27 14:31 | 2025-11-27 14:48 | 0:17 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was replaced
NOCINC0006451987 | External Reconciliation | Site Down | P2 | IHS_EDO_0795A | T3218 | IBD | Asaba | Edo | 3 - Low | ED0630 | SOUTH SOUTH |  | 2025-11-25 21:17 | Evelyn Emagurehor | 2025-11-25 21:14 | 2025-11-25 21:32 | 1039 | 2025-11-25 21:14 | 2025-11-25 21:32 | 0:17 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Grid-DG synchronization failure due to incomplete grid phase. DG was powered manually. (No diesel outage after validation). | Grid-DG synchronization failure due to incomplete grid phase. DG was powered manually. (No diesel outage after validation).
NOCINC0006483889 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0738C | DL1027 | ASB | Asaba | Delta | 3 - Low | DL0732 | SOUTH SOUTH |  | 2025-11-30 00:01 | Bukola Olabanji | 2025-11-30 00:01 | 2025-11-30 00:18 | 1039 | 2025-11-30 00:01 | 2025-11-30 00:18 | 0:17 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | Airtel NG, MTN NG |  | Kevwe Oshoture |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | DG low frequency governor was adjusted
NOCINC0006449497 | External Reconciliation | Site Down | P2 | IHS_EDO_0017B | ED5089 | IBD | Asaba | Edo | 3 - Low | ED0663 | SOUTH SOUTH |  | 2025-11-25 15:21 | Emmanuel Faleti | 2025-11-25 15:20 | 2025-11-25 15:38 | 1039 | 2025-11-25 15:20 | 2025-11-25 15:38 | 0:17 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty charging alternator was excited pending replacement (No diesel outage after validation) | Faulty charging alternator was excited pending replacement (No diesel outage after validation)
NOCINC0006475735 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0825A | T3979 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 21:26 | Titus Tosin | 2025-11-28 21:22 | 2025-11-28 21:40 | 1038 | 2025-11-28 21:22 | 2025-11-28 21:40 | 0:17 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty load breaker was replaced
NOCINC0006458917 | External Reconciliation | Site Down | P2 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 16:04 | Emmanuel Faleti | 2025-11-26 16:03 | 2025-11-26 16:20 | 1036 | 2025-11-26 16:03 | 2025-11-26 16:20 | 0:17 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Ste is affected by ED4860. (No diesel outage after validation) | POFC: Ste is affected by ED4860. (No diesel outage after validation)
NOCINC0006471112 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0899A | KW4559 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 09:56 | Praise Okezie | 2025-11-28 09:54 | 2025-11-28 10:11 | 1035 | 2025-11-28 09:54 | 2025-11-28 10:11 | 0:17 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Afolabi Ganiyyu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | PPM (Generator servicing) was carried out on site.
NOCINC0006474929 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0042B | DL0624 | ASB | Asaba | Delta | 3 - Low | DL0809 | SOUTH SOUTH |  | 2025-11-28 19:25 | Quadri Ogundare | 2025-11-28 19:23 | 2025-11-28 19:40 | 1034 | 2025-11-28 19:23 | 2025-11-28 19:40 | 0:17 | BJ Bison NGA | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006459118 | External Reconciliation | Site Down | P3 | IHS_WAR_0963C | DL4026 | ASB | Asaba | Delta | 3 - Low | DL0975 | SOUTH SOUTH |  | 2025-11-26 16:40 | Mary Odefemi | 2025-11-26 16:38 | 2025-11-26 16:55 | 1028 | 2025-11-26 16:38 | 2025-11-26 16:55 | 0:17 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | MTN NG, Airtel NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 4 | Faulty radiator was worked on (No diesel outage after validation)
NOCINC0006472932 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0766A | T3144 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 14:37 | Okusanya Joseph | 2025-11-28 14:36 | 2025-11-28 14:54 | 1028 | 2025-11-28 14:36 | 2025-11-28 14:54 | 0:17 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Failed rectifier module, module was added
NOCINC0006449898 | External Reconciliation | Site Down | P4 | IHS_OYO_1242H | OY4479 | IBD | Ibadan | Oyo | 3 - Low | OY1532 | WEST |  | 2025-11-25 16:20 | Victor Otugo | 2025-11-25 16:18 | 2025-11-25 16:35 | 1027 | 2025-11-25 16:18 | 2025-11-25 16:35 | 0:17 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG Udervoltage alarm was cleared
NOCINC0006480367 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0012B | ED5016 | IBD | Asaba | Edo | 3 - Low | ED0637 | SOUTH SOUTH |  | 2025-11-29 14:04 | Evelyn Emagurehor | 2025-11-29 14:03 | 2025-11-29 14:20 | 1025 | 2025-11-29 14:03 | 2025-11-29 14:20 | 0:17 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Tripped load breaker due to partial contact was worked on (No diesel outage after validation)
NOCINC0006448637 | External Reconciliation | Site Down | P3 | IHS_EDO_1196H | ED5129 | IBD | Asaba | Edo | 3 - Low | ED0626 | SOUTH SOUTH |  | 2025-11-25 13:37 | Oluwatomisin Sogbesan | 2025-11-25 13:34 | 2025-11-25 13:51 | 1023 | 2025-11-25 13:34 | 2025-11-25 13:51 | 0:17 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Burnt load braker was replaced (No diesel outage after validation) | Burnt load braker was replaced (No diesel outage after validation)
NOCINC0006489226 | Resolved | Site Down | P1 | IHS_WAR_0932B | DL3316 | ASB | Asaba | Delta | 3 - Low | DL0672 | SOUTH SOUTH |  | 2025-11-30 19:11 | Ezinne Ubachukwu | 2025-11-30 19:08 | 2025-11-30 19:25 | 1013 | 2025-11-30 19:08 | 2025-11-30 19:25 | 0:17 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 2 | MTN NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Suspected passive issue, Awaiting RCA from FSE
NOCINC0006467416 | External Reconciliation | Site Down | P2 | IHS_OYO_1020A | OY3854 | IBD | Ibadan | Oyo | 3 - Low | OY1418 | WEST |  | 2025-11-27 19:30 | Sheriff Salami | 2025-11-27 19:27 | 2025-11-27 19:44 | 1011 | 2025-11-27 19:27 | 2025-11-27 19:44 | 0:17 | Inhouse | 3RD Party Power Failure | Passive | Power Provided By 3RD Party | Power Provided By 3RD Party | 2 / 2 | MTN NG, Airtel NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | 3rd party power failure. Power was provided by 3rd party(IITA)
NOCINC0006440877 | External Reconciliation | Site Down | P4 | IHS_WAR_0964B | DL4012 | ASB | Asaba | Delta | 3 - Low | DL1306 | SOUTH SOUTH |  | 2025-11-24 14:21 | Ayokunle Samuel | 2025-11-24 14:21 | 2025-11-24 14:36 | 890 | 2025-11-24 14:19 | 2025-11-24 14:36 | 0:17 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Monday Agha | Igwe Samuel | Igwe Samuel | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed rectifier module was reset. (No diesel outage after validation) | Failed rectifier module was reset. (No diesel outage after validation)
NOCINC0006438955 | External Reconciliation | Site Down | P2 | IHS_OSU_0953A | OS4274 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 09:35 | Victor Otugo | 2025-11-24 09:31 | 2025-11-24 09:48 | 1008 | 2025-11-24 09:31 | 2025-11-24 09:48 | 0:17 | IPT | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 2 | Airtel NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | hybrid synchronization failure due to frozen Orion, Orion was reset
NOCINC0006478831 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 10:59 | Kehinde Akinbowale | 2025-11-29 10:55 | 2025-11-29 11:12 | 1007 | 2025-11-29 10:55 | 2025-11-29 11:12 | 0:17 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | Airtel NG, MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty AVR was replaced to restore site(No diesel outage after validation) | Faulty AVR was replaced to restore site(No diesel outage after validation)
NOCINC0006486383 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0791A | T3007 | IBD | Ibadan | Oyo | 3 - Low | OY0941 | WEST |  | 2025-11-30 11:45 | Victor Otugo | 2025-11-30 11:44 | 2025-11-30 12:01 | 1002 | 2025-11-30 11:44 | 2025-11-30 12:01 | 0:17 | SPS | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 3 | Airtel NG, MTN NG |  | BASHIR ABDULRASAQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 3 | PPM (Generator servicing) was carried out on Site with Ref IHSREF/25113010463093108642
NOCINC0006465712 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-27 14:55 | Muhammed Hashirudeen | 2025-11-27 14:55 | 2025-11-27 15:11 | 1002 | 2025-11-27 14:55 | 2025-11-27 15:11 | 0:17 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006447713 | External Reconciliation | Site Down | P1 | IHS_EDO_0772A | T0916 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 11:40 | Oluwatomisin Sogbesan | 2025-11-25 11:40 | 2025-11-25 11:57 | 1001 | 2025-11-25 11:40 | 2025-11-25 11:57 | 0:17 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Saheed Yusuf |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Generator servicing was carried out on site (No diesel outage after validation) | Generator servicing was carried out on site (No diesel outage after validation)
NOCINC0006490001 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1208A | AN0578 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 21:59 | Kehinde Akinbowale | 2025-11-30 21:59 | 2025-11-30 22:14 | 916 | 2025-11-30 21:57 | 2025-11-30 22:14 | 0:17 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 1 | MTN NG |  | Madu Modestus | Madu Modestus | Madu Modestus | Fady Safwat | Aliyu Garuba |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Low DG frequency, Governor was adjusted(No diesel outage after validation) | Low DG frequency, Governor was adjusted(No diesel outage after validation)
NOCINC0006444215 | External Reconciliation | Site Down | P3 | IHS_IBA_0103C | OY4368 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 21:58 | Damilola Paseda | 2025-11-24 21:56 | 2025-11-24 22:12 | 998 | 2025-11-24 21:56 | 2025-11-24 22:12 | 0:17 | SPS | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify | 1 | Failed rectifier module was reset | Failed rectifier module was reset
NOCINC0006439704 | External Reconciliation | Site Down | P3 | IHS_KWA_0914A | KW4594 | IBD | Ibadan | Kwara | 3 - Low | KW0418 | WEST |  | 2025-11-24 12:11 | Azeezat Adekunle | 2025-11-24 12:11 | 2025-11-24 12:28 | 996 | 2025-11-24 12:11 | 2025-11-24 12:28 | 0:17 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | tripped load breaker was enabled
NOCINC0006489656 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0922A | T3550 | IBD | Ibadan | Oyo | 3 - Low | OY0712 | WEST |  | 2025-11-30 20:47 | Damilola Paseda | 2025-11-30 20:45 | 2025-11-30 21:02 | 995 | 2025-11-30 20:45 | 2025-11-30 21:02 | 0:17 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen CSU, CSU was reset | Hybrid synchronization failure due to frozen CSU, CSU was reset
NOCINC0006474113 | Internal Reconciliation | Site Down | P4 | IHS_OYO_0023B | OY4041 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 17:23 | Praise Okezie | 2025-11-28 17:21 | 2025-11-28 17:38 | 994 | 2025-11-28 17:21 | 2025-11-28 17:38 | 0:17 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start
NOCINC0006465371 | External Reconciliation | Site Down | P4 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 14:09 | Elizabeth Apata | 2025-11-27 14:06 | 2025-11-27 14:23 | 993 | 2025-11-27 14:06 | 2025-11-27 14:23 | 0:17 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site is powered from ED4860
NOCINC0006470365 | Internal Reconciliation | Site Down | P2 | IHS_OND_0977A | OD4733 | IBD | Ibadan | Osun | 3 - Low | ON0772 | WEST |  | 2025-11-28 07:47 | Mary Elaigwu | 2025-11-28 07:47 | 2025-11-28 08:04 | 992 | 2025-11-28 07:47 | 2025-11-28 08:04 | 0:17 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Aja |  |  | Ibrahim Akinpelu | Emmanuel Aja |  | Oluwafemi Iyiola | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | High engine temperature, coolant was added and power restored
NOCINC0006449202 | External Reconciliation | Site Down | P3 | IHS_ANA_0755E | AN0125 | ASB | Asaba | Anambra | 3 - Low | AN0820 | SOUTH EAST |  | 2025-11-25 14:42 | Oluwatoyin Fagite | 2025-11-25 14:40 | 2025-11-25 14:57 | 991 | 2025-11-25 14:40 | 2025-11-25 14:57 | 0:17 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Appeal John |  |  | Erik Nwodo | Nwigbo Chijioke |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006464967 | External Reconciliation | Site Down | P4 | IHS_OSU_0875A | OS3995 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 13:07 | Okusanya Joseph | 2025-11-27 13:05 | 2025-11-27 13:23 | 1051 | 2025-11-27 13:06 | 2025-11-27 13:23 | 0:17 | IPT | Equipment Repair | Passive | ACDG Gen | Gen Temp High | 1 / 1 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | High engine temperature due to blocked radiator, coolant was added and radiator was flushed.
NOCINC0006489162 | Internal Reconciliation | Site Down | P1 | IHS_OYO_1057A | OY2867 | IBD | Ibadan | Oyo | 3 - Low | OY0976 | WEST |  | 2025-11-30 19:00 | Victor Otugo | 2025-11-30 18:59 | 2025-11-30 19:15 | 989 | 2025-11-30 18:59 | 2025-11-30 19:15 | 0:16 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gas Flow | 2 / 2 | MTN NG, Airtel NG |  | Lukman Mohammed |  | Iyiola Azeez | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty gas line was worked on
NOCINC0006479856 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0807A | T2670 | ASB | Asaba | Delta | 3 - Low | DL0893 | SOUTH SOUTH |  | 2025-11-29 13:02 | Ayomide Akindolie | 2025-11-29 13:02 | 2025-11-29 13:19 | 989 | 2025-11-29 13:02 | 2025-11-29 13:19 | 0:16 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 2 / 2 | Airtel NG, MTN NG |  | Stanley Odira |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty radiator hose was worked on (No diesel outage after validation) | Faulty radiator hose was worked on (No diesel outage after validation)
NOCINC0006490229 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0922A | T3550 | IBD | Ibadan | Oyo | 3 - Low | OY0712 | WEST |  | 2025-11-30 22:46 | Damilola Paseda | 2025-11-30 22:44 | 2025-11-30 23:01 | 989 | 2025-11-30 22:44 | 2025-11-30 23:01 | 0:16 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 2 / 2 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting passive update from FSE | Suspected passive issue, awaiting passive update from FSE
NOCINC0006465377 | External Reconciliation | Site Down | P1 | IHS_EDO_0996A | ED4860 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 14:10 | Elizabeth Apata | 2025-11-27 14:07 | 2025-11-27 14:23 | 986 | 2025-11-27 14:07 | 2025-11-27 14:23 | 0:16 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on No diesel outage after validation) | Faulty ATS contactor was worked on No diesel outage after validation)
NOCINC0006457895 | External Reconciliation | Site Down | P3 | IHS_EDO_1308B | - | - | Asaba | Edo | 3 - Low | ED0795 | SOUTH SOUTH |  | 2025-11-26 13:37 | Emmanuel Faleti | 2025-11-26 13:29 | 2025-11-26 13:45 | 983 | 2025-11-26 13:29 | 2025-11-26 13:45 | 0:16 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | Airtel NG |  | Mike Imomoh | Mike Imomoh | Mike Imomoh | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Generator servicing was completed at site. (No diesel outage after validation) | Generator servicing was completed at site. (No diesel outage after validation)
NOCINC0006447899 | External Reconciliation | Site Down | P3 | IHS_EDO_0978A | ED2153 | IBD | Asaba | Edo | 3 - Low | ED0709 | SOUTH SOUTH |  | 2025-11-25 12:06 | Oluwatomisin Sogbesan | 2025-11-25 12:04 | 2025-11-25 12:20 | 980 | 2025-11-25 12:04 | 2025-11-25 12:20 | 0:16 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 2 | MTN NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 2 | DG high temperature due to low coolants level. coolant was added (No diesel outage after validation) | DG high temperature due to low coolants level. coolant was added (No diesel outage after validation)
NOCINC0006489114 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0922A | T3550 | IBD | Ibadan | Oyo | 3 - Low | OY0712 | WEST |  | 2025-11-30 18:47 | Aishat Oyedeji | 2025-11-30 18:46 | 2025-11-30 19:02 | 980 | 2025-11-30 18:46 | 2025-11-30 19:02 | 0:16 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen CSU, CSU was reset | Hybrid synchronization failure due to frozen CSU, CSU was reset
NOCINC0006459524 | External Reconciliation | Site Down | P1 | IHS_KWA_0965H | KW2351 | IBD | Ibadan | Kwara | 3 - Low | KW0579 | WEST |  | 2025-11-26 17:53 | Titus Tosin | 2025-11-26 17:53 | 2025-11-26 18:09 | 978 | 2025-11-26 17:53 | 2025-11-26 18:09 | 0:16 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 3 / 3 | MTN NG, Airtel NG, INQ |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was completed at site
NOCINC0006475781 | Internal Reconciliation | Site Down | P2 | IHS_IBA_0716E | OY4328 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 21:32 | Bosede Kutelu | 2025-11-28 21:30 | 2025-11-28 21:46 | 975 | 2025-11-28 21:30 | 2025-11-28 21:46 | 0:16 | SPS | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Failed Rectifier Module Was Reset
NOCINC0006476321 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1126A | AN0439 | ASB | Asaba | Anambra | 3 - Low | AN0667 | SOUTH EAST |  | 2025-11-28 23:13 | Femi Olanipekun | 2025-11-28 23:11 | 2025-11-28 23:27 | 974 | 2025-11-28 23:11 | 2025-11-28 23:27 | 0:16 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | Amadi Fabian | Tijani Haruna | Tijani Haruna | Henry Wanogho | Ifeanyi Chukusa |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Low oil pressure, oil was added. (No diesel outage after validation) | Low oil pressure, oil was added. (No diesel outage after validation)
NOCINC0006475392 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1066A | DL0404 | ASB | Asaba | Delta | 3 - Low | DL0746 | SOUTH SOUTH |  | 2025-11-28 20:41 | Mary Odefemi | 2025-11-28 20:41 | 2025-11-28 20:57 | 971 | 2025-11-28 20:41 | 2025-11-28 20:57 | 0:16 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Solenoid Coil | 2 / 2 | Airtel NG, MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty solenoid was worked on (No diesel outage after validation)
NOCINC0006468626 | External Reconciliation | Site Down | P2 | IHS_OYO_0932A | T3873 | IBD | Ibadan | Oyo | 3 - Low | OY1125 | WEST | The link between the server and the ME is broken@2025-11-27 23:05:23@OY1125(31125) | 2025-11-27 23:26 | System Administrator | 2025-11-27 23:05 | 2025-11-28 | 3263 | 2025-11-27 22:07 | 2025-11-27 22:23 | 0:16 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 2 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to failed csu, csu was reset
NOCINC0006485553 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1110A | DL0668 | ASB | Asaba | Delta | 3 - Low | DL0676 | SOUTH SOUTH |  | 2025-11-30 09:19 | Ayomide Akindolie | 2025-11-30 09:19 | 2025-11-30 09:35 | 969 | 2025-11-30 09:19 | 2025-11-30 09:35 | 0:16 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low Oil Pressure, Oil was added. | Low Oil Pressure, Oil was added. . (No diesel outage after validation).
NOCINC0006477691 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0874A | ED3970 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 07:43 | Elizabeth Apata | 2025-11-29 07:41 | 2025-11-29 07:57 | 967 | 2025-11-29 07:41 | 2025-11-29 07:57 | 0:16 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Faulty AVR was worked on to restore power to the site. (No diesel outage after validation). | Faulty AVR was worked on to restore power to the site. (No diesel outage after validation).
NOCINC0006451944 | External Reconciliation | Site Down | P1 | IHS_DEL_0870A | T2742 | ASB | Asaba | Delta | 3 - Low | DL1269 | SOUTH SOUTH |  | 2025-11-25 21:11 | Ayomide Akindolie | 2025-11-25 21:10 | 2025-11-25 21:26 | 966 | 2025-11-25 21:10 | 2025-11-25 21:26 | 0:16 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Fuel Lifting Pump Faulty | 2 / 2 | MTN NG, Airtel NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 2 | Faulty lift pump was worked on (No diesel outage after validation)
NOCINC0006474212 | Internal Reconciliation | Site Down | P4 | IHS_IBA_0028V | OY2880 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 17:36 | Damilola Paseda | 2025-11-28 17:34 | 2025-11-28 17:50 | 963 | 2025-11-28 17:34 | 2025-11-28 17:50 | 0:16 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Module | 1 / 1 | MTN NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to failed CSU, CSU was reset | Hybrid synchronization failure due to failed CSU, CSU was reset
NOCINC0006475547 | Internal Reconciliation | Site Down | P4 | IHS_OND_0993A | OD4818 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 21:00 | Iyesioluwa Ola | 2025-11-28 20:54 | 2025-11-28 21:08 | 836 | 2025-11-28 20:52 | 2025-11-28 21:08 | 0:16 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen SMU, frozen SMU was reset
NOCINC0006490405 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0921B | EK6303 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-30 23:51 | Maureen Uchehorke | 2025-11-30 23:44 | 2025-12-01 00:32 | 2892 | 2025-11-30 23:44 | 2025-12-01 | 0:16 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | GG crank battery, external battery was used to start the GG
NOCINC0006465238 | External Reconciliation | Site Down | P2 | IHS_WAR_0947B | DL3302 | ASB | Asaba | Delta | 3 - Low | DL0838 | SOUTH SOUTH |  | 2025-11-27 13:52 | Uthman Akinola | 2025-11-27 13:51 | 2025-11-27 14:07 | 960 | 2025-11-27 13:51 | 2025-11-27 14:07 | 0:16 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | Airtel NG, MTN NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 2 | Flat stater battery due to faulty starter module, external battery was used to restore the site (No diesel outage after validation) | Flat stater battery due to faulty starter module, external battery was used to restore the site (No diesel outage after validation)
NOCINC0006473598 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0758A | T3714 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-28 16:14 | Testimony Akinyemi | 2025-11-28 16:14 | 2025-11-28 16:15 | 60 | 2025-11-28 16:14 | 2025-11-28 16:30 | 0:16 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 2 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | weak BUB, GG auto restart
NOCINC0006461185 | External Reconciliation | Site Down | P3 | IHS_ILO_0020B | KW4554 | IBD | Ibadan | Kwara | 3 - Low | KW0563 | WEST |  | 2025-11-26 22:45 | Precious Attah | 2025-11-26 22:44 | 2025-11-26 23:00 | 960 | 2025-11-26 22:44 | 2025-11-26 23:00 | 0:16 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | failed charging alternator was excited
NOCINC0006466935 | External Reconciliation | Site Down | P4 | IHS_OYO_1121C | OY6542 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 18:01 | Sheriff Salami | 2025-11-27 17:57 | 2025-11-27 18:13 | 960 | 2025-11-27 17:57 | 2025-11-27 18:13 | 0:16 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen SMU, SMU was reset.
NOCINC0006474295 | Internal Reconciliation | Site Down | P4 | IHS_OYO_0023B | OY4041 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 17:45 | Praise Okezie | 2025-11-28 17:43 | 2025-11-28 17:59 | 959 | 2025-11-28 17:43 | 2025-11-28 17:59 | 0:16 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start
NOCINC0006464730 | External Reconciliation | Site Down | P4 | IHS_OSU_0822A | T3621 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 12:35 | Oluwatomisin Ogunleye | 2025-11-27 12:33 | 2025-11-27 12:49 | 957 | 2025-11-27 12:33 | 2025-11-27 12:49 | 0:16 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Failed rectifier module was reset
NOCINC0006454209 | External Reconciliation | Site Down | P1 | IHS_BEN_0747E | ED6149 | IBD | Asaba | Edo | 3 - Low | ED0502 | SOUTH SOUTH |  | 2025-11-26 01:02 | Evelyn Emagurehor | 2025-11-26 01:00 | 2025-11-26 01:16 | 956 | 2025-11-26 01:00 | 2025-11-26 01:16 | 0:16 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Ismail Adeyinka |  |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Failed DG charging alternator was excited to restore power to the site. (No diesel outage after validation). | Failed DG charging alternator was excited to restore power to the site. (No diesel outage after validation).
NOCINC0006458638 | External Reconciliation | Site Down | P4 | IHS_OYO_0023B | OY4041 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 15:26 | Oluwatomisin Ogunleye | 2025-11-26 15:24 | 2025-11-26 15:40 | 953 | 2025-11-26 15:24 | 2025-11-26 15:40 | 0:16 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Weak DG was primed to start
NOCINC0006474117 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0001B | OY2931 | IBD | Ibadan | Oyo | 3 - Low | OY0906 | WEST |  | 2025-11-28 17:23 | Damilola Paseda | 2025-11-28 17:22 | 2025-11-28 17:38 | 948 | 2025-11-28 17:22 | 2025-11-28 17:38 | 0:16 | SPS | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 5 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to incomplete phase, DG powered manually. | Grid to DG synchronization failure due to incomplete phase, DG powered manually.
NOCINC0006438554 | External Reconciliation | Site Down | P4 | IHS_ANA_1071A | AN0307 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 08:38 | Abundance Otunola | 2025-11-24 08:32 | 2025-11-24 08:48 | 947 | 2025-11-24 08:32 | 2025-11-24 08:48 | 0:16 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Over Frequency | 2 / 2 | Airtel NG, MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG over frequency, governor was adjusted. (No diesel outage after validation)
NOCINC0006467645 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 20:11 | Muhammed Hashirudeen | 2025-11-27 20:10 | 2025-11-27 20:26 | 942 | 2025-11-27 20:10 | 2025-11-27 20:26 | 0:16 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Hybrid system was reset due to synchronization failure. (No diesel outage after validation) | Hybrid system was reset due to synchronization failure. (No diesel outage after validation)
NOCINC0006466161 | External Reconciliation | Site Down | P3 | IHS_OYO_0813A | T3061 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 15:55 | Mutmainnah Saba | 2025-11-27 15:51 | 2025-11-27 16:07 | 937 | 2025-11-27 15:51 | 2025-11-27 16:07 | 0:16 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | voltage fluctuation due to absence of BUB, GG auto restart
NOCINC0006447161 | External Reconciliation | Site Down | P1 | IHS_DEL_1164A | DL0626 | ASB | Asaba | Delta | 3 - Low | DL0600 | SOUTH SOUTH |  | 2025-11-25 10:54 | Tracy Osarumwense | 2025-11-25 10:54 | 2025-11-25 11:09 | 936 | 2025-11-25 10:54 | 2025-11-25 11:09 | 0:16 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Tripped Load Breaker was enabled. | Tripped Load Breaker was enabled. (No diesel outage after validation).
NOCINC0006482186 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-29 18:43 | Valentine Adinnu | 2025-11-29 18:42 | 2025-11-29 18:58 | 935 | 2025-11-29 18:42 | 2025-11-29 18:58 | 0:16 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 2 | MTN NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid -DG synchronization failure due to unstable grid supply, DG was powered manually | Grid -DG synchronization failure due to unstable grid supply, DG was powered manually
NOCINC0006455110 | External Reconciliation | Site Down | P3 | IHS_EDO_1245B | ED5509 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 05:33 | Ayomide Akindolie | 2025-11-26 05:33 | 2025-11-26 05:49 | 934 | 2025-11-26 05:33 | 2025-11-26 05:49 | 0:16 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Oil Pump | 1 / 1 | MTN NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Failed oil pump was worked on (No diesel outage after validation)
NOCINC0006450431 | External Reconciliation | Site Down | P2 | IHS_OYO_1020A | OY3854 | IBD | Ibadan | Oyo | 3 - Low | OY1418 | WEST |  | 2025-11-25 17:15 | Hardy Oko | 2025-11-25 17:12 | 2025-11-25 17:28 | 928 | 2025-11-25 17:12 | 2025-11-25 17:28 | 0:15 | Inhouse | 3RD Party Power Failure | Passive | Power Provided By 3RD Party | Power Provided By 3RD Party | 2 / 2 | Airtel NG, MTN NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Power provided by third party IITA
NOCINC0006481927 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0970A | T3827 | IBD | Ibadan | Oyo | 3 - Low | OY1352 | WEST |  | 2025-11-29 17:52 | Aishat Oyedeji | 2025-11-29 17:52 | 2025-11-29 18:07 | 925 | 2025-11-29 17:52 | 2025-11-29 18:07 | 0:15 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Delay in hybrid synchronization, DG auto-restored | Delay in hybrid synchronization, DG auto-restored
NOCINC0006464092 | External Reconciliation | Site Down | P1 | IHS_OYO_0902A | T3865 | IBD | Ibadan | Oyo | 3 - Low | OY0963 | WEST |  | 2025-11-27 11:27 | Sheriff Salami | 2025-11-27 11:24 | 2025-11-27 11:39 | 923 | 2025-11-27 11:24 | 2025-11-27 11:39 | 0:15 | Inhouse | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 2 / 2 | Airtel NG, MTN NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 3 | RMS Snag Clearance was carried out on site with Access REF: IHSREF/25112619132567557214
NOCINC0006442673 | External Reconciliation | Site Down | P4 | IHS_IBA_0068B | OY4011 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 17:56 | Aishat Oyedeji | 2025-11-24 17:56 | 2025-11-24 18:11 | 922 | 2025-11-24 17:56 | 2025-11-24 18:11 | 0:15 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Lukman Mohammed | Habeeb Adepoju |  | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Voltage fluctuation due to weak BUB, GG auto-restarted. | Voltage fluctuation due to weak BUB, GG auto-restarted.
NOCINC0006463623 | External Reconciliation | Site Down | P3 | IHS_ANA_1132A | AN0750 | ASB | Asaba | Anambra | 3 - Low | AN0754 | SOUTH EAST |  | 2025-11-27 10:14 | Gbemisola Adedeji | 2025-11-27 10:12 | 2025-11-27 10:27 | 922 | 2025-11-27 10:12 | 2025-11-27 10:27 | 0:15 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | Madu Modestus | Madu Modestus | Madu Modestus | Fady Safwat | Aliyu Garuba |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Low oil pressure, oil was added (No diesel outage after validation). | Low oil pressure, oil was added (No diesel outage after validation).
NOCINC0006460241 | External Reconciliation | Site Down | P1 | IHS_OSU_0793A | T3039 | IBD | Ibadan | Osun | 3 - Low | OS0834 | WEST |  | 2025-11-26 20:04 | Marvellous Emecheta | 2025-11-26 20:01 | 2025-11-26 20:16 | 920 | 2025-11-26 20:01 | 2025-11-26 20:16 | 0:15 | IPT | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Grid DG synchronisation delay due to unstable grid supply, DG was powered manually.
NOCINC0006449134 | External Reconciliation | Site Down | P1 | IHS_DEL_0854A | T2730 | ASB | Asaba | Delta | 3 - Low | - | - | gNodeB Out of Service@2025-11-25 14:14:50@N2730 | 2025-11-25 14:35 | System Administrator | 2025-11-25 14:15 | 2025-11-25 14:30 | 918 | 2025-11-25 14:15 | 2025-11-25 14:30 | 0:15 | Tyllium NGA | Equipment Repair | Passive | Control Panel | ATS Relay Faulty | 1 / 2 | MTN NG |  | Gabriel Akhamiogu |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Delay in hybrid synchronisation due to faulty ATS relay
NOCINC0006463741 | External Reconciliation | Site Down | P1 | IHS_OYO_1186H | OY4460 | IBD | Ibadan | Oyo | 3 - Low | OY0767 | WEST | Cascaded Incident from TTO6748389 - Cascade Removed From TTO6748389 | 2025-11-27 10:35 | Titus Tosin | 2025-11-27 10:32 | 2025-11-27 10:47 | 916 | 2025-11-27 10:32 | 2025-11-27 10:47 | 0:15 | SPS | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | PPM (Generator servicing ) was carried out on site with Ihsref/2511141159563352604
NOCINC0006474158 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1020A | OY3854 | IBD | Ibadan | Oyo | 3 - Low | OY1418 | WEST |  | 2025-11-28 17:28 | Valentine Adinnu | 2025-11-28 17:24 | 2025-11-28 17:39 | 916 | 2025-11-28 17:24 | 2025-11-28 17:39 | 0:15 | Inhouse | 3RD Party Power Failure | Passive | Power Provided By 3RD Party | Power Provided By 3RD Party | 2 / 2 | Airtel NG, MTN NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Power provided by 3rd party, power restored at IITA | Power provided by 3rd party, power restored at IITA
NOCINC0006445964 | External Reconciliation | Site Down | P2 | IHS_OYO_1020A | OY3854 | IBD | Ibadan | Oyo | 3 - Low | OY1418 | WEST |  | 2025-11-25 08:23 | Hardy Oko | 2025-11-25 08:19 | 2025-11-25 08:34 | 911 | 2025-11-25 08:19 | 2025-11-25 08:34 | 0:15 | Inhouse | 3RD Party Power Failure | Passive | Power Provided By 3RD Party | Power Provided By 3RD Party | 2 / 2 | MTN NG, Airtel NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | 3rd party power failure. Power was provided by 3rd party (IITA)
NOCINC0006449075 | External Reconciliation | Site Down | P3 | IHS_EDO_0978A | ED2153 | IBD | Asaba | Edo | 3 - Low | ED0709 | SOUTH SOUTH |  | 2025-11-25 14:31 | Emmanuel Faleti | 2025-11-25 14:31 | 2025-11-25 14:46 | 907 | 2025-11-25 14:31 | 2025-11-25 14:46 | 0:15 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 2 / 2 | MTN NG, Airtel NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 2 | Faulty temperature sensor switch was worked on (No diesel outage after validation) | Faulty temperature sensor switch was worked on (No diesel outage after validation)
NOCINC0006486634 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1020A | OY3854 | IBD | Ibadan | Oyo | 3 - Low | OY1418 | WEST |  | 2025-11-30 12:24 | Hardy Oko | 2025-11-30 12:13 | 2025-11-30 12:28 | 906 | 2025-11-30 12:13 | 2025-11-30 12:28 | 0:15 | Inhouse | 3RD Party Power Failure | Passive | Power Provided By 3RD Party | Power Provided By 3RD Party | 2 / 2 | MTN NG, Airtel NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | 3rd party power failure. Power was provided by 3rd party(IITA)
NOCINC0006441394 | External Reconciliation | Site Down | P1 | IHS_OYO_0857A | T3581 | IBD | Ibadan | Oyo | 3 - Low | OY1146 | WEST |  | 2025-11-24 15:21 | Victor Otugo | 2025-11-24 15:14 | 2025-11-24 15:29 | 903 | 2025-11-24 15:14 | 2025-11-24 15:29 | 0:15 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - High Engine Temp - Clogged Radiator | 1 / 2 | MTN NG |  | Azeez Salami | Samuel Olaobaju |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 12 | GG high temperature due to low coolant level, coolant was added. | GG high temperature due to low coolant level, coolant was added.
NOCINC0006488386 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1393H | AN0065 | ASB | Asaba | Anambra | 3 - Low | AN0312 | SOUTH EAST |  | 2025-11-30 16:44 | Aderonke Olowojoba | 2025-11-30 16:40 | 2025-11-30 16:55 | 900 | 2025-11-30 16:40 | 2025-11-30 16:55 | 0:15 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted(No diesel outage after validation) | Low DG frequency, Governor was adjusted(No diesel outage after validation)
NOCINC0006439462 | External Reconciliation | Site Down | P2 | IHS_EDO_0976A | ED2148 | IBD | Asaba | Edo | 3 - Low | ED0659 | SOUTH SOUTH |  | 2025-11-24 11:12 | Oluwatomisin Sogbesan | 2025-11-24 11:09 | 2025-11-24 11:24 | 900 | 2025-11-24 11:09 | 2025-11-24 11:24 | 0:15 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Hammed Abubakar |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation) | Low DG frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006463782 | External Reconciliation | Site Down | P1 | IHS_OYO_1174H | OY2820 | IBD | Ibadan | Oyo | 3 - Low | OY0083 | WEST |  | 2025-11-27 10:42 | Bosede Kutelu | 2025-11-27 10:42 | 2025-11-27 10:57 | 896 | 2025-11-27 10:42 | 2025-11-27 10:57 | 0:15 | SPS | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | PPM (geneartor servicing) was carried out ref IHSREF/25111412001858311778
NOCINC0006445817 | External Reconciliation | Site Down | P4 | IHS_EDO_1016A | ED2166 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 07:35 | Azeezat Badmus | 2025-11-25 07:31 | 2025-11-25 07:46 | 896 | 2025-11-25 07:31 | 2025-11-25 07:46 | 0:15 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Mike Imomoh | Mike Imomoh | Mike Imomoh | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | PPM was completed at site (No diesel outage after validation)
NOCINC0006476052 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1020A | OY3854 | IBD | Ibadan | Oyo | 3 - Low | OY1418 | WEST |  | 2025-11-28 22:16 | Sheriff Salami | 2025-11-28 22:13 | 2025-11-28 22:28 | 894 | 2025-11-28 22:13 | 2025-11-28 22:28 | 0:15 | Inhouse | 3RD Party Power Failure | Passive | Power Provided By 3RD Party | Power Provided By 3RD Party | 2 / 2 | MTN NG, Airtel NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | 3rd party power failure. Power was provided by 3rd party(IITA)
NOCINC0006446648 | External Reconciliation | Site Down | P2 | IHS_EDO_1222B | ED6223 | IBD | Asaba | Edo | 3 - Low | ED0732 | SOUTH SOUTH |  | 2025-11-25 09:38 | Oluwatomisin Sogbesan | 2025-11-25 09:38 | 2025-11-25 09:53 | 892 | 2025-11-25 09:38 | 2025-11-25 09:53 | 0:15 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | Airtel NG, MTN NG |  | Asukwo Effiong | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on. (No diesel outage after validation) | Faulty fuel pump was worked on. (No diesel outage after validation)
NOCINC0006489600 | Internal Reconciliation | Site Down | P1 | IHS_OND_0853A | T3443 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 20:38 | Maureen Uchehorke | 2025-11-30 20:36 | 2025-11-30 20:51 | 889 | 2025-11-30 20:36 | 2025-11-30 20:51 | 0:15 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Failed Rectifier Module was Reset
NOCINC0006476596 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 00:55 | Akachukwu Ugwu | 2025-11-29 00:52 | 2025-11-29 01:07 | 889 | 2025-11-29 00:52 | 2025-11-29 01:07 | 0:15 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under voltage alarm AVR adjusted (No diesel outage after validation). | DG under voltage alarm AVR adjusted (No diesel outage after validation).
NOCINC0006463167 | External Reconciliation | Site Down | P3 | IHS_KWA_0756A | T3118 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 08:48 | Titus Tosin | 2025-11-27 08:47 | 2025-11-27 09:02 | 887 | 2025-11-27 08:47 | 2025-11-27 09:02 | 0:15 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | PPM (Generator servicing ) was carried out on site
NOCINC0006443671 | External Reconciliation | Site Down | P4 | IHS_OND_1006A | OD2578 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-24 20:31 | Maureen Uchehorke | 2025-11-24 20:27 | 2025-11-24 20:42 | 887 | 2025-11-24 20:27 | 2025-11-24 20:42 | 0:15 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Benjamin Onwu |  |  | Ibrahim Akinpelu | Benjamin Onwu |  | Victor Adeoye | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG underfrequency alarm was cleared
NOCINC0006445821 | External Reconciliation | Site Down | P1 | IHS_DEL_0796A | T2635 | ASB | Asaba | Delta | 3 - Low | DL0985 | SOUTH SOUTH |  | 2025-11-25 07:36 | Solomon Bankole | 2025-11-25 07:34 | 2025-11-25 07:49 | 884 | 2025-11-25 07:34 | 2025-11-25 07:49 | 0:15 | Tyllium NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 3 | Airtel NG |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | PPM was carried out on site | PPM was carried out on site
NOCINC0006456744 | External Reconciliation | Site Down | P3 | IHS_KWA_0938C | KW4662 | IBD | Ibadan | Kwara | 3 - Low | KW0422 | WEST |  | 2025-11-26 10:56 | Titus Tosin | 2025-11-26 10:56 | 2025-11-26 11:11 | 884 | 2025-11-26 10:56 | 2025-11-26 11:11 | 0:15 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Generator serving PPM completed at site
NOCINC0006439876 | External Reconciliation | Site Down | P3 | IHS_OSU_0799A | T3037 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 12:46 | Oluwatomisin Ogunleye | 2025-11-24 12:45 | 2025-11-24 13:00 | 883 | 2025-11-24 12:45 | 2025-11-24 13:00 | 0:15 | IPT | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Odufu Friday |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify | 1 | PPM (Generator servicing) was completed at site
NOCINC0006460167 | External Reconciliation | Site Down | P3 | IHS_DEL_0896A | T2777 | ASB | Asaba | Delta | 3 - Low | DL0250 | SOUTH SOUTH | Cascaded Incident from TTO6744417 - Cascade Removed From TTO6744417 | 2025-11-26 19:48 | Patrick Okoro | 2025-11-26 19:47 | 2025-11-26 20:02 | 880 | 2025-11-26 19:47 | 2025-11-26 20:02 | 0:15 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Low oil pressure, oil was added to power the site (No diesel outage after validation) | Low oil pressure, oil was added to power the site (No diesel outage after validation)
NOCINC0006444473 | External Reconciliation | Site Down | P3 | IHS_OSU_0869A | T3670 | IBD | Ibadan | Osun | 3 - Low | OS0668 | WEST |  | 2025-11-24 22:48 | Valentine Adinnu | 2025-11-24 22:46 | 2025-11-24 23:01 | 879 | 2025-11-24 22:46 | 2025-11-24 23:01 | 0:15 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 2 / 2 | MTN NG, Airtel NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Suspected passive issue, awaiting passive update from FSE | Suspected passive issue, awaiting passive update from FSE
NOCINC0006487993 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0914A | KW4594 | IBD | Ibadan | Kwara | 3 - Low | KW0418 | WEST |  | 2025-11-30 15:40 | Azeezat Adekunle | 2025-11-30 15:40 | 2025-11-30 15:55 | 878 | 2025-11-30 15:40 | 2025-11-30 15:55 | 0:15 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty load breaker was replaced
NOCINC0006477795 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0046B | DL0738 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 08:12 | Mary Odefemi | 2025-11-29 08:10 | 2025-11-29 08:24 | 876 | 2025-11-29 08:10 | 2025-11-29 08:24 | 0:15 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Planned activity - RMS snag clearance with valid ref IHSREF/25112817413594336284
NOCINC0006456303 | External Reconciliation | Site Down | P3 | IHS_ILO_0060C | KW4693 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-26 09:39 | Titus Tosin | 2025-11-26 09:39 | 2025-11-26 09:54 | 875 | 2025-11-26 09:39 | 2025-11-26 09:54 | 0:15 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Olapade Babatunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled.
NOCINC0006479702 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1020A | OY3854 | IBD | Ibadan | Oyo | 3 - Low | OY1418 | WEST |  | 2025-11-29 12:45 | Valentine Adinnu | 2025-11-29 12:42 | 2025-11-29 12:56 | 871 | 2025-11-29 12:42 | 2025-11-29 12:56 | 0:15 | Inhouse | 3RD Party Power Failure | Passive | Power Provided By 3RD Party | Power Provided By 3RD Party | 2 / 2 | Airtel NG, MTN NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Power provided by 3rd party, power restored at IITA | Power provided by 3rd party, power restored at IITA
NOCINC0006473556 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 16:07 | Muhammed Hashirudeen | 2025-11-28 16:06 | 2025-11-28 16:21 | 868 | 2025-11-28 16:06 | 2025-11-28 16:21 | 0:14 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is affected by ED4860. (No diesel outage after validation)
NOCINC0006467720 | External Reconciliation | Site Down | P2 | IHS_OYO_1020A | OY3854 | IBD | Ibadan | Oyo | 3 - Low | OY1418 | WEST |  | 2025-11-27 20:26 | Marvellous Emecheta | 2025-11-27 20:26 | 2025-11-27 20:40 | 867 | 2025-11-27 20:26 | 2025-11-27 20:40 | 0:14 | Inhouse | 3RD Party Power Failure | Passive | Power Provided By 3RD Party | Power Provided By 3RD Party | 2 / 2 | Airtel NG, MTN NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Power provided by third party IITA
NOCINC0006457483 | External Reconciliation | Site Down | P1 | IHS_EDO_0774A | T3210 | IBD | Asaba | Edo | 3 - Low | ED0477 | SOUTH SOUTH |  | 2025-11-26 12:31 | Emmanuel Faleti | 2025-11-26 12:30 | 2025-11-26 12:45 | 867 | 2025-11-26 12:30 | 2025-11-26 12:45 | 0:14 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Hybrid synchronization failure due to degraded BUB. DG powered manually (No diesel outage after validation)
NOCINC0006445631 | External Reconciliation | Site Down | P2 | IHS_EDO_0017B | ED5089 | IBD | Asaba | Edo | 3 - Low | ED0663 | SOUTH SOUTH |  | 2025-11-25 06:54 | Azeezat Badmus | 2025-11-25 06:54 | 2025-11-25 07:08 | 866 | 2025-11-25 06:54 | 2025-11-25 07:08 | 0:14 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006452233 | External Reconciliation | Site Down | P2 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 22:16 | Evelyn Emagurehor | 2025-11-25 22:11 | 2025-11-25 22:25 | 864 | 2025-11-25 22:11 | 2025-11-25 22:25 | 0:14 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site is powered from ED4860. (No diesel outage after validation). | Site is powered from ED4860. (No diesel outage after validation).
NOCINC0006488165 | Internal Reconciliation | Site Down | P1 | IHS_OND_0831A | T3963 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 16:08 | Yewande Adeagbo | 2025-11-30 16:07 | 2025-11-30 16:21 | 864 | 2025-11-30 16:07 | 2025-11-30 16:21 | 0:14 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 13 | Start failure alarm was cleared and GG was restarted.
NOCINC0006452062 | External Reconciliation | Site Down | P4 | IHS_OSU_0875A | OS3995 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 21:35 | Azeezat Adekunle | 2025-11-25 21:31 | 2025-11-25 21:45 | 863 | 2025-11-25 21:31 | 2025-11-25 21:45 | 0:14 | IPT | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure, DG was Powered manually
NOCINC0006489003 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0865A | T3680 | IBD | Ibadan | Osun | 3 - Low | OS0949 | WEST |  | 2025-11-30 18:22 | Aishat Oyedeji | 2025-11-30 18:22 | 2025-11-30 18:36 | 863 | 2025-11-30 18:22 | 2025-11-30 18:36 | 0:14 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 2 | MTN NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset
NOCINC0006482112 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0774A | T3210 | IBD | Asaba | Edo | 3 - Low | ED0477 | SOUTH SOUTH |  | 2025-11-29 18:29 | Azeezat Badmus | 2025-11-29 18:29 | 2025-11-29 18:43 | 862 | 2025-11-29 18:29 | 2025-11-29 18:43 | 0:14 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Hybrid synchronization failure due to degraded BUB. DG powered automatically (No diesel ouatge after validation) | Hybrid synchronization failure due to degraded BUB. DG powered automatically (No diesel ouatge after validation)
NOCINC0006489976 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0729A | T3049 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-30 21:54 | Maureen Uchehorke | 2025-11-30 21:52 | 2025-11-30 22:06 | 860 | 2025-11-30 21:52 | 2025-11-30 22:06 | 0:14 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 5 | voltage fluctuation due to weak BUB, GG auto restart
NOCINC0006467810 | External Reconciliation | Site Down | P1 | IHS_EDO_0774A | T3210 | IBD | Asaba | Edo | 3 - Low | ED0477 | SOUTH SOUTH |  | 2025-11-27 20:40 | Emmanuel Faleti | 2025-11-27 20:40 | 2025-11-27 20:54 | 859 | 2025-11-27 20:40 | 2025-11-27 20:54 | 0:14 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 7 | Hybrid synchronization failure due to start fail alarm. RES: Alarm was cleared, and Gen powered manually to restore the site. (No diesel outage after validation) | Hybrid synchronization failure due to start fail alarm. RES: Alarm was cleared, and Gen powered manually to restore the site. (No diesel outage after validation)
NOCINC0006456685 | External Reconciliation | Site Down | P1 | IHS_EDO_0778A | T3246 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 10:45 | Azeezat Badmus | 2025-11-26 10:43 | 2025-11-26 10:58 | 857 | 2025-11-26 10:43 | 2025-11-26 10:58 | 0:14 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | PPM was completed at site (No diesel outage after validation)
NOCINC0006489130 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0865A | T3680 | IBD | Ibadan | Osun | 3 - Low | OS0949 | WEST |  | 2025-11-30 18:49 | Aishat Oyedeji | 2025-11-30 18:48 | 2025-11-30 19:02 | 857 | 2025-11-30 18:48 | 2025-11-30 19:02 | 0:14 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 2 | MTN NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset
NOCINC0006476787 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 02:34 | Akachukwu Ugwu | 2025-11-29 02:30 | 2025-11-29 02:44 | 854 | 2025-11-29 02:30 | 2025-11-29 02:44 | 0:14 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under frequency alarm Governor adjusted (No diesel outage after validation). | DG under frequency alarm Governor adjusted (No diesel outage after validation).
NOCINC0006478392 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0046B | DL0738 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 09:53 | Quadri Ogundare | 2025-11-29 09:26 | 2025-11-29 09:40 | 852 | 2025-11-29 09:26 | 2025-11-29 09:40 | 0:14 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Planned activity - RMS snag clearance with valid ref IHSREF/25112817413594336284
NOCINC0006476436 | Internal Reconciliation | Site Down | P3 | IHS_EKI_0018B | EK4403 | IBD | Ibadan | Ekiti | 3 - Low | EK0484 | WEST |  | 2025-11-29 | Iyesioluwa Ola | 2025-11-29 | 2025-11-29 00:14 | 850 | 2025-11-29 | 2025-11-29 00:14 | 0:14 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Battery | 2 / 2 | MTN NG, Airtel NG |  | Ajao Oyekunle |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | weak crank battery. external battery was used to power DG
NOCINC0006483943 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0774A | T3210 | IBD | Asaba | Edo | 3 - Low | ED0477 | SOUTH SOUTH |  | 2025-11-30 00:19 | Muhammed Hashirudeen | 2025-11-30 00:18 | 2025-11-30 00:32 | 849 | 2025-11-30 00:18 | 2025-11-30 00:32 | 0:14 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 11 | Hybrid synchronization failure due to degraded BUB. DG powered automatically (No diesel ouatge after validation)
NOCINC0006446917 | External Reconciliation | Site Down | P1 | IHS_DEL_1107A | DL0092 | ASB | Asaba | Delta | 3 - Low | DL0660 | SOUTH SOUTH |  | 2025-11-25 10:13 | Tracy Osarumwense | 2025-11-25 10:13 | 2025-11-25 10:27 | 849 | 2025-11-25 10:13 | 2025-11-25 10:27 | 0:14 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | Babatunde Jimoh� |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Low Oil Pressure, Oil was added. | Low Oil Pressure, Oil was added. (No diesel outage after validation).
NOCINC0006483005 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0729A | T3049 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 21:15 | Abisoye Olaleye | 2025-11-29 21:13 | 2025-11-29 21:27 | 846 | 2025-11-29 21:13 | 2025-11-29 21:27 | 0:14 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 6 | voltage fluctuation due to weak BUB, GG auto restart
NOCINC0006449858 | External Reconciliation | Site Down | P2 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 16:11 | Emmanuel Faleti | 2025-11-25 16:11 | 2025-11-25 16:25 | 845 | 2025-11-25 16:11 | 2025-11-25 16:25 | 0:14 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is affected by ED4860. (No diesel outage after validation) | POFC: Site is affected by ED4860. (No diesel outage after validation)
NOCINC0006470336 | External Reconciliation | Site Down | P4 | IHS_KWA_0751A | T3135 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 07:42 | Osarieme Charles | 2025-11-28 07:38 | 2025-11-28 07:52 | 842 | 2025-11-28 07:38 | 2025-11-28 07:52 | 0:14 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Seun Tunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive issue at site awaiting RCA from FSE
NOCINC0006490232 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0801A | T0092 | IBD | Ibadan | Oyo | 3 - Low | OY1694 | WEST |  | 2025-11-30 22:49 | Damilola Paseda | 2025-11-30 22:48 | 2025-11-30 23:02 | 842 | 2025-11-30 22:48 | 2025-11-30 23:02 | 0:14 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 2 | MTN NG |  | Lukman Mohammed | Isah Ahmed |  | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 4 | Voltage fluctuation due to high load on GG, GG auto-restarted | Voltage fluctuation due to high load on GG, GG auto-restarted
NOCINC0006478149 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1000A | DL0101 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 09:20 | Ayokunle Samuel | 2025-11-29 09:17 | 2025-11-29 09:31 | 841 | 2025-11-29 09:17 | 2025-11-29 09:31 | 0:14 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 1 / 1 | MTN NG |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed charging alternator was excited to restore. (No diesel outage after validation) | Failed charging alternator was excited to restore. (No diesel outage after validation)
NOCINC0006461970 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-27 02:11 | Aderonke Olowojoba | 2025-11-27 02:07 | 2025-11-27 02:21 | 840 | 2025-11-27 02:07 | 2025-11-27 02:21 | 0:14 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation)
NOCINC0006482311 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0844A | EK2229 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 19:06 | Zainab Bello | 2025-11-29 19:06 | 2025-11-29 19:20 | 840 | 2025-11-29 19:06 | 2025-11-29 19:20 | 0:14 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Hybrid Synchronisation failure due to over voltage discharge alarm
NOCINC0006477373 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 06:17 | Akachukwu Ugwu | 2025-11-29 06:13 | 2025-11-29 06:27 | 840 | 2025-11-29 06:13 | 2025-11-29 06:27 | 0:14 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under voltage alarm. AVR adjusted (No diesel outage after validation). | DG under voltage alarm. AVR adjusted (No diesel outage after validation).
NOCINC0006482072 | Internal Reconciliation | Site Down | P1 | IHS_IBA_0107C | OY4031 | IBD | Ibadan | Oyo | 3 - Low | OY1005 | WEST |  | 2025-11-29 18:21 | Maureen Idoko | 2025-11-29 18:20 | 2025-11-29 18:34 | 838 | 2025-11-29 18:20 | 2025-11-29 18:34 | 0:14 | Biswal | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out on site with IHSREF/25110413472912507222 | PPM (Generator servicing) was carried out on site with IHSREF/25110413472912507222
NOCINC0006476785 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0729A | T3049 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 02:34 | Iyesioluwa Ola | 2025-11-29 02:33 | 2025-11-29 02:47 | 837 | 2025-11-29 02:33 | 2025-11-29 02:47 | 0:14 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 5 | Voltage fluctuation due to weak BUB, GG auto restart
NOCINC0006456562 | External Reconciliation | Site Down | P1 | IHS_OYO_0001B | OY2931 | IBD | Ibadan | Oyo | 3 - Low | OY0906 | WEST |  | 2025-11-26 10:23 | Ifechi Ugwueze | 2025-11-26 10:23 | 2025-11-26 10:37 | 836 | 2025-11-26 10:23 | 2025-11-26 10:37 | 0:14 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 5 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Failed Charging Alternator was Excited
NOCINC0006473430 | Internal Reconciliation | Site Down | P1 | IHS_OSU_1048B | OS4766 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 15:49 | Valentine Adinnu | 2025-11-28 15:48 | 2025-11-28 16:01 | 834 | 2025-11-28 15:48 | 2025-11-28 16:01 | 0:14 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - Low Oil Pressure | 1 / 1 | MTN NG |  | Odufu Friday |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Low oil pressure, oil was added | Low oil pressure, oil was added
NOCINC0006451862 | External Reconciliation | Site Down | P2 | IHS_OND_0840A | T3842 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-25 20:57 | Ihuoma Opurum | 2025-11-25 20:57 | 2025-11-25 21:11 | 834 | 2025-11-25 20:57 | 2025-11-25 21:11 | 0:14 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Anawanti Kingsley |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Weak crank battery. An external battery was used to power the site.
NOCINC0006441903 | External Reconciliation | Site Down | P1 | IHS_EDO_0774A | T3210 | IBD | Asaba | Edo | 3 - Low | ED0477 | SOUTH SOUTH |  | 2025-11-24 16:30 | Evelyn Emagurehor | 2025-11-24 16:29 | 2025-11-24 16:43 | 834 | 2025-11-24 16:29 | 2025-11-24 16:43 | 0:14 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Hybrid synchronization failure due to degraded BUB. DG powered manually with external battery (No diesel outage after validation) | Hybrid synchronization failure due to degraded BUB. DG powered manually with external battery (No diesel outage after validation)
NOCINC0006467486 | External Reconciliation | Site Down | P4 | IHS_KWA_0985H | KW4726 | IBD | Ibadan | Kwara | 3 - Low | KW0557 | West |  | 2025-11-27 19:44 | Titus Tosin | 2025-11-27 19:44 | 2025-11-27 19:58 | 834 | 2025-11-27 19:44 | 2025-11-27 19:58 | 0:14 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | Airtel NG, MTN NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Grid-DG Synchronization Failure due to unstable grid supply, DG was powered manually | Grid-DG Synchronization Failure due to unstable grid supply, DG was powered manually
NOCINC0006471885 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 11:41 | Azeezat Badmus | 2025-11-28 11:41 | 2025-11-28 11:55 | 832 | 2025-11-28 11:41 | 2025-11-28 11:55 | 0:14 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Suspected passive fault, awaiting update from FSE
NOCINC0006457681 | External Reconciliation | Site Down | P2 | IHS_KWA_1016B | KW6415 | IBD | Ibadan | Kwara | 3 - Low | KW0512 | WEST |  | 2025-11-26 12:54 | Titus Tosin | 2025-11-26 12:53 | 2025-11-26 13:06 | 832 | 2025-11-26 12:53 | 2025-11-26 13:06 | 0:14 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was completed at site
NOCINC0006462591 | External Reconciliation | Site Down | P1 | IHS_EDO_0774A | T3210 | IBD | Asaba | Edo | 3 - Low | ED0477 | SOUTH SOUTH |  | 2025-11-27 06:24 | Oluwatomisin Sogbesan | 2025-11-27 06:22 | 2025-11-27 06:35 | 830 | 2025-11-27 06:22 | 2025-11-27 06:35 | 0:14 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Hybrid Synchronisation Failure due to degraded BUB. DG powered manually (No diesel outage after validation) | Hybrid Synchronisation Failure due to degraded BUB. DG powered manually (No diesel outage after validation)
NOCINC0006473106 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0801A | T3116 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 14:59 | Praise Okezie | 2025-11-28 14:56 | 2025-11-28 15:10 | 828 | 2025-11-28 14:56 | 2025-11-28 15:10 | 0:14 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | tripped load breaker was enabled
NOCINC0006471988 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0030B | OY4291 | IBD | Ibadan | Oyo | 3 - Low | OY1356 | WEST |  | 2025-11-28 11:59 | Praise Okezie | 2025-11-28 11:58 | 2025-11-28 12:12 | 825 | 2025-11-28 11:58 | 2025-11-28 12:12 | 0:14 | SPS | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | PPM done (Generator servicing) with Access Ref Ihsref/25112709360409109962
NOCINC0006480308 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1190A | DL0432 | ASB | Asaba | Delta | 3 - Low | DL0565 | SOUTH SOUTH | Site Abis control link broken@2025-11-29 13:38:57@DL0565 | 2025-11-29 13:56 | System Administrator | 2025-11-29 13:39 | 2025-11-29 13:53 | 824 | 2025-11-29 13:39 | 2025-11-29 13:53 | 0:14 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006456850 | External Reconciliation | Site Down | P2 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 11:15 | Emmanuel Faleti | 2025-11-26 11:15 | 2025-11-26 11:29 | 823 | 2025-11-26 11:15 | 2025-11-26 11:29 | 0:14 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is powered from ED4860. (No diesel outage after validation)
NOCINC0006472561 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 13:35 | Muhammed Hashirudeen | 2025-11-28 13:34 | 2025-11-28 13:48 | 823 | 2025-11-28 13:34 | 2025-11-28 13:48 | 0:14 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is affected by ED4860. (No diesel outage after validation)
NOCINC0006473607 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0911A | T2775 | ASB | Asaba | Delta | 3 - Low | DL0560 | SOUTH SOUTH |  | 2025-11-28 16:16 | Quadri Ogundare | 2025-11-28 16:15 | 2025-11-28 16:28 | 819 | 2025-11-28 16:15 | 2025-11-28 16:28 | 0:14 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 2 / 2 | Airtel NG, MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Faulty water pump was replaced
NOCINC0006448556 | External Reconciliation | Site Down | P4 | IHS_EDO_1045C | ED6119 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 13:30 | Emmanuel Faleti | 2025-11-25 13:29 | 2025-11-25 13:43 | 815 | 2025-11-25 13:29 | 2025-11-25 13:43 | 0:14 | MPI NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Lift Pump | 1 / 1 | MTN NG |  | Kazeem Ajiboye |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty hand primer was serviced to restore power on site (No diesel outage after validation) | Faulty hand primer was serviced to restore power on site (No diesel outage after validation)
NOCINC0006489145 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0774A | T3210 | IBD | Asaba | Edo | 3 - Low | ED0477 | SOUTH SOUTH |  | 2025-11-30 18:55 | Evelyn Emagurehor | 2025-11-30 18:55 | 2025-11-30 19:09 | 815 | 2025-11-30 18:55 | 2025-11-30 19:09 | 0:14 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Hybrid synchronization failure due to degraded BUB. DG powered manually (No diesel outage after validation) | Hybrid synchronization failure due to degraded BUB. DG powered manually
NOCINC0006442567 | External Reconciliation | Site Down | P3 | IHS_EDO_0942A | ED3375 | IBD | Asaba | Edo | 3 - Low | ED0500 | SOUTH SOUTH |  | 2025-11-24 17:38 | Evelyn Emagurehor | 2025-11-24 17:34 | 2025-11-24 17:48 | 812 | 2025-11-24 17:34 | 2025-11-24 17:48 | 0:14 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | SIMON SUNDAY | Francis Udoh |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Failed charging alternator was excited to restore power to the site. (No diesel outage after validation). | Failed charging alternator was excited to restore power to the site. (No diesel outage after validation).
NOCINC0006487824 | Internal Reconciliation | Site Down | P3 | IHS_OYO_0813A | T3061 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 15:15 | Aishat Oyedeji | 2025-11-30 15:13 | 2025-11-30 15:26 | 810 | 2025-11-30 15:13 | 2025-11-30 15:26 | 0:14 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Voltage fluctuation due to no BUB, GG auto-restarted. | Voltage fluctuation due to no BUB, GG auto-restarted.
NOCINC0006446501 | External Reconciliation | Site Down | P2 | IHS_EDO_0819A | T3222 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 09:18 | Emmanuel Faleti | 2025-11-25 09:18 | 2025-11-25 09:31 | 809 | 2025-11-25 09:18 | 2025-11-25 09:31 | 0:13 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Mike Imomoh | Mike Imomoh | Mike Imomoh | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Generator servicing was completed at site. (No diesel outage after validation) | Generator servicing was completed at site. (No diesel outage after validation)
NOCINC0006462188 | External Reconciliation | Site Down | P2 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 04:03 | Oluwatomisin Sogbesan | 2025-11-27 04:03 | 2025-11-27 04:16 | 808 | 2025-11-27 04:03 | 2025-11-27 04:16 | 0:13 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Team confirmed site is affected by ed4860 | Team confirmed site is affected by ed4860
NOCINC0006487119 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1151A | DL0675 | ASB | Asaba | Delta | 3 - Low | DL0761 | SOUTH SOUTH |  | 2025-11-30 13:28 | Ayomide Akindolie | 2025-11-30 13:28 | 2025-11-30 13:41 | 804 | 2025-11-30 13:28 | 2025-11-30 13:41 | 0:13 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Tripped load breaker was re-eneabled (No diesel outage after validation)
NOCINC0006450963 | External Reconciliation | Site Down | P1 | IHS_OYO_0969A | T3006 | IBD | Ibadan | Oyo | 3 - Low | OY1057 | WEST |  | 2025-11-25 18:54 | Victor Otugo | 2025-11-25 18:54 | 2025-11-25 19:07 | 803 | 2025-11-25 18:54 | 2025-11-25 19:07 | 0:13 | SPS | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | Airtel NG, MTN NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty injector pump was worked on
NOCINC0006477196 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 05:16 | Akachukwu Ugwu | 2025-11-29 05:11 | 2025-11-29 05:24 | 802 | 2025-11-29 05:11 | 2025-11-29 05:24 | 0:13 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under voltage alarm AVR adjusted (No diesel outage after validation). | DG under voltage alarm AVR adjusted (No diesel outage after validation).
NOCINC0006464420 | External Reconciliation | Site Down | P2 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 12:03 | Muhammed Hashirudeen | 2025-11-27 12:03 | 2025-11-27 12:16 | 802 | 2025-11-27 12:03 | 2025-11-27 12:16 | 0:13 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site is powered from ED4860
NOCINC0006450816 | External Reconciliation | Site Down | P2 | IHS_OND_0838A | T3930 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-25 18:30 | Fuanekwu Christopher | 2025-11-25 18:12 | 2025-11-25 18:25 | 802 | 2025-11-25 18:12 | 2025-11-25 18:25 | 0:13 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - RPM - Gas Flow | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Freeze gas line was worked on
NOCINC0006449870 | External Reconciliation | Site Down | P1 | IHS_OSU_0969A | OS2662 | IBD | Ibadan | Osun | 3 - Low | OS0685 | WEST |  | 2025-11-25 16:14 | Precious Attah | 2025-11-25 16:13 | 2025-11-25 16:26 | 800 | 2025-11-25 16:13 | 2025-11-25 16:26 | 0:13 | IPT | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | Tobiloba Oladejo |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on
NOCINC0006448171 | External Reconciliation | Site Down | P4 | IHS_KWA_0985H | KW4726 | IBD | Ibadan | Kwara | 3 - Low | KW0557 | West |  | 2025-11-25 12:38 | Oluwatomisin Ogunleye | 2025-11-25 12:38 | 2025-11-25 12:51 | 799 | 2025-11-25 12:38 | 2025-11-25 12:51 | 0:13 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to Unstable Grid Supply Issue, DG powered manually.
NOCINC0006447119 | External Reconciliation | Site Down | P3 | IHS_OYO_0813A | T3061 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 10:46 | Victor Otugo | 2025-11-25 10:46 | 2025-11-25 10:59 | 798 | 2025-11-25 10:46 | 2025-11-25 10:59 | 0:13 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | voltage fluctuation due to no bub at site
NOCINC0006480209 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1020A | ED4941 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 13:46 | Ayomide Akindolie | 2025-11-29 13:45 | 2025-11-29 13:58 | 797 | 2025-11-29 13:45 | 2025-11-29 13:58 | 0:13 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | AZUBUIKE EMEH | Shagba Terkula | Emeh Azubike | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Tripped Load breaker was re-enabled (No diesel outage after validation) | Tripped Load breaker was re-enabled (No diesel outage after validation)
NOCINC0006451872 | External Reconciliation | Site Down | P3 | IHS_OYO_0813A | T3061 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 21:00 | Aishat Oyedeji | 2025-11-25 20:57 | 2025-11-25 21:11 | 797 | 2025-11-25 20:57 | 2025-11-25 21:11 | 0:13 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Voltage fluctuation due to no BUB, GG auto-restarted. | Voltage fluctuation due to no BUB, GG auto-restarted.
NOCINC0006478415 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0046B | DL0738 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 10:00 | Ayomide Akindolie | 2025-11-29 09:57 | 2025-11-29 10:11 | 796 | 2025-11-29 09:57 | 2025-11-29 10:11 | 0:13 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Planned activity - RMS snag clearance with valid ref IHSREF/25112817413594336284
NOCINC0006488483 | Internal Reconciliation | Site Down | P1 | IHS_OND_0831A | T3963 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 17:00 | Yewande Adeagbo | 2025-11-30 16:59 | 2025-11-30 17:12 | 796 | 2025-11-30 16:59 | 2025-11-30 17:12 | 0:13 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 13 | Start failure alarm was cleared and GG was restarted.
NOCINC0006462340 | External Reconciliation | Site Down | P1 | IHS_EKI_0729A | T3049 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-27 05:11 | Oluwadara Bankole | 2025-11-27 05:06 | 2025-11-27 05:19 | 793 | 2025-11-27 05:06 | 2025-11-27 05:19 | 0:13 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 5 | Voltage fluctuation due to weak BUB, GG auto restart | Voltage fluctuation due to weak BUB, GG auto restart
NOCINC0006474049 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-28 17:12 | Kehinde Akinbowale | 2025-11-28 17:09 | 2025-11-28 17:22 | 786 | 2025-11-28 17:09 | 2025-11-28 17:22 | 0:13 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled(No diesel outage after validation) | Tripped load breaker was enabled(No diesel outage after validation)
NOCINC0006474894 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0879H | T2907 | ASB | Asaba | Delta | 3 - Low | DL0635 | SOUTH SOUTH |  | 2025-11-28 19:18 | Bukola Olabanji | 2025-11-28 19:16 | 2025-11-28 19:29 | 786 | 2025-11-28 19:16 | 2025-11-28 19:29 | 0:13 | BJ Bison NGA | Equipment Repair | Passive | Rectifier | Rectifier - Circuit Breaker | 1 / 2 | Airtel NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty rectifier circuit breaker was replaced (No diesel outage after validation)
NOCINC0006488110 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1393H | AN0065 | ASB | Asaba | Anambra | 3 - Low | AN0312 | SOUTH EAST |  | 2025-11-30 16:02 | Aderonke Olowojoba | 2025-11-30 15:57 | 2025-11-30 16:10 | 786 | 2025-11-30 15:57 | 2025-11-30 16:10 | 0:13 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Low DG frequency, Governor was adjusted(No diesel outage after validation) | Low DG frequency, Governor was adjusted(No diesel outage after validation)
NOCINC0006447110 | External Reconciliation | Site Down | P1 | IHS_ANA_1103A | AN0332 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 10:45 | Oluwatoyin Fagite | 2025-11-25 10:39 | 2025-11-25 10:52 | 785 | 2025-11-25 10:39 | 2025-11-25 10:52 | 0:13 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Augustine Okoro | Ademola Adekunle | Ademola Adekunle | Henry Wanogho | Ifeanyi Chukusa |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Low DG frequency, governor was adjusted (No diesel outage after validation)
NOCINC0006477033 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 04:13 | Akachukwu Ugwu | 2025-11-29 04:11 | 2025-11-29 04:24 | 784 | 2025-11-29 04:11 | 2025-11-29 04:24 | 0:13 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | DG under voltage alarm AVR adjusted (No diesel outage after validation). | DG under voltage alarm AVR adjusted (No diesel outage after validation).
NOCINC0006444648 | External Reconciliation | Site Down | P4 | IHS_OYO_1291B | OY1070 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 23:46 | Damilola Paseda | 2025-11-24 23:44 | 2025-11-24 23:57 | 782 | 2025-11-24 23:44 | 2025-11-24 23:57 | 0:13 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Lukman Mohammed | Habeeb Adepoju |  | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Voltage fluctuation due to no BUB, GG auto-restarted. | Voltage fluctuation due to no BUB, GG auto-restarted.
NOCINC0006486950 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1393H | AN0065 | ASB | Asaba | Anambra | 3 - Low | AN0312 | SOUTH EAST |  | 2025-11-30 13:10 | Abundance Otunola | 2025-11-30 13:07 | 2025-11-30 13:20 | 781 | 2025-11-30 13:07 | 2025-11-30 13:20 | 0:13 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Tripped off load breaker was worked on. (No diesel outage after validation) | Tripped off load breaker was worked on. (No diesel outage after validation)
NOCINC0006452006 | External Reconciliation | Site Down | P2 | IHS_OND_0840A | T3842 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-25 21:23 | Ihuoma Opurum | 2025-11-25 21:22 | 2025-11-25 21:35 | 780 | 2025-11-25 21:22 | 2025-11-25 21:35 | 0:13 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Crank Battery Weak/Dead | 1 / 1 | MTN NG |  | Anawanti Kingsley |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Weak crank battery. An external battery was used to power the site.
NOCINC0006478468 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1066A | DL0404 | ASB | Asaba | Delta | 3 - Low | DL0746 | SOUTH SOUTH |  | 2025-11-29 10:09 | Quadri Ogundare | 2025-11-29 10:09 | 2025-11-29 10:22 | 778 | 2025-11-29 10:09 | 2025-11-29 10:22 | 0:13 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled (No diesel outage after validation) | Tripped DG Load breaker was enabled (No diesel outage after validation)
NOCINC0006443970 | External Reconciliation | Site Down | P3 | IHS_EDO_0832A | T3284 | IBD | Asaba | Edo | 3 - Low | ED0845 | SOUTH SOUTH |  | 2025-11-24 21:23 | Azeezat Badmus | 2025-11-24 21:21 | 2025-11-24 21:33 | 774 | 2025-11-24 21:21 | 2025-11-24 21:33 | 0:13 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006439690 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST |  | 2025-11-24 12:07 | Abundance Otunola | 2025-11-24 12:05 | 2025-11-24 12:18 | 773 | 2025-11-24 12:05 | 2025-11-24 12:18 | 0:13 | BJ Bison NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006466654 | External Reconciliation | Site Down | P3 | IHS_EDO_1184H | ED2105 | IBD | Asaba | Edo | 3 - Low | ED0862 | SOUTH SOUTH |  | 2025-11-27 17:12 | Muhammed Hashirudeen | 2025-11-27 17:12 | 2025-11-27 17:25 | 769 | 2025-11-27 17:12 | 2025-11-27 17:25 | 0:13 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed rectifier module was reset (No diesel outage after validation)
NOCINC0006452217 | External Reconciliation | Site Down | P1 | IHS_KWA_0774A | T3128 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 22:12 | Ihuoma Opurum | 2025-11-25 22:11 | 2025-11-25 22:24 | 766 | 2025-11-25 22:11 | 2025-11-25 22:24 | 0:13 | IPT | Grid Supply | Passive | Grid | National Grid - Low Current Supply | 1 / 1 | MTN NG |  | Enorch Dauda |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Grid-DG synchronization failure due to low current supply. DG was powered manually.
NOCINC0006454854 | External Reconciliation | Site Down | P3 | IHS_OYO_0813A | T3061 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 03:37 | Aishat Oyedeji | 2025-11-26 03:37 | 2025-11-26 03:50 | 766 | 2025-11-26 03:37 | 2025-11-26 03:50 | 0:13 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Voltage fluctuation due to no BUB, GG auto-restarted. | Voltage fluctuation due to no BUB, GG auto-restarted.
NOCINC0006456017 | External Reconciliation | Site Down | P2 | IHS_OND_0783A | T3423 | IBD | Ibadan | Ondo | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-26 08:30:56@T3423_IyayuQIdoani | 2025-11-26 08:45 | System Administrator | 2025-11-26 08:31 | 2025-11-26 08:44 | 760 | 2025-11-26 08:31 | 2025-11-26 08:44 | 0:13 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gas Flow | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty gas line was worked on
NOCINC0006447036 | External Reconciliation | Site Down | P1 | IHS_EKI_0729A | T3049 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-25 10:34 | Mary Elaigwu | 2025-11-25 10:34 | 2025-11-25 10:46 | 758 | 2025-11-25 10:34 | 2025-11-25 10:46 | 0:13 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 4 | voltage fluctuation due to weak BUB, GG auto restart
NOCINC0006440571 | External Reconciliation | Site Down | P1 | IHS_OND_0789A | T3408 | IBD | Ibadan | Ondo | 3 - Low | ON0576 | WEST |  | 2025-11-24 13:38 | Yewande Adeagbo | 2025-11-24 13:38 | 2025-11-24 13:50 | 757 | 2025-11-24 13:38 | 2025-11-24 13:50 | 0:13 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | MTN NG, Airtel NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | faulty control failure worked on
NOCINC0006467453 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-27 19:40 | Akachukwu Ugwu | 2025-11-27 19:36 | 2025-11-27 19:49 | 755 | 2025-11-27 19:36 | 2025-11-27 19:49 | 0:13 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Faulty AVR was worked on (No diesel outage after validation) | Faulty AVR was worked on (No diesel outage after validation)
NOCINC0006450060 | External Reconciliation | Site Down | P1 | IHS_EDO_0774A | T3210 | IBD | Asaba | Edo | 3 - Low | ED0477 | SOUTH SOUTH |  | 2025-11-25 16:35 | Emmanuel Faleti | 2025-11-25 16:34 | 2025-11-25 16:47 | 753 | 2025-11-25 16:34 | 2025-11-25 16:47 | 0:13 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Hybrid synchronization failure due to start fail alarm. RES: Alarm was cleared, and Gen powered manually to restore the site. (No diesel outage after validation) | Hybrid synchronization failure due to start fail alarm. RES: Alarm was cleared, and Gen powered manually to restore the site. (No diesel outage after validation)
NOCINC0006443227 | External Reconciliation | Site Down | P2 | IHS_WAR_0928B | DL3323 | ASB | Asaba | Delta | 3 - Low | DL0890 | SOUTH SOUTH |  | 2025-11-24 19:14 | Ayokunle Samuel | 2025-11-24 19:14 | 2025-11-24 19:26 | 752 | 2025-11-24 19:14 | 2025-11-24 19:26 | 0:13 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Contactor | 2 / 2 | MTN NG, Airtel NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Faulty load contactor was worked on ( No diesel outage after validation) | Faulty load contactor was worked on ( No diesel outage after validation)
NOCINC0006489028 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0809A | T2678 | ASB | Asaba | Delta | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-30 17:56:36@T2678_Amai Road Obiaruku | 2025-11-30 18:26 | System Administrator | 2025-11-30 17:57 | 2025-11-30 18:09 | 750 | 2025-11-30 17:57 | 2025-11-30 18:09 | 0:12 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Suspected Passive Issue, Awaiting Update from FSE. | Suspected Passive Issue, Awaiting Update from FSE.
NOCINC0006445914 | External Reconciliation | Site Down | P1 | IHS_EDO_0891A | T3363 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 08:05 | Azeezat Badmus | 2025-11-25 08:04 | 2025-11-25 08:17 | 748 | 2025-11-25 08:04 | 2025-11-25 08:17 | 0:12 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 1 / 1 | MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed Rectifier cabinet was worked on (No diesel outage after validation) | Failed Rectifier cabinet was worked on (No diesel outage after validation)
NOCINC0006459412 | External Reconciliation | Site Down | P4 | IHS_EKI_0874K | EK4417 | IBD | Ibadan | Ekiti | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-26 17:16:00@EK4417_Old Ise RD Emure Ekiti | 2025-11-26 17:30 | System Administrator | 2025-11-26 17:16 | 2025-11-26 17:28 | 745 | 2025-11-26 17:16 | 2025-11-26 17:28 | 0:12 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - RPM - Gas Flow | 1 / 1 | MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | frozen gas line was worked on
NOCINC0006487093 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1020A | OY3854 | IBD | Ibadan | Oyo | 3 - Low | OY1418 | WEST |  | 2025-11-30 13:22 | Favour Ahize | 2025-11-30 13:20 | 2025-11-30 13:32 | 745 | 2025-11-30 13:20 | 2025-11-30 13:32 | 0:12 | Inhouse | 3RD Party Power Failure | Passive | Power Provided By 3RD Party | Power Provided By 3RD Party | 2 / 2 | Airtel NG, MTN NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Power provided by 3rd party, power restored at IITA
NOCINC0006483552 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1442B | AN3470 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 22:35 | Uthman Akinola | 2025-11-29 22:35 | 2025-11-29 22:47 | 742 | 2025-11-29 22:35 | 2025-11-29 22:47 | 0:12 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Delay in hybrid sychronisation, DG powered manually (no diesel outage after validation)
NOCINC0006440073 | External Reconciliation | Site Down | P1 | IHS_OND_0789A | T3408 | IBD | Ibadan | Ondo | 3 - Low | ON0576 | WEST |  | 2025-11-24 13:01 | Yewande Adeagbo | 2025-11-24 13:00 | 2025-11-24 13:13 | 740 | 2025-11-24 13:00 | 2025-11-24 13:13 | 0:12 | Huawei | Grid Supply | Passive | Grid | National Grid - Circuit Breaker | 2 / 2 | MTN NG, Airtel NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | faulty grid circuit breaker was replaced
NOCINC0006466133 | External Reconciliation | Site Down | P1 | IHS_OYO_1111C | OY4445 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 15:49 | Oluwatomisin Ogunleye | 2025-11-27 15:47 | 2025-11-27 15:59 | 739 | 2025-11-27 15:47 | 2025-11-27 15:59 | 0:12 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen SMU, SMU was reset.
NOCINC0006477972 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0046B | DL0738 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 08:48 | Ayomide Akindolie | 2025-11-29 08:48 | 2025-11-29 09:00 | 738 | 2025-11-29 08:48 | 2025-11-29 09:00 | 0:12 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Planned activity - RMS snag clearance with valid ref IHSREF/25112817413594336284
NOCINC0006481965 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0014V | - | - | Asaba | Edo | 3 - Low | ED0016 | SOUTH SOUTH |  | 2025-11-29 17:59 | Azeezat Badmus | 2025-11-29 17:59 | 2025-11-29 18:11 | 737 | 2025-11-29 17:59 | 2025-11-29 18:11 | 0:12 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 1 / 1 | Airtel NG |  | SIMON SUNDAY | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty water pump was worked on (No diesel outage after validation)
NOCINC0006449938 | External Reconciliation | Site Down | P2 | IHS_OYO_0701E | OY4307 | IBD | Ibadan | Oyo | 3 - Low | OY0911 | WEST |  | 2025-11-25 16:26 | Victor Otugo | 2025-11-25 16:25 | 2025-11-25 16:37 | 736 | 2025-11-25 16:25 | 2025-11-25 16:37 | 0:12 | SPS | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | Airtel NG, MTN NG |  | BASHIR ABDULRASAQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Grid-DG synchronization failure due to unstable grid supply issue. DG was powered manually.
NOCINC0006470798 | External Reconciliation | Site Down | P1 | IHS_KWA_0762A | T3130 | IBD | Ibadan | Kwara | 3 - Low | KW0513 | WEST |  | 2025-11-28 09:11 | Okusanya Joseph | 2025-11-28 09:10 | 2025-11-28 09:22 | 735 | 2025-11-28 09:10 | 2025-11-28 09:22 | 0:12 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Afolabi Ganiyyu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 6 | Generator servicing (ppm) was carried out at site
NOCINC0006445352 | External Reconciliation | Site Down | P4 | IHS_OYO_1011A | T3599 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 05:04 | Damilola Paseda | 2025-11-25 05:03 | 2025-11-25 05:15 | 733 | 2025-11-25 05:03 | 2025-11-25 05:15 | 0:12 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Azeez Salami |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Voltage fluctuation due to weak BUB, GG auto-restarted. | Voltage fluctuation due to weak BUB, GG auto-restarted.
NOCINC0006464885 | External Reconciliation | Site Down | P3 | IHS_OSU_0073B | OS4386 | IBD | Ibadan | Osun | 3 - Low | OS0712 | WEST |  | 2025-11-27 12:56 | Okusanya Joseph | 2025-11-27 12:54 | 2025-11-27 13:06 | 733 | 2025-11-27 12:54 | 2025-11-27 13:06 | 0:12 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on
NOCINC0006481333 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1104A | DL0752 | ASB | Asaba | Delta | 3 - Low | DL0704 | SOUTH SOUTH |  | 2025-11-29 16:23 | Ayokunle Samuel | 2025-11-29 16:19 | 2025-11-29 16:31 | 732 | 2025-11-29 16:19 | 2025-11-29 16:31 | 0:12 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | MTN NG, Airtel NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low oil pressure, Oil was topped. (No diesel outage after validation) | Low oil pressure, Oil was topped. (No diesel outage after validation)
NOCINC0006460860 | External Reconciliation | Site Down | P3 | IHS_EDO_0832A | T3284 | IBD | Asaba | Edo | 3 - Low | ED0845 | SOUTH SOUTH |  | 2025-11-26 21:42 | Oluwatomisin Sogbesan | 2025-11-26 21:41 | 2025-11-26 21:53 | 732 | 2025-11-26 21:41 | 2025-11-26 21:53 | 0:12 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | weak DG primed to start (No diesel outage after validation) | weak DG primed to start (No diesel outage after validation)
NOCINC0006475995 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0832A | T3284 | IBD | Asaba | Edo | 3 - Low | ED0845 | SOUTH SOUTH |  | 2025-11-28 22:04 | Elizabeth Apata | 2025-11-28 22:00 | 2025-11-28 22:12 | 732 | 2025-11-28 22:00 | 2025-11-28 22:12 | 0:12 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | weak DG was primed to start (No diesel outage after validation)
NOCINC0006446535 | External Reconciliation | Site Down | P1 | IHS_EDO_0891A | T3363 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 09:24 | Emmanuel Faleti | 2025-11-25 09:23 | 2025-11-25 09:35 | 729 | 2025-11-25 09:23 | 2025-11-25 09:35 | 0:12 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 1 / 1 | MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Failed Rectifier cabinet was worked on. (No diesel outage after validation) | Failed Rectifier cabinet was worked on. (No diesel outage after validation)
NOCINC0006448346 | External Reconciliation | Site Down | P2 | IHS_OYO_0701E | OY4307 | IBD | Ibadan | Oyo | 3 - Low | OY0911 | WEST |  | 2025-11-25 13:01 | Mutmainnah Saba | 2025-11-25 13:00 | 2025-11-25 13:12 | 729 | 2025-11-25 13:00 | 2025-11-25 13:12 | 0:12 | SPS | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | MTN NG, Airtel NG |  | BASHIR ABDULRASAQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Grid-DG Synchronization Failure due to weak BUB,DG auto started
NOCINC0006454844 | External Reconciliation | Site Down | P1 | IHS_DEL_1066A | DL0404 | ASB | Asaba | Delta | 3 - Low | DL0746 | SOUTH SOUTH |  | 2025-11-26 03:29 | Ayomide Akindolie | 2025-11-26 03:29 | 2025-11-26 03:41 | 722 | 2025-11-26 03:29 | 2025-11-26 03:41 | 0:12 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 2 / 2 | Airtel NG, MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006472358 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0909A | T3792 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 13:00 | Muhammed Hashirudeen | 2025-11-28 13:00 | 2025-11-28 13:12 | 721 | 2025-11-28 13:00 | 2025-11-28 13:12 | 0:12 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 2 | Hybrid synchronization failure. DG powered manually (No diesel ouatge after validation)
NOCINC0006451692 | External Reconciliation | Site Down | P3 | IHS_AUC_0003B | ED4850 | IBD | Asaba | Edo | 3 - Low | ED0680 | SOUTH SOUTH |  | 2025-11-25 20:32 | Evelyn Emagurehor | 2025-11-25 20:27 | 2025-11-25 20:39 | 720 | 2025-11-25 20:27 | 2025-11-25 20:39 | 0:12 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 2 | MTN NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation). | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation).
NOCINC0006459327 | External Reconciliation | Site Down | P4 | IHS_OND_0716E | OD6010 | IBD | Ibadan | Ondo | 3 - Low | ON0832 | WEST |  | 2025-11-26 17:17 | Iyesioluwa Ola | 2025-11-26 17:16 | 2025-11-26 17:28 | 720 | 2025-11-26 17:16 | 2025-11-26 17:28 | 0:12 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | Airtel NG |  | Sanusi Idowu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Generator servicing (PPM) was carried out with access ref IHSREF/25112307505132881366
NOCINC0006468239 | External Reconciliation | Site Down | P1 | IHS_OND_0831A | T3963 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-27 21:59 | Mary Elaigwu | 2025-11-27 21:59 | 2025-11-27 22:11 | 720 | 2025-11-27 21:59 | 2025-11-27 22:11 | 0:12 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 26 | Start failure alarm was cleared ...DCGG RESTARTED
NOCINC0006471575 | Internal Reconciliation | Site Down | P3 | IHS_ILO_0031B | KW4580 | IBD | Ibadan | Kwara | 3 - Low | KW0666 | West |  | 2025-11-28 10:59 | Okusanya Joseph | 2025-11-28 10:59 | 2025-11-28 11:11 | 718 | 2025-11-28 10:59 | 2025-11-28 11:11 | 0:12 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Olapade Babatunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Tripped load breaker was enable
NOCINC0006481224 | Internal Reconciliation | Site Down | P1 | IHS_OYO_1037A | OY2967 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 16:08 | Aishat Oyedeji | 2025-11-29 16:07 | 2025-11-29 16:19 | 715 | 2025-11-29 16:07 | 2025-11-29 16:19 | 0:12 | SPS | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 1 / 3 | MTN NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 3 | Grid to DG synchronization failure due to incomplete phase, DG powered manually. | Grid to DG synchronization failure due to incomplete phase, DG powered manually.
NOCINC0006484704 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1449B | AN3476 | ASB | Asaba | Anambra | 3 - Low | AN0744 | SOUTH EAST |  | 2025-11-30 05:28 | Gbemisola Adedeji | 2025-11-30 05:26 | 2025-11-30 05:38 | 708 | 2025-11-30 05:26 | 2025-11-30 05:38 | 0:12 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | DG under frequency, governor was adjusted (No diesel outage after validation) | DG under frequency, governor was adjusted (No diesel outage after validation)
NOCINC0006463277 | External Reconciliation | Site Down | P4 | IHS_EDO_1231B | ED5510 | IBD | Asaba | Edo | 3 - Low | ED1047 | SOUTH SOUTH |  | 2025-11-27 09:13 | Bukola Olabanji | 2025-11-27 09:11 | 2025-11-27 09:23 | 707 | 2025-11-27 09:11 | 2025-11-27 09:23 | 0:12 | MPI NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Delay in hybrid synchronization, DG was auto-powered.
NOCINC0006487174 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0791A | T0184 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 13:30 | Ayokunle Samuel | 2025-11-30 13:27 | 2025-11-30 13:39 | 706 | 2025-11-30 13:27 | 2025-11-30 13:39 | 0:12 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Outage Issue | 1 / 1 | MTN NG |  | Idowu Dare |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Grid synchronization delay, DG powered to restore site. (No diesel outage after validation) | Grid synchronization delay, DG powered to restore site. (No diesel outage after validation)
NOCINC0006466875 | External Reconciliation | Site Down | P2 | IHS_ILO_0722E | KW4707 | IBD | Ibadan | Kwara | 3 - Low | KW0447 | WEST |  | 2025-11-27 17:50 | Samuel Omole | 2025-11-27 17:39 | 2025-11-27 17:51 | 705 | 2025-11-27 17:39 | 2025-11-27 17:51 | 0:12 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | PPM (generator servicing) was done on site
NOCINC0006482685 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1140A | DL0341 | ASB | Asaba | Delta | 3 - Low | DL1187 | SOUTH SOUTH |  | 2025-11-29 20:18 | Solomon Bankole | 2025-11-29 20:16 | 2025-11-29 20:28 | 702 | 2025-11-29 20:16 | 2025-11-29 20:28 | 0:12 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | failed rectifier module was reset
NOCINC0006446008 | External Reconciliation | Site Down | P3 | IHS_EDO_0848A | T3328 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 08:35 | Emmanuel Faleti | 2025-11-25 08:35 | 2025-11-25 08:46 | 701 | 2025-11-25 08:35 | 2025-11-25 08:46 | 0:12 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Mike Imomoh | Mike Imomoh | Mike Imomoh | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Generator servicing was completed at site. (No diesel outage after validation) | Generator servicing was completed at site. (No diesel outage after validation)
NOCINC0006488464 | Internal Reconciliation | Site Down | P1 | IHS_AWK_0016B | AN0088 | ASB | Asaba | Anambra | 3 - Low | AN0662 | SOUTH EAST |  | 2025-11-30 16:57 | Ayokunle Samuel | 2025-11-30 16:55 | 2025-11-30 17:07 | 697 | 2025-11-30 16:55 | 2025-11-30 17:07 | 0:12 | BJ Bison NGA | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Air Intake | 2 / 2 | Airtel NG, MTN NG |  | Egbujor Victor | Hillary Uduak | Hillary Uduak | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Air intake was flushed out. (No diesel outage after validation) | Air intake was flushed out. (No diesel outage after validation)
NOCINC0006463837 | External Reconciliation | Site Down | P1 | IHS_WAR_0875H | T2874 | ASB | Asaba | Delta | 3 - Low | DL0400 | SOUTH SOUTH | NodeB Unavailable@2025-11-27 10:33:53@U2874 | 2025-11-27 10:48 | System Administrator | 2025-11-27 10:34 | 2025-11-27 10:45 | 689 | 2025-11-27 10:34 | 2025-11-27 10:45 | 0:11 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Stanley Odira |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006477564 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1449B | AN3476 | ASB | Asaba | Anambra | 3 - Low | AN0744 | SOUTH EAST |  | 2025-11-29 07:14 | Akachukwu Ugwu | 2025-11-29 07:11 | 2025-11-29 07:23 | 686 | 2025-11-29 07:11 | 2025-11-29 07:23 | 0:11 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation). | Low DG frequency, Governor was adjusted (No diesel outage after validation).
NOCINC0006441535 | External Reconciliation | Site Down | P3 | IHS_EDO_0987A | ED2044 | IBD | Asaba | Edo | 3 - Low | ED0551 | SOUTH SOUTH |  | 2025-11-24 15:42 | Evelyn Emagurehor | 2025-11-24 15:42 | 2025-11-24 15:53 | 681 | 2025-11-24 15:42 | 2025-11-24 15:53 | 0:11 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 2 | Airtel NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak Refurbished DG was primed to start to restore the site. (No diesel outage after validation). | Weak Refurbished DG was primed to start to restore the site. (No diesel outage after validation).
NOCINC0006466137 | External Reconciliation | Site Down | P2 | IHS_OND_0769A | T0910 | IBD | Ibadan | Ondo | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-27 15:36:47@T0910_Ore Quarry | 2025-11-27 15:50 | System Administrator | 2025-11-27 15:37 | 2025-11-27 15:48 | 680 | 2025-11-27 15:37 | 2025-11-27 15:48 | 0:11 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Daniel Akinfenwa |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | start failure alarm was cleared from the module
NOCINC0006467941 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 21:05 | Emmanuel Faleti | 2025-11-27 21:05 | 2025-11-27 21:16 | 676 | 2025-11-27 21:05 | 2025-11-27 21:16 | 0:11 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Hybrid system was reset due to synchronization failure. (No diesel outage after validation) | Hybrid system was reset due to synchronization failure. (No diesel outage after validation)
NOCINC0006456470 | External Reconciliation | Site Down | P1 | IHS_EDO_0996A | ED4860 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 10:09 | Azeezat Badmus | 2025-11-26 10:09 | 2025-11-26 10:20 | 674 | 2025-11-26 10:09 | 2025-11-26 10:20 | 0:11 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006464284 | External Reconciliation | Site Down | P4 | IHS_EDO_1101C | ED6122 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 11:42 | Bukola Olabanji | 2025-11-27 11:41 | 2025-11-27 11:52 | 671 | 2025-11-27 11:41 | 2025-11-27 11:52 | 0:11 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | MTN NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Insufficient Rectifier module, module was added (no diesel outage after validation).
NOCINC0006444073 | External Reconciliation | Site Down | P1 | IHS_EDO_0891A | T3363 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 21:36 | Azeezat Badmus | 2025-11-24 21:34 | 2025-11-24 21:45 | 669 | 2025-11-24 21:34 | 2025-11-24 21:45 | 0:11 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 1 / 1 | MTN NG |  | Oladele Daniel Hammed |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty rectifier cabinet was worked on (No diesel outage after validation)
NOCINC0006480354 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1190A | DL0432 | ASB | Asaba | Delta | 3 - Low | DL0565 | SOUTH SOUTH |  | 2025-11-29 14:02 | Ayomide Akindolie | 2025-11-29 14:00 | 2025-11-29 14:11 | 668 | 2025-11-29 14:00 | 2025-11-29 14:11 | 0:11 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006474496 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0870K | EK4415 | IBD | Ibadan | Ekiti | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-28 18:04:50@ | 2025-11-28 18:17 | System Administrator | 2025-11-28 18:06 | 2025-11-28 18:18 | 667 | 2025-11-28 18:06 | 2025-11-28 18:18 | 0:11 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | voltage fluctuation, GG auto restart
NOCINC0006439221 | External Reconciliation | Site Down | P1 | IHS_EDO_0755A | T0230 | IBD | Asaba | Edo | 3 - Low | ED0450 | SOUTH SOUTH | 4G ZTE Sitedown@2025-11-24 10:10:11@ED0450(50450) | 2025-11-24 10:25 | System Administrator | 2025-11-24 10:10 | 2025-11-24 10:21 | 665 | 2025-11-24 10:10 | 2025-11-24 10:21 | 0:11 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 3 | Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on to restore power to the site. (No diesel outage after validation). | Faulty ATS contactor was worked on to restore power to the site. (No diesel outage after validation).
NOCINC0006466029 | External Reconciliation | Site Down | P4 | IHS_ANA_1087A | AN0315 | ASB | Asaba | Anambra | 3 - Low | AN1131 | SOUTH EAST |  | 2025-11-27 15:37 | Akachukwu Ugwu | 2025-11-27 15:35 | 2025-11-27 15:46 | 665 | 2025-11-27 15:35 | 2025-11-27 15:46 | 0:11 | Tyllium NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG servicing was completed (No diesel outage after validation). | DG servicing was completed (No diesel outage after validation).
NOCINC0006436474 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-23 23:40:36@T2449_Apedegbais | 2025-11-23 23:57 | System Administrator | 2025-11-23 23:46 | 2025-11-24 00:11 | 1473 | 2025-11-24 | 2025-11-24 00:11 | 0:11 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Suspected passive, awaiting update .
NOCINC0006458101 | External Reconciliation | Site Down | P3 | IHS_OYO_0022B | OY4182 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 14:10 | Ifechi Ugwueze | 2025-11-26 14:07 | 2025-11-26 14:18 | 659 | 2025-11-26 14:07 | 2025-11-26 14:18 | 0:11 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | Aramide Kazeem |  | Aramide Kazeem | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify | 1 | Weak DG was primed to start
NOCINC0006440378 | External Reconciliation | Site Down | P4 | IHS_EDO_1240B | ED5542 | IBD | Asaba | Edo | 3 - Low | ED1126 | SOUTH SOUTH |  | 2025-11-24 13:18 | Ayomide Akindolie | 2025-11-24 13:18 | 2025-11-24 13:29 | 659 | 2025-11-24 13:18 | 2025-11-24 13:29 | 0:11 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Jude Audu | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG Under Frequency, Governor was adjusted. | DG Under Frequency, Governor was adjusted.
NOCINC0006459841 | External Reconciliation | Site Down | P1 | IHS_ONT_0007B | AN0684 | ASB | Asaba | Anambra | 3 - Low | AN0435 | SOUTH EAST |  | 2025-11-26 18:50 | Oluwatoyin Fagite | 2025-11-26 18:49 | 2025-11-26 18:59 | 654 | 2025-11-26 18:49 | 2025-11-26 18:59 | 0:11 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Appeal John |  |  | Erik Nwodo | Nwigbo Chijioke |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty load breaker was replaced (No diesel outage after validation). | Faulty load breaker was replaced (No diesel outage after validation).
NOCINC0006448912 | External Reconciliation | Site Down | P4 | IHS_EDO_1066C | ED6132 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 14:01 | Oluwatomisin Sogbesan | 2025-11-25 14:00 | 2025-11-25 14:11 | 652 | 2025-11-25 14:00 | 2025-11-25 14:11 | 0:11 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 1 | MTN NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG underfrequency, governor was adjusted (No diesel outage after validation) | DG underfrequency, governor was adjusted (No diesel outage after validation)
NOCINC0006441212 | External Reconciliation | Site Down | P4 | IHS_EDO_0963A | ED3347 | IBD | Asaba | Edo | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-24 14:48:44@ED3347_Ikweran | 2025-11-24 15:03 | System Administrator | 2025-11-24 14:50 | 2025-11-24 15:01 | 650 | 2025-11-24 14:50 | 2025-11-24 15:01 | 0:11 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Radiator | 1 / 1 | MTN NG |  | Mike Imomoh | Mike Imomoh | Mike Imomoh | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty radiator was replaced to restore power on site (No diesel outage after validation) | Faulty radiator was replaced to restore power on site (No diesel outage after validation)
NOCINC0006439289 | External Reconciliation | Site Down | P3 | IHS_OSU_0816A | T3605 | IBD | Ibadan | Osun | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-24 10:26:45@T3605_OluponaIwo | 2025-11-24 10:39 | System Administrator | 2025-11-24 10:27 | 2025-11-24 10:38 | 650 | 2025-11-24 10:27 | 2025-11-24 10:38 | 0:11 | IPT | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | hybrid synchronization failure due to frozen Orion, Orion was reset
NOCINC0006449750 | External Reconciliation | Site Down | P2 | IHS_ANA_1287C | AN1109 | ASB | Asaba | Anambra | 3 - Low | AN0612 | SOUTH EAST |  | 2025-11-25 15:59 | Ezinne Ubachukwu | 2025-11-25 15:51 | 2025-11-25 16:02 | 647 | 2025-11-25 15:51 | 2025-11-25 16:02 | 0:11 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006456148 | External Reconciliation | Site Down | P4 | IHS_UHO_0001B | ED2170 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 09:12 | Emmanuel Faleti | 2025-11-26 09:12 | 2025-11-26 09:22 | 645 | 2025-11-26 09:12 | 2025-11-26 09:22 | 0:11 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Mike Imomoh | Mike Imomoh | Mike Imomoh | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | PPM was completed at site (No diesel outage after validation)
NOCINC0006446051 | External Reconciliation | Site Down | P1 | IHS_ONT_0021B | AN0403 | ASB | Asaba | Anambra | 3 - Low | AN0619 | SOUTH EAST |  | 2025-11-25 08:45 | Patrick Okoro | 2025-11-25 08:45 | 2025-11-25 08:56 | 643 | 2025-11-25 08:45 | 2025-11-25 08:56 | 0:11 | BJ Bison NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Amadi Fabian | Tijani Haruna | Tijani Haruna | Henry Wanogho | Ifeanyi Chukusa |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | generator servicing was done
NOCINC0006451130 | External Reconciliation | Site Down | P1 | IHS_OSU_0771A | T3080 | IBD | Ibadan | Osun | 3 - Low | OS0968 | WEST | Huawei 3G SiteDown@2025-11-25 18:57:19@U3080B | 2025-11-25 19:15 | System Administrator | 2025-11-25 19:01 | 2025-11-25 19:12 | 641 | 2025-11-25 19:01 | 2025-11-25 19:12 | 0:11 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 1 / 2 | MTN NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | DG-Grid synchronisation failure due to National grid incomplete phase, Dg powered manually
NOCINC0006471621 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0911A | T2775 | ASB | Asaba | Delta | 3 - Low | DL0560 | SOUTH SOUTH |  | 2025-11-28 11:04 | Bukola Olabanji | 2025-11-28 11:04 | 2025-11-28 11:14 | 640 | 2025-11-28 11:04 | 2025-11-28 11:14 | 0:11 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Tripped DG load breaker was enabled (No diesel outage after validation) | Tripped DG load breaker was enabled (No diesel outage after validation)
NOCINC0006478244 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1449B | AN3476 | ASB | Asaba | Anambra | 3 - Low | AN0744 | SOUTH EAST |  | 2025-11-29 09:33 | Kehinde Akinbowale | 2025-11-29 09:29 | 2025-11-29 09:40 | 639 | 2025-11-29 09:29 | 2025-11-29 09:40 | 0:11 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | Airtel NG, MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted(No diesel outage after validation) | Low DG frequency, Governor was adjusted(No diesel outage after validation)
NOCINC0006442876 | External Reconciliation | Site Down | P4 | IHS_ANA_1229A | AN0565 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 18:19 | Aderonke Olowojoba | 2025-11-24 18:11 | 2025-11-24 18:22 | 637 | 2025-11-24 18:11 | 2025-11-24 18:22 | 0:11 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006481084 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0868A | T3324 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 15:48 | Evelyn Emagurehor | 2025-11-29 15:46 | 2025-11-29 15:56 | 637 | 2025-11-29 15:46 | 2025-11-29 15:56 | 0:11 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 1 / 1 | MTN NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 4 | low oil pressure, oil was added (No diesel outage after validation)
NOCINC0006461909 | External Reconciliation | Site Down | P4 | IHS_DEL_1137A | DL0685 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 01:34 | Ezinne Ubachukwu | 2025-11-27 01:30 | 2025-11-27 01:41 | 637 | 2025-11-27 01:30 | 2025-11-27 01:41 | 0:11 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006452698 | External Reconciliation | Site Down | P1 | IHS_EDO_0811A | T3209 | IBD | Asaba | Edo | 3 - Low | ED0479 | SOUTH SOUTH |  | 2025-11-25 23:16 | Evelyn Emagurehor | 2025-11-25 23:14 | 2025-11-25 23:24 | 637 | 2025-11-25 23:14 | 2025-11-25 23:24 | 0:11 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 2 / 2 | MTN NG, Airtel NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Low DG frequency, governor was adjusted. (No diesel outage after validation). | Low DG frequency, governor was adjusted. (No diesel outage after validation).
NOCINC0006487818 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1035A | DL0001 | ASB | Asaba | Delta | 3 - Low | DL0853 | SOUTH SOUTH |  | 2025-11-30 15:14 | Ayokunle Samuel | 2025-11-30 15:14 | 2025-11-30 15:24 | 636 | 2025-11-30 15:14 | 2025-11-30 15:24 | 0:11 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006440557 | External Reconciliation | Site Down | P2 | IHS_AWK_0026B | AN0740 | ASB | Asaba | Anambra | 3 - Low | AN0500 | SOUTH EAST |  | 2025-11-24 13:36 | Aderonke Olowojoba | 2025-11-24 13:31 | 2025-11-24 13:42 | 636 | 2025-11-24 13:31 | 2025-11-24 13:42 | 0:11 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Moses Kenechukwu | Kenneth Ogbodo | Kenneth Ogbodo | Fady Safwat | Aliyu Garuba |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006473196 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1077K | OY2888 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 15:11 | Damilola Paseda | 2025-11-28 15:09 | 2025-11-28 15:20 | 625 | 2025-11-28 15:09 | 2025-11-28 15:20 | 0:10 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Olaitan Olajide | Habeeb Adepoju |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Low voltage alarm was cleared from the control module | Low voltage alarm was cleared from the control module
NOCINC0006472135 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1246B | ED5521 | IBD | Asaba | Edo | 3 - Low | ED1124 | SOUTH SOUTH |  | 2025-11-28 12:26 | Bukola Olabanji | 2025-11-28 12:24 | 2025-11-28 12:35 | 624 | 2025-11-28 12:24 | 2025-11-28 12:35 | 0:10 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Omakoji | Odihirin Omoaukhe | Odihirin Omoaukhe | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty Rectifier module was replaced (No diesel outage after validation) | Faulty Rectifier module was replaced (No diesel outage after validation)
NOCINC0006465301 | External Reconciliation | Site Down | P4 | IHS_DEL_0989A | DL2827 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 14:00 | Femi Olanipekun | 2025-11-27 13:59 | 2025-11-27 14:09 | 623 | 2025-11-27 13:59 | 2025-11-27 14:09 | 0:10 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006439663 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST |  | 2025-11-24 12:00 | Abundance Otunola | 2025-11-24 11:52 | 2025-11-24 12:03 | 623 | 2025-11-24 11:52 | 2025-11-24 12:03 | 0:10 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006465137 | External Reconciliation | Site Down | P4 | IHS_ANA_1084A | AN0312 | ASB | Asaba | Anambra | 3 - Low | AN0772 | SOUTH EAST |  | 2025-11-27 13:35 | Gbemisola Adedeji | 2025-11-27 13:33 | 2025-11-27 13:43 | 617 | 2025-11-27 13:33 | 2025-11-27 13:43 | 0:10 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Tripped load breaker was enabled (No diesel outage after validation). | Tripped load breaker was enabled (No diesel outage after validation).
NOCINC0006445240 | External Reconciliation | Site Down | P3 | IHS_OSU_0869A | T3670 | IBD | Ibadan | Osun | 3 - Low | OS0668 | WEST |  | 2025-11-25 04:08 | Valentine Adinnu | 2025-11-25 04:06 | 2025-11-25 04:17 | 617 | 2025-11-25 04:06 | 2025-11-25 04:17 | 0:10 | IPT | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | Airtel NG, MTN NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Delay in hybrid synchronization due to weak BUB, DG auto-restored | Delay in hybrid synchronization due to weak BUB, DG auto-restored
NOCINC0006461282 | External Reconciliation | Site Down | P4 | IHS_ANA_1229A | AN0565 | ASB | Asaba | Anambra | 3 - Low | - | - | NE Is Disconnected@2025-11-26 22:58:00@LAN0565 | 2025-11-26 23:12 | System Administrator | 2025-11-26 22:58 | 2025-11-26 23:08 | 616 | 2025-11-26 22:58 | 2025-11-26 23:08 | 0:10 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006477746 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1449B | AN3476 | ASB | Asaba | Anambra | 3 - Low | AN0744 | SOUTH EAST |  | 2025-11-29 07:59 | Akachukwu Ugwu | 2025-11-29 07:55 | 2025-11-29 09:01 | 3915 | 2025-11-29 07:55 | 2025-11-29 08:06 | 0:10 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | Airtel NG, MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Low DG frequency, Governor was adjusted (No diesel outage after validation). | Low DG frequency, Governor was adjusted (No diesel outage after validation).
NOCINC0006476521 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0920B | DL3279 | ASB | Asaba | Delta | 3 - Low | DL1228 | SOUTH SOUTH |  | 2025-11-29 00:30 | Femi Olanipekun | 2025-11-29 00:30 | 2025-11-29 00:40 | 609 | 2025-11-29 00:30 | 2025-11-29 00:40 | 0:10 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Contactor | 2 / 3 | MTN NG, Airtel NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Tripped load contactor was engaged (No diesel outage after validation) | Tripped load contactor was engaged (No diesel outage after validation)
NOCINC0006438469 | External Reconciliation | Site Down | P4 | IHS_OND_0830A | T3846 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-24 08:24 | Abisoye Olaleye | 2025-11-24 08:22 | 2025-11-24 08:32 | 608 | 2025-11-24 08:22 | 2025-11-24 08:32 | 0:10 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | START FAILURE DCGG RESTARTED
NOCINC0006463829 | External Reconciliation | Site Down | P1 | IHS_OYO_0001B | OY2931 | IBD | Ibadan | Oyo | 3 - Low | OY0906 | WEST |  | 2025-11-27 10:46 | Mutmainnah Saba | 2025-11-27 10:42 | 2025-11-27 10:52 | 606 | 2025-11-27 10:42 | 2025-11-27 10:52 | 0:10 | SPS | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 5 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Grid outage due to incomplete phase, DG powered automatically
NOCINC0006483878 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0023B | OS4273 | IBD | Ibadan | Osun | 3 - Low | OS0702 | WEST |  | 2025-11-29 23:55 | Mutmainnah Saba | 2025-11-29 23:52 | 2025-11-30 00:02 | 604 | 2025-11-29 23:52 | 2025-11-30 00:02 | 0:10 | IPT | Equipment Repair | Passive | Rectifier | Rectifier Module | 1 / 1 | Airtel NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Failed rectifier module was reset
NOCINC0006462660 | External Reconciliation | Site Down | P2 | IHS_ANA_1449B | AN3476 | ASB | Asaba | Anambra | 3 - Low | AN0744 | SOUTH EAST |  | 2025-11-27 06:41 | Aderonke Olowojoba | 2025-11-27 06:34 | 2025-11-27 06:44 | 604 | 2025-11-27 06:34 | 2025-11-27 06:44 | 0:10 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006445836 | External Reconciliation | Site Down | P1 | IHS_UMU_0001B | AN0093 | ASB | Asaba | Anambra | 3 - Low | AN0453 | SOUTH EAST |  | 2025-11-25 07:43 | Kehinde Akinbowale | 2025-11-25 07:42 | 2025-11-25 07:52 | 602 | 2025-11-25 07:42 | 2025-11-25 07:52 | 0:10 | Tyllium NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Aneke Christian | Habib Muhammed | Habib Muhammed | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | PPM(Generator Servicing) was completed at site | PPM(Generator Servicing) was completed at site
NOCINC0006488743 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-30 17:38 | Testimony Akinyemi | 2025-11-30 17:36 | 2025-11-30 17:46 | 600 | 2025-11-30 17:36 | 2025-11-30 17:46 | 0:10 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006458886 | External Reconciliation | Site Down | P4 | IHS_EKI_0873K | EK2260 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-26 16:00 | Mary Elaigwu | 2025-11-26 15:59 | 2025-11-26 16:09 | 600 | 2025-11-26 15:59 | 2025-11-26 16:09 | 0:10 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Oluwafemi Oluwasegun |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | hybrid synchronization failure due to overdischarge alarm was cleared
NOCINC0006468797 | External Reconciliation | Site Down | P1 | IHS_AGB_0004B | DL0002 | ASB | Asaba | Delta | 3 - Low | DL0412 | SOUTH SOUTH |  | 2025-11-28 00:18 | Patrick Okoro | 2025-11-28 00:16 | 2025-11-28 00:26 | 599 | 2025-11-28 00:16 | 2025-11-28 00:26 | 0:10 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006470402 | External Reconciliation | Site Down | P2 | IHS_DEL_0982A | DL0025 | ASB | Asaba | Delta | 3 - Low | DL0566 | SOUTH SOUTH |  | 2025-11-28 07:55 | Oluwatobiloba Are | 2025-11-28 07:54 | 2025-11-28 08:04 | 597 | 2025-11-28 07:54 | 2025-11-28 08:04 | 0:10 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Relay Faulty | 2 / 2 | MTN NG, Airtel NG |  | Stanley Odira | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Faulty starter relay was replaced (No diesel outage after validation) | Faulty starter relay was replaced (No diesel outage after validation)
NOCINC0006442261 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 16:52 | Tracy Osarumwense | 2025-11-24 16:52 | 2025-11-24 17:02 | 589 | 2025-11-24 16:52 | 2025-11-24 17:02 | 0:10 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006450899 | External Reconciliation | Site Down | P1 | IHS_DEL_1044A | DL0415 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 18:43 | Oluwatobiloba Are | 2025-11-25 18:43 | 2025-11-25 18:52 | 560 | 2025-11-25 18:42 | 2025-11-25 18:52 | 0:10 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Short duration outage, site came up without technical intervention
NOCINC0006469655 | External Reconciliation | Site Down | P4 | IHS_DEL_1082A | DL0083 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 03:47 | Patrick Okoro | 2025-11-28 03:47 | 2025-11-28 03:57 | 587 | 2025-11-28 03:47 | 2025-11-28 03:57 | 0:10 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006465434 | External Reconciliation | Site Down | P4 | IHS_ANA_1222A | AN0553 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 14:16 | Akachukwu Ugwu | 2025-11-27 14:14 | 2025-11-27 14:23 | 587 | 2025-11-27 14:14 | 2025-11-27 14:23 | 0:10 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006453746 | External Reconciliation | Site Down | P4 | IHS_DEL_1142A | DL0762 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 00:50 | Ayokunle Samuel | 2025-11-26 00:50 | 2025-11-26 00:53 | 166 | 2025-11-26 00:43 | 2025-11-26 00:53 | 0:10 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention. | Site inter failed and cleared without any technical intervention.
NOCINC0006474560 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1007A | T4857 | ASB | Asaba | Anambra | 3 - Low | AN0595 | SOUTH EAST |  | 2025-11-28 18:25 | Kehinde Akinbowale | 2025-11-28 18:23 | 2025-11-28 18:33 | 585 | 2025-11-28 18:23 | 2025-11-28 18:33 | 0:10 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | Airtel NG, MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Tripped DG load breaker was enabled No diesel outage after validation) | Tripped DG load breaker was enabled No diesel outage after validation)
NOCINC0006479636 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1193B | DL0455 | ASB | Asaba | Delta | 3 - Low | DL1209 | South South |  | 2025-11-29 12:33 | Ayomide Akindolie | 2025-11-29 12:33 | 2025-11-29 12:43 | 583 | 2025-11-29 12:33 | 2025-11-29 12:43 | 0:10 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | HENRY OMELE |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006467797 | External Reconciliation | Site Down | P1 | IHS_ANA_0938A | T4833 | ASB | Asaba | Anambra | 3 - Low | AN0133 | SOUTH EAST |  | 2025-11-27 20:38 | Patrick Okoro | 2025-11-27 20:37 | 2025-11-27 20:47 | 580 | 2025-11-27 20:37 | 2025-11-27 20:47 | 0:10 | Tyllium NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Esan Enoch | Femi Balogun | Femi Balogun | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | generator servicing was done at site
NOCINC0006467841 | External Reconciliation | Site Down | P3 | IHS_ANA_1442B | AN3470 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 20:45 | Patrick Okoro | 2025-11-27 20:40 | 2025-11-27 20:50 | 578 | 2025-11-27 20:40 | 2025-11-27 20:50 | 0:10 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006482439 | Internal Reconciliation | Site Down | P2 | IHS_ANA_0847A | T4031 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 19:21 | Solomon Bankole | 2025-11-29 19:18 | 2025-11-29 19:28 | 577 | 2025-11-29 19:18 | 2025-11-29 19:28 | 0:10 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kingsley Obele | Kingsley Obele | Kingsley Obele | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention.
NOCINC0006469732 | External Reconciliation | Site Down | P1 | IHS_EDO_0814A | T3489 | IBD | Asaba | Edo | 3 - Low | - | - | OML Fault@2025-11-28 04:04:50@T3489_Akugbe_Village | 2025-11-28 04:17 | System Administrator | 2025-11-28 04:06 | 2025-11-28 04:15 | 577 | 2025-11-28 04:06 | 2025-11-28 04:15 | 0:10 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | MICHAEL TONDO | Micheal Tondo | Micheal Tondo | Cornelius Yakubu | Elochukwu Umeohana |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without interventionn
NOCINC0006488867 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0979A | DL0033 | ASB | Asaba | Delta | 3 - Low | DL0481 | SOUTH SOUTH |  | 2025-11-30 18:00 | Ayokunle Samuel | 2025-11-30 18:00 | 2025-11-30 18:08 | 457 | 2025-11-30 17:58 | 2025-11-30 18:08 | 0:10 | Tyllium NGA | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 3 | MTN NG, Airtel NG |  | Victor Ezeh |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Hybrid synchronization delay, DG powered to restore the site. (No diesel outage after validation) | Hybrid synchronization delay, DG powered to restore the site. (No diesel outage after validation)
NOCINC0006451096 | External Reconciliation | Site Down | P4 | IHS_WAR_0813B | DL3110 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 19:07 | Ezinne Ubachukwu | 2025-11-25 19:02 | 2025-11-25 19:12 | 575 | 2025-11-25 19:02 | 2025-11-25 19:12 | 0:10 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006451031 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 19:04 | Ezinne Ubachukwu | 2025-11-25 18:59 | 2025-11-25 19:09 | 575 | 2025-11-25 18:59 | 2025-11-25 19:09 | 0:10 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006467147 | External Reconciliation | Site Down | P2 | IHS_KWA_0787A | T3166 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 18:38 | Okusanya Joseph | 2025-11-27 18:37 | 2025-11-27 18:47 | 575 | 2025-11-27 18:37 | 2025-11-27 18:47 | 0:10 | IPT | Fuel Outage (Probable) | Passive | Diesel | Fuel Line Issue | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Blocked fuel.line was flushed
NOCINC0006447843 | External Reconciliation | Site Down | P2 | IHS_EDO_1219B | ED6214 | IBD | Asaba | Edo | 3 - Low | ED0738 | SOUTH SOUTH |  | 2025-11-25 11:56 | Tracy Osarumwense | 2025-11-25 11:54 | 2025-11-25 12:03 | 572 | 2025-11-25 11:54 | 2025-11-25 12:03 | 0:10 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Alade Olufemi Olufem | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006489551 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0708E | OY4493 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 20:30 | Praise Okezie | 2025-11-30 20:27 | 2025-11-30 20:37 | 572 | 2025-11-30 20:27 | 2025-11-30 20:37 | 0:10 | SPS | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | weak DG primed to start
NOCINC0006481431 | Internal Reconciliation | Site Down | P1 | IHS_WAR_0875H | T2874 | ASB | Asaba | Delta | 3 - Low | DL0400 | SOUTH SOUTH | Huawei 3G SiteDown@2025-11-29 16:21:26@U2874 | 2025-11-29 16:36 | System Administrator | 2025-11-29 16:21 | 2025-11-29 16:31 | 572 | 2025-11-29 16:21 | 2025-11-29 16:31 | 0:10 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Stanley Odira |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006480829 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-29 15:08 | Ayomide Akindolie | 2025-11-29 15:05 | 2025-11-29 15:15 | 571 | 2025-11-29 15:05 | 2025-11-29 15:15 | 0:10 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006455791 | External Reconciliation | Site Down | P2 | IHS_ANA_1449B | AN3476 | ASB | Asaba | Anambra | 3 - Low | AN0744 | SOUTH EAST |  | 2025-11-26 07:56 | Abundance Otunola | 2025-11-26 07:56 | 2025-11-26 08:05 | 571 | 2025-11-26 07:56 | 2025-11-26 08:05 | 0:10 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | DG under frequency, Governor adjusted (No diesel outage after validation). | DG under frequency, Governor adjusted (No diesel outage after validation).
NOCINC0006478098 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1403H | AN0007 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 09:13 | Abundance Otunola | 2025-11-29 09:05 | 2025-11-29 09:15 | 569 | 2025-11-29 09:05 | 2025-11-29 09:15 | 0:09 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006451593 | External Reconciliation | Site Down | P2 | IHS_DEL_0964A | DL2989 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 20:21 | Ayomide Akindolie | 2025-11-25 20:21 | 2025-11-25 20:30 | 567 | 2025-11-25 20:21 | 2025-11-25 20:30 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006438656 | External Reconciliation | Site Down | P4 | IHS_DEL_1052A | DL0317 | ASB | Asaba | Edo | 3 - Low | - | - | CSL Fault@2025-11-24 08:33:47@DL0317_Pan Ocean Gas_Oghara | 2025-11-24 08:46 | System Administrator | 2025-11-24 08:34 | 2025-11-24 08:43 | 565 | 2025-11-24 08:34 | 2025-11-24 08:43 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006456160 | External Reconciliation | Site Down | P4 | IHS_BEN_0077C | ED5145 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 09:15 | Mary Odefemi | 2025-11-26 09:13 | 2025-11-26 09:22 | 564 | 2025-11-26 09:13 | 2025-11-26 09:22 | 0:09 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006483556 | Internal Reconciliation | Site Down | P1 | IHS_IFU_0001B | AN0118 | ASB | Asaba | Anambra | 3 - Low | AN0300 | SOUTH EAST |  | 2025-11-29 22:36 | Gbemisola Adedeji | 2025-11-29 22:30 | 2025-11-29 22:39 | 563 | 2025-11-29 22:30 | 2025-11-29 22:39 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Egbujor Victor | Ebenezer Babafemi | Ebenezer Babafemi | Henry Wanogho | Ifeanyi Chukusa |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006463638 | External Reconciliation | Site Down | P2 | IHS_EDO_0977A | ED2149 | IBD | Asaba | Edo | 3 - Low | ED0751 | SOUTH SOUTH |  | 2025-11-27 10:17 | Muhammed Hashirudeen | 2025-11-27 10:13 | 2025-11-27 10:22 | 563 | 2025-11-27 10:13 | 2025-11-27 10:22 | 0:09 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Samuel Oluwasegun | Samuel Omomule | Samuel Omomule | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Generator servicing completed at site with ref IHSREF/25111213511008328017 SARI0008829003 | Generator servicing completed at site with ref IHSREF/25111213511008328017 SARI0008829003
NOCINC0006440591 | External Reconciliation | Site Down | P1 | IHS_OSU_0791A | T3026 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 13:43 | Precious Attah | 2025-11-24 13:41 | 2025-11-24 13:51 | 560 | 2025-11-24 13:41 | 2025-11-24 13:51 | 0:09 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 1 | MTN NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Grid to DG synchronization failure due to Grid outage issue, DG powered manually.
NOCINC0006483396 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1215A | AN0775 | ASB | Asaba | Anambra | 3 - Low | AN0766 | SOUTH EAST |  | 2025-11-29 22:10 | Gbemisola Adedeji | 2025-11-29 22:06 | 2025-11-29 22:15 | 559 | 2025-11-29 22:06 | 2025-11-29 22:15 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Egbujor Victor | Ebenezer Babafemi | Ebenezer Babafemi | Henry Wanogho | Ifeanyi Chukusa |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 2 | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006464705 | External Reconciliation | Site Down | P4 | IHS_DEL_1137A | DL0685 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 12:31 | Femi Olanipekun | 2025-11-27 12:27 | 2025-11-27 12:36 | 558 | 2025-11-27 12:27 | 2025-11-27 12:36 | 0:09 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006452806 | External Reconciliation | Site Down | P2 | IHS_DEL_0966A | T2440 | PHC | Asaba | Delta | 3 - Low | - | - | The link between the server and the ME is broken@2025-11-25 23:25:33@T2440 | 2025-11-25 23:38 | System Administrator | 2025-11-25 23:26 | 2025-11-25 23:35 | 558 | 2025-11-25 23:26 | 2025-11-25 23:35 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006480066 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-29 13:31 | Ayomide Akindolie | 2025-11-29 13:30 | 2025-11-29 13:39 | 557 | 2025-11-29 13:30 | 2025-11-29 13:39 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006482042 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0761E | OS2764 | IBD | Ibadan | Kwara | 3 - Low | OS0823 | WEST |  | 2025-11-29 18:16 | Azeezat Adekunle | 2025-11-29 18:14 | 2025-11-29 18:23 | 553 | 2025-11-29 18:14 | 2025-11-29 18:23 | 0:09 | IPT | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | MTN NG, Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | PPM (Generator servicing) was carried out
NOCINC0006456155 | External Reconciliation | Site Down | P2 | IHS_DEL_0921A | T2952 | ASB | Asaba | Delta | 3 - Low | DL0763 | SOUTH SOUTH | Cascaded Incident from TTO6739961 - Cascade Removed From TTO6739961 | 2025-11-26 09:14 | Oluwatobiloba Are | 2025-11-26 09:10 | 2025-11-26 09:19 | 551 | 2025-11-26 09:10 | 2025-11-26 09:19 | 0:09 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006465753 | External Reconciliation | Site Down | P3 | IHS_OSU_0058B | OS4265 | IBD | Ibadan | Osun | 3 - Low | OS0701 | WEST |  | 2025-11-27 15:05 | Mutmainnah Saba | 2025-11-27 15:01 | 2025-11-27 15:10 | 551 | 2025-11-27 15:01 | 2025-11-27 15:10 | 0:09 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | MTN NG, Airtel NG |  | Hakeem Abayomi | Hakeem Abayomi | Hakeem Abayomi | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed fuel pump was worked on
NOCINC0006481136 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 15:54 | Ayomide Akindolie | 2025-11-29 15:54 | 2025-11-29 16:03 | 550 | 2025-11-29 15:54 | 2025-11-29 16:03 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006460846 | External Reconciliation | Site Down | P2 | IHS_DEL_0964A | DL2989 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 21:40 | Tracy Osarumwense | 2025-11-26 21:40 | 2025-11-26 21:49 | 549 | 2025-11-26 21:40 | 2025-11-26 21:49 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006474470 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0966A | T2440 | PHC | Asaba | Delta | 3 - Low | - | - | The link between the server and the ME is broken@2025-11-28 18:00:59@T2440 | 2025-11-28 18:14 | System Administrator | 2025-11-28 18:01 | 2025-11-28 18:10 | 548 | 2025-11-28 18:01 | 2025-11-28 18:10 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006481767 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0882C | EK4514 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-29 17:27 | Testimony Akinyemi | 2025-11-29 17:26 | 2025-11-29 17:35 | 546 | 2025-11-29 17:26 | 2025-11-29 17:35 | 0:09 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Charging Alternator | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | charging alternator was replaced
NOCINC0006445126 | External Reconciliation | Site Down | P3 | IHS_EDO_0749A | T0218 | IBD | Asaba | Edo | 3 - Low | ED0700 | SOUTH SOUTH |  | 2025-11-25 03:03 | Azeezat Badmus | 2025-11-25 03:02 | 2025-11-25 03:11 | 545 | 2025-11-25 03:02 | 2025-11-25 03:11 | 0:09 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Outage Issue | 2 / 2 | Airtel NG, MTN NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Grid synchronization delay due to weak bub, DG powered manually (No diesel outage after validation)
NOCINC0006464533 | External Reconciliation | Site Down | P1 | IHS_WAR_0059C | DL0852 | ASB | Asaba | Delta | 3 - Low | DL0572 | SOUTH SOUTH |  | 2025-11-27 12:13 | Mary Odefemi | 2025-11-27 12:08 | 2025-11-27 12:17 | 544 | 2025-11-27 12:08 | 2025-11-27 12:17 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 21 | Short duration outage
NOCINC0006480737 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-29 14:54 | Ayomide Akindolie | 2025-11-29 14:54 | 2025-11-29 15:04 | 544 | 2025-11-29 14:54 | 2025-11-29 15:04 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006485207 | Internal Reconciliation | Site Down | P3 | IHS_AGB_0005B | DL0430 | ASB | Asaba | Delta | 3 - Low | DL0522 | SOUTH SOUTH |  | 2025-11-30 08:05 | Uthman Akinola | 2025-11-30 08:02 | 2025-11-30 08:11 | 543 | 2025-11-30 08:02 | 2025-11-30 08:11 | 0:09 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006480465 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 14:19 | Ayomide Akindolie | 2025-11-29 14:19 | 2025-11-29 14:28 | 540 | 2025-11-29 14:19 | 2025-11-29 14:28 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006481292 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 16:16 | Ayomide Akindolie | 2025-11-29 16:14 | 2025-11-29 16:23 | 540 | 2025-11-29 16:14 | 2025-11-29 16:23 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006482240 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-29 18:41:21@T2719_30 Emevor Orogun Road | 2025-11-29 18:53 | System Administrator | 2025-11-29 18:47 | 2025-11-29 18:50 | 180 | 2025-11-29 18:47 | 2025-11-29 18:56 | 0:09 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without any technical intervention | Site came up without any technical intervention
NOCINC0006462502 | External Reconciliation | Site Down | P3 | IHS_ANA_0856A | T4064 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 06:03 | Aderonke Olowojoba | 2025-11-27 05:59 | 2025-11-27 06:08 | 540 | 2025-11-27 05:59 | 2025-11-27 06:08 | 0:09 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 3 | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006449789 | External Reconciliation | Site Down | P4 | IHS_EDO_1034A | ED2103 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 16:02 | Emmanuel Faleti | 2025-11-25 16:02 | 2025-11-25 16:11 | 540 | 2025-11-25 16:02 | 2025-11-25 16:11 | 0:09 | MPI NGA | Equipment Repair | Passive | Rectifier | Rectifier Battery | 1 / 1 | MTN NG |  | SAHEED SHONDE | Babatunde Olayiwola | Shonde Saheed | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Faulty rectifier battery was isolated (No diesel outage after validation) | Faulty rectifier battery was isolated (No diesel outage after validation)
NOCINC0006471042 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0885A | T4116 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 09:47 | Gbemisola Adedeji | 2025-11-28 09:45 | 2025-11-28 09:54 | 540 | 2025-11-28 09:45 | 2025-11-28 09:54 | 0:09 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 1 / 1 | MTN NG |  | Obinna Festus | Festus Obinna | Festus Obinna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Low oil Pressure alarm was cleared(No diesel outage after validation) | Low oil Pressure alarm was cleared(No diesel outage after validation)
NOCINC0006479696 | Internal Reconciliation | Site Down | P4 | IHS_OND_0033B | OD2599 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 12:44 | Maureen Uchehorke | 2025-11-29 12:42 | 2025-11-29 12:51 | 540 | 2025-11-29 12:42 | 2025-11-29 12:51 | 0:09 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - AVR | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG Voltage Fluctuation, AVR Was Adjusted
NOCINC0006452875 | External Reconciliation | Site Down | P4 | IHS_EDO_1002A | ED4937 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 00:09 | Evelyn Emagurehor | 2025-11-26 00:07 | 2025-11-26 00:16 | 537 | 2025-11-26 00:07 | 2025-11-26 00:16 | 0:09 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | GODFREY NATHANIEL |  | Nathaniel Godfrey | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006473442 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0908A | T4099 | ASB | Asaba | Anambra | 3 - Low | AN0964 | SOUTH EAST |  | 2025-11-28 15:50 | Gbemisola Adedeji | 2025-11-28 15:48 | 2025-11-28 15:57 | 537 | 2025-11-28 15:48 | 2025-11-28 15:57 | 0:09 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Tripped DG load breaker was enabled (No diesel outage after validation) | Tripped DG load breaker was enabled (No diesel outage after validation)
NOCINC0006457350 | External Reconciliation | Site Down | P1 | IHS_EDO_0996A | ED4860 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 12:13 | Emmanuel Faleti | 2025-11-26 12:10 | 2025-11-26 12:19 | 536 | 2025-11-26 12:10 | 2025-11-26 12:19 | 0:09 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on. (No diesel outage after validation) | Faulty ATS contactor was worked on. (No diesel outage after validation)
NOCINC0006440566 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 13:37 | Tracy Osarumwense | 2025-11-24 13:36 | 2025-11-24 13:45 | 535 | 2025-11-24 13:36 | 2025-11-24 13:45 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006444602 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-24 23:29 | Kehinde Akinbowale | 2025-11-24 23:27 | 2025-11-24 23:35 | 534 | 2025-11-24 23:27 | 2025-11-24 23:35 | 0:09 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Weak DG was primed to start(No diesel outage after validation) | Weak DG was primed to start(No diesel outage after validation)
NOCINC0006474737 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0776A | T3201 | IBD | Asaba | Edo | 3 - Low | ED0556 | SOUTH SOUTH |  | 2025-11-28 18:46 | Azeezat Badmus | 2025-11-28 18:44 | 2025-11-28 18:53 | 529 | 2025-11-28 18:44 | 2025-11-28 18:53 | 0:09 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Kazeem Ajiboye |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | site cleared with no technical intervention
NOCINC0006472233 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0824A | T3959 | IBD | Ibadan | Kwara | 3 - Low | KW0495 | WEST |  | 2025-11-28 12:41 | Okusanya Joseph | 2025-11-28 12:39 | 2025-11-28 12:48 | 527 | 2025-11-28 12:39 | 2025-11-28 12:48 | 0:09 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 7 | Short duration outage, site was up with no intervention.
NOCINC0006440597 | External Reconciliation | Site Down | P3 | IHS_ANA_1061A | AN4165 | ASB | Asaba | Anambra | 3 - Low | AN0863 | SOUTH EAST |  | 2025-11-24 13:44 | Aderonke Olowojoba | 2025-11-24 13:40 | 2025-11-24 13:49 | 526 | 2025-11-24 13:40 | 2025-11-24 13:49 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Harrison Igbinedion | Harrison Igbinedion | Harrison Igbinedion | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006457594 | External Reconciliation | Site Down | P1 | IHS_DEL_1020A | DL0113 | ASB | Asaba | Delta | 3 - Low | DL0742 | SOUTH SOUTH | CSL Fault@2025-11-26 12:34:02@DL0113_Sokobulu | 2025-11-26 12:46 | System Administrator | 2025-11-26 12:41 | 2025-11-26 12:49 | 526 | 2025-11-26 12:41 | 2025-11-26 12:49 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006477578 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 07:19 | Akachukwu Ugwu | 2025-11-29 07:14 | 2025-11-29 07:22 | 525 | 2025-11-29 07:14 | 2025-11-29 07:22 | 0:09 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006437679 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-24 04:19 | Gbemisola Adedeji | 2025-11-24 04:16 | 2025-11-24 04:25 | 523 | 2025-11-24 04:16 | 2025-11-24 04:25 | 0:09 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty injector was worked on (No diesel outage after validation) | Faulty injector was worked on (No diesel outage after validation)
NOCINC0006439607 | External Reconciliation | Site Down | P4 | IHS_ANA_1440B | AN3475 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 11:41 | Aderonke Olowojoba | 2025-11-24 11:37 | 2025-11-24 11:46 | 522 | 2025-11-24 11:37 | 2025-11-24 11:46 | 0:09 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obinna Clinton |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006488899 | Internal Reconciliation | Site Down | P4 | IHS_ASA_0003B | DL0483 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 18:04 | Ezinne Ubachukwu | 2025-11-30 17:59 | 2025-11-30 18:07 | 521 | 2025-11-30 17:59 | 2025-11-30 18:07 | 0:09 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Victor Ezeh |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006476913 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 03:51 | Akachukwu Ugwu | 2025-11-29 03:47 | 2025-11-29 03:56 | 517 | 2025-11-29 03:47 | 2025-11-29 03:56 | 0:09 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006446930 | External Reconciliation | Site Down | P1 | IHS_DEL_1017A | DL0111 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 10:16 | Oluwatobiloba Are | 2025-11-25 10:15 | 2025-11-25 10:23 | 516 | 2025-11-25 10:15 | 2025-11-25 10:23 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Short duration outage, site came up without technical intervention
NOCINC0006460669 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-26 21:07 | Aderonke Olowojoba | 2025-11-26 21:02 | 2025-11-26 21:11 | 516 | 2025-11-26 21:02 | 2025-11-26 21:11 | 0:09 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006477147 | Internal Reconciliation | Site Down | P1 | IHS_IBA_0713E | - | - | Ibadan | Oyo | 3 - Low | OY0979 | WEST |  | 2025-11-29 04:53 | Bosede Kutelu | 2025-11-29 04:52 | 2025-11-29 05:00 | 516 | 2025-11-29 04:52 | 2025-11-29 05:00 | 0:09 | SPS | Equipment Repair | Passive | Control Panel | ATS Relay Faulty | 1 / 1 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Faulty ATS relay was worked on
NOCINC0006479656 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1135A | DL0688 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 12:36 | Ayomide Akindolie | 2025-11-29 12:33 | 2025-11-29 12:42 | 515 | 2025-11-29 12:33 | 2025-11-29 12:42 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | HENRY OMELE | Henry Ikede | Henry Ikede | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006486938 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0743C | DL1071 | ASB | Asaba | Delta | 3 - Low | DL1075 | SOUTH SOUTH |  | 2025-11-30 13:08 | Ezinne Ubachukwu | 2025-11-30 13:05 | 2025-11-30 13:13 | 514 | 2025-11-30 13:05 | 2025-11-30 13:13 | 0:09 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006450893 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 18:42 | Oluwatobiloba Are | 2025-11-25 18:42 | 2025-11-25 18:51 | 514 | 2025-11-25 18:42 | 2025-11-25 18:51 | 0:09 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Short duration outage, site came up without technical intervention
NOCINC0006483346 | Internal Reconciliation | Site Down | P3 | IHS_AWK_0019B | AN0577 | ASB | Asaba | Anambra | 3 - Low | AN0767 | SOUTH EAST |  | 2025-11-29 22:02 | Gbemisola Adedeji | 2025-11-29 21:58 | 2025-11-29 22:06 | 507 | 2025-11-29 21:58 | 2025-11-29 22:06 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Egbujor Victor | Ebenezer Babafemi | Ebenezer Babafemi | Henry Wanogho | Ifeanyi Chukusa |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006451950 | External Reconciliation | Site Down | P3 | IHS_OSU_0073B | OS4386 | IBD | Ibadan | Osun | 3 - Low | OS0712 | WEST |  | 2025-11-25 21:12 | Azeezat Adekunle | 2025-11-25 21:11 | 2025-11-25 21:19 | 506 | 2025-11-25 21:11 | 2025-11-25 21:19 | 0:08 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006485893 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-30 10:22 | Ayomide Akindolie | 2025-11-30 10:22 | 2025-11-30 10:30 | 506 | 2025-11-30 10:22 | 2025-11-30 10:30 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006484330 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1174A | AN0558 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 03:10 | Gbemisola Adedeji | 2025-11-30 03:05 | 2025-11-30 03:14 | 505 | 2025-11-30 03:05 | 2025-11-30 03:14 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006438709 | External Reconciliation | Site Down | P4 | IHS_DEL_0955A | T2713 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 08:53 | Ayomide Akindolie | 2025-11-24 08:52 | 2025-11-24 09:01 | 505 | 2025-11-24 08:52 | 2025-11-24 09:01 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KELECHI LEWIS |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006464803 | External Reconciliation | Site Down | P4 | IHS_EDO_1048C | ED6125 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 12:45 | Mary Odefemi | 2025-11-27 12:41 | 2025-11-27 12:49 | 503 | 2025-11-27 12:41 | 2025-11-27 12:49 | 0:08 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006476684 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 01:41 | Akachukwu Ugwu | 2025-11-29 01:37 | 2025-11-29 01:46 | 503 | 2025-11-29 01:37 | 2025-11-29 01:46 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006463693 | External Reconciliation | Site Down | P1 | IHS_OYO_0902A | T3865 | IBD | Ibadan | Oyo | 3 - Low | OY0963 | WEST |  | 2025-11-27 10:29 | Mutmainnah Saba | 2025-11-27 10:26 | 2025-11-27 10:35 | 501 | 2025-11-27 10:26 | 2025-11-27 10:35 | 0:08 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 2 / 2 | MTN NG, Airtel NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 3 | Tripped load breaker enabled
NOCINC0006472470 | Internal Reconciliation | Site Down | P3 | IHS_ILO_0703E | T3173 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 13:17 | Okusanya Joseph | 2025-11-28 13:16 | 2025-11-28 13:24 | 501 | 2025-11-28 13:16 | 2025-11-28 13:24 | 0:08 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Generator servicing (PPM) was carried out
NOCINC0006449533 | External Reconciliation | Site Down | P1 | IHS_DEL_0967A | DL2791 | ASB | Asaba | Delta | 3 - Low | DL1264 | SOUTH SOUTH |  | 2025-11-25 15:28 | Ezinne Ubachukwu | 2025-11-25 15:25 | 2025-11-25 15:33 | 500 | 2025-11-25 15:25 | 2025-11-25 15:33 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site restored without any technical intervention
NOCINC0006457744 | External Reconciliation | Site Down | P1 | IHS_DEL_1044A | DL0415 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-26 12:55:58@DL0415_Kurutie | 2025-11-26 13:08 | System Administrator | 2025-11-26 13:02 | 2025-11-26 13:10 | 500 | 2025-11-26 13:02 | 2025-11-26 13:10 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Short duration outage, site came up without technical intervention
NOCINC0006457896 | External Reconciliation | Site Down | P4 | IHS_ANA_1229A | AN0565 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 13:37 | Akachukwu Ugwu | 2025-11-26 13:34 | 2025-11-26 13:42 | 499 | 2025-11-26 13:34 | 2025-11-26 13:42 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006465509 | External Reconciliation | Site Down | P1 | IHS_DEL_0896A | T2777 | ASB | Asaba | Delta | 3 - Low | DL0250 | SOUTH SOUTH |  | 2025-11-27 14:25 | Femi Olanipekun | 2025-11-27 14:25 | 2025-11-27 14:33 | 498 | 2025-11-27 14:25 | 2025-11-27 14:33 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006457139 | External Reconciliation | Site Down | P2 | IHS_DEL_0877A | T2772 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 11:41 | Oluwatobiloba Are | 2025-11-26 11:37 | 2025-11-26 11:45 | 498 | 2025-11-26 11:37 | 2025-11-26 11:45 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006457790 | External Reconciliation | Site Down | P3 | IHS_EDO_0874A | ED3970 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 13:14 | Azeezat Badmus | 2025-11-26 13:13 | 2025-11-26 13:21 | 497 | 2025-11-26 13:13 | 2025-11-26 13:21 | 0:08 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | site cleared with no technical intervention
NOCINC0006463889 | External Reconciliation | Site Down | P3 | IHS_WAR_0952B | DL3353 | ASB | Asaba | Delta | 3 - Low | DL0900 | SOUTH SOUTH |  | 2025-11-27 10:58 | Bukola Olabanji | 2025-11-27 10:56 | 2025-11-27 11:05 | 496 | 2025-11-27 10:56 | 2025-11-27 11:05 | 0:08 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Kehinde Adekanbi |  |  | Erik Nwodo | John Wekpe |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006443579 | External Reconciliation | Site Down | P3 | IHS_KWA_0939C | KW6391 | IBD | Ibadan | Kwara | 3 - Low | KW0598 | WEST |  | 2025-11-24 20:17 | Azeezat Adekunle | 2025-11-24 20:16 | 2025-11-24 20:25 | 496 | 2025-11-24 20:16 | 2025-11-24 20:25 | 0:08 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | dg under voltage alarm cleared
NOCINC0006480925 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1042A | AN0113 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 15:26 | Ayokunle Samuel | 2025-11-29 15:23 | 2025-11-29 15:31 | 494 | 2025-11-29 15:23 | 2025-11-29 15:31 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kingsley Obele | Kingsley Obele | Kingsley Obele | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention.
NOCINC0006468184 | External Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-27 21:39:56@T2719_30 Emevor Orogun Road | 2025-11-27 21:52 | System Administrator | 2025-11-27 21:45 | 2025-11-27 21:54 | 493 | 2025-11-27 21:45 | 2025-11-27 21:54 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site cleared without intervention
NOCINC0006476671 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1002A | T4877 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 01:33 | Femi Olanipekun | 2025-11-29 01:31 | 2025-11-29 01:39 | 492 | 2025-11-29 01:31 | 2025-11-29 01:39 | 0:08 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obinna Clinton |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006476254 | Internal Reconciliation | Site Down | P2 | IHS_EDO_1023A | ED4913 | IBD | Asaba | Edo | 3 - Low | ED0497 | SOUTH SOUTH |  | 2025-11-28 22:55 | Elizabeth Apata | 2025-11-28 22:53 | 2025-11-28 23:01 | 492 | 2025-11-28 22:53 | 2025-11-28 23:01 | 0:08 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Hybrid synchronization failure. DG was powered manually (No diesel outage after validation)
NOCINC0006466565 | External Reconciliation | Site Down | P3 | IHS_OZO_0001C | DL0884 | ASB | Asaba | Delta | 3 - Low | DL0715 | SOUTH SOUTH |  | 2025-11-27 16:58 | Femi Olanipekun | 2025-11-27 16:58 | 2025-11-27 17:06 | 492 | 2025-11-27 16:58 | 2025-11-27 17:06 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006489894 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1002A | ED4937 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 21:40 | Azeezat Badmus | 2025-11-30 21:39 | 2025-11-30 21:47 | 492 | 2025-11-30 21:39 | 2025-11-30 21:47 | 0:08 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | GODFREY NATHANIEL |  | Nathaniel Godfrey | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention
NOCINC0006460293 | External Reconciliation | Site Down | P3 | IHS_ILO_0721E | KW4750 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-26 20:11 | Titus Tosin | 2025-11-26 20:09 | 2025-11-26 20:17 | 491 | 2025-11-26 20:09 | 2025-11-26 20:17 | 0:08 | IPT | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 2 / 2 | MTN NG, Airtel NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to Unstable Grid Supply Issue, DG powered manually.
NOCINC0006438181 | External Reconciliation | Site Down | P2 | IHS_AWK_0026B | AN0740 | ASB | Asaba | Anambra | 3 - Low | AN0500 | SOUTH EAST |  | 2025-11-24 06:56 | Gbemisola Adedeji | 2025-11-24 06:53 | 2025-11-24 07:01 | 491 | 2025-11-24 06:53 | 2025-11-24 07:01 | 0:08 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Moses Kenechukwu | Kenneth Ogbodo | Kenneth Ogbodo | Fady Safwat | Aliyu Garuba |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Failed rectifier module was replaced (No diesel outage after validation). | Failed rectifier module was replaced (No diesel outage after validation).
NOCINC0006474821 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0008B | ED5007 | IBD | Asaba | Edo | 3 - Low | ED1032 | SOUTH SOUTH |  | 2025-11-28 19:06 | Abundance Otunola | 2025-11-28 19:03 | 2025-11-28 19:11 | 488 | 2025-11-28 19:03 | 2025-11-28 19:11 | 0:08 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | MICHAEL TONDO | Micheal Tondo | Micheal Tondo | Cornelius Yakubu | Elochukwu Umeohana |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006449879 | External Reconciliation | Site Down | P4 | IHS_DEL_0905A | T2768 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 16:16 | Ezinne Ubachukwu | 2025-11-25 16:12 | 2025-11-25 16:20 | 487 | 2025-11-25 16:12 | 2025-11-25 16:20 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006465605 | External Reconciliation | Site Down | P2 | IHS_EDO_1019A | ED2129 | IBD | Asaba | Edo | 3 - Low | ED0631 | SOUTH SOUTH |  | 2025-11-27 14:42 | Muhammed Hashirudeen | 2025-11-27 14:42 | 2025-11-27 14:50 | 487 | 2025-11-27 14:42 | 2025-11-27 14:50 | 0:08 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Samuel Oluwasegun | Samuel Omomule | Samuel Omomule | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | failed charging alternator was excited (No diesel outage after validation)
NOCINC0006438693 | External Reconciliation | Site Down | P3 | IHS_DEL_0968A | DL0008 | ASB | Asaba | Delta | 3 - Low | DL0930 | SOUTH SOUTH |  | 2025-11-24 08:50 | Ezinne Ubachukwu | 2025-11-24 08:49 | 2025-11-24 08:58 | 487 | 2025-11-24 08:49 | 2025-11-24 08:58 | 0:08 | Tyllium NGA | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty ATS contactor was energized. (No diesel outage after validation) | Faulty ATS contactor was energized. (No diesel outage after validation)
NOCINC0006443393 | External Reconciliation | Site Down | P3 | IHS_EDO_1312B | - | - | Asaba | Edo | 3 - Low | ED0818 | SOUTH SOUTH |  | 2025-11-24 19:43 | Ayomide Akindolie | 2025-11-24 19:43 | 2025-11-24 19:51 | 486 | 2025-11-24 19:43 | 2025-11-24 19:51 | 0:08 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006476670 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 01:31 | Akachukwu Ugwu | 2025-11-29 01:25 | 2025-11-29 01:33 | 485 | 2025-11-29 01:25 | 2025-11-29 01:33 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006486940 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-30 13:08 | Ayomide Akindolie | 2025-11-30 13:07 | 2025-11-30 13:15 | 485 | 2025-11-30 13:07 | 2025-11-30 13:15 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006455747 | External Reconciliation | Site Down | P4 | IHS_AWK_0030C | AN0891 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 07:47 | Abundance Otunola | 2025-11-26 07:44 | 2025-11-26 07:52 | 484 | 2025-11-26 07:44 | 2025-11-26 07:52 | 0:08 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006462608 | External Reconciliation | Site Down | P2 | IHS_ANA_1208A | AN0578 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-27 06:13:27@AN0578_Samuel Nwakaemes Compound | 2025-11-27 06:26 | System Administrator | 2025-11-27 06:13 | 2025-11-27 06:21 | 480 | 2025-11-27 06:13 | 2025-11-27 06:21 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Madu Modestus | Madu Modestus | Madu Modestus | Fady Safwat | Aliyu Garuba |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006449137 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 14:35 | Oluwatomisin Sogbesan | 2025-11-25 14:32 | 2025-11-25 14:40 | 480 | 2025-11-25 14:32 | 2025-11-25 14:40 | 0:08 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006459508 | External Reconciliation | Site Down | P4 | IHS_EKI_0874K | EK4417 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-26 17:48 | Mary Elaigwu | 2025-11-26 17:46 | 2025-11-26 17:54 | 480 | 2025-11-26 17:46 | 2025-11-26 17:54 | 0:08 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - RPM - Gas Flow | 1 / 1 | MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | frozen gas line was worked on
NOCINC0006482962 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0966A | T2440 | PHC | Asaba | Delta | 3 - Low | - | - | The link between the server and the ME is broken@2025-11-29 20:53:55@T2440 | 2025-11-29 21:06 | System Administrator | 2025-11-29 20:54 | 2025-11-29 21:02 | 478 | 2025-11-29 20:54 | 2025-11-29 21:02 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006446726 | External Reconciliation | Site Down | P2 | IHS_DEL_1087A | DL0700 | ASB | Asaba | Delta | 3 - Low | DL0770 | SOUTH SOUTH |  | 2025-11-25 09:52 | Oluwatobiloba Are | 2025-11-25 09:52 | 2025-11-25 10:00 | 477 | 2025-11-25 09:52 | 2025-11-25 10:00 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006484292 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0804A | T3230 | IBD | Asaba | Edo | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-30 02:39:24@ | 2025-11-30 02:54 | System Administrator | 2025-11-30 02:39 | 2025-11-30 02:47 | 475 | 2025-11-30 02:39 | 2025-11-30 02:47 | 0:08 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 1 | MTN NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Burnt DC breaker was replaced (No diesel outage after validation)
NOCINC0006462068 | External Reconciliation | Site Down | P4 | IHS_ANA_1174A | AN0558 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-27 02:50:40@AN0558_Ebenato Amichi | 2025-11-27 03:03 | System Administrator | 2025-11-27 03:00 | 2025-11-27 03:08 | 474 | 2025-11-27 03:00 | 2025-11-27 03:08 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006438869 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 09:27 | Ezinne Ubachukwu | 2025-11-24 09:26 | 2025-11-24 09:34 | 473 | 2025-11-24 09:26 | 2025-11-24 09:34 | 0:08 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006481269 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1229A | AN0565 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 16:14 | Kehinde Akinbowale | 2025-11-29 16:11 | 2025-11-29 16:19 | 473 | 2025-11-29 16:11 | 2025-11-29 16:19 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006441760 | External Reconciliation | Site Down | P2 | IHS_DEL_0957A | T2919 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 16:24 | Ezinne Ubachukwu | 2025-11-24 16:20 | 2025-11-24 16:28 | 473 | 2025-11-24 16:20 | 2025-11-24 16:28 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006452857 | External Reconciliation | Site Down | P4 | IHS_OYO_1084K | OY4079 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 00:01 | Aishat Oyedeji | 2025-11-26 00:01 | 2025-11-26 00:09 | 472 | 2025-11-26 00:01 | 2025-11-26 00:09 | 0:08 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Olaitan Olajide | Habeeb Adepoju |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | start failure alarm was cleared from the control module.
NOCINC0006477347 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-29 06:08 | Akachukwu Ugwu | 2025-11-29 06:03 | 2025-11-29 06:11 | 470 | 2025-11-29 06:03 | 2025-11-29 06:11 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006438850 | External Reconciliation | Site Down | P4 | IHS_DEL_0968A | DL0008 | ASB | Asaba | Delta | 3 - Low | DL0930 | SOUTH SOUTH |  | 2025-11-24 09:23 | Ayokunle Samuel | 2025-11-24 09:21 | 2025-11-24 09:29 | 470 | 2025-11-24 09:21 | 2025-11-24 09:29 | 0:08 | Tyllium NGA | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty ATS contactor was energized. (No diesel outage after validation) | Faulty ATS contactor was energized. (No diesel outage after validation)
NOCINC0006456806 | External Reconciliation | Site Down | P4 | IHS_EDO_1021A | ED4883 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 11:08 | Azeezat Badmus | 2025-11-26 11:05 | 2025-11-26 11:13 | 469 | 2025-11-26 11:05 | 2025-11-26 11:13 | 0:08 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Mike Imomoh | Mike Imomoh | Mike Imomoh | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | PPM was completed at site (No diesel outage after validation)
NOCINC0006471271 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1316B | AN3147 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 10:17 | Kehinde Akinbowale | 2025-11-28 10:14 | 2025-11-28 10:22 | 468 | 2025-11-28 10:14 | 2025-11-28 10:22 | 0:08 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006471786 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1211A | AN0767 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 11:25 | Kehinde Akinbowale | 2025-11-28 11:24 | 2025-11-28 11:32 | 465 | 2025-11-28 11:24 | 2025-11-28 11:32 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Aneke Christian | Habib Muhammed | Habib Muhammed | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006439648 | External Reconciliation | Site Down | P1 | IHS_DEL_0993A | DL0005 | ASB | Asaba | Delta | 3 - Low | DL1260 | SOUTH SOUTH |  | 2025-11-24 11:53 | Ayomide Akindolie | 2025-11-24 11:53 | 2025-11-24 12:01 | 465 | 2025-11-24 11:53 | 2025-11-24 12:01 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006474802 | Internal Reconciliation | Site Down | P3 | IHS_OSU_1035H | OS4263 | IBD | Ibadan | Osun | 3 - Low | OS0894 | WEST |  | 2025-11-28 19:02 | Valentine Adinnu | 2025-11-28 18:57 | 2025-11-28 19:05 | 462 | 2025-11-28 18:57 | 2025-11-28 19:05 | 0:08 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | Airtel NG, MTN NG |  | Adejumobi Tunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed rectifier module was reset | Failed rectifier module was reset
NOCINC0006461388 | External Reconciliation | Site Down | P4 | IHS_EDO_1002A | ED4937 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 23:34 | Oluwatomisin Sogbesan | 2025-11-26 23:33 | 2025-11-26 23:41 | 462 | 2025-11-26 23:33 | 2025-11-26 23:41 | 0:08 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | GODFREY NATHANIEL |  | Nathaniel Godfrey | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006489404 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0033V | ED5147 | IBD | Asaba | Edo | 3 - Low | ED0453 | SOUTH SOUTH |  | 2025-11-30 19:51 | Ayomide Akindolie | 2025-11-30 19:51 | 2025-11-30 19:58 | 461 | 2025-11-30 19:51 | 2025-11-30 19:58 | 0:08 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006469462 | External Reconciliation | Site Down | P1 | IHS_DEL_0966A | T2440 | PHC | Asaba | Delta | 3 - Low | - | - | ZTE 3G SiteDown@2025-11-28 01:54:12@T2440 | 2025-11-28 02:07 | System Administrator | 2025-11-28 02:04 | 2025-11-28 02:12 | 460 | 2025-11-28 02:04 | 2025-11-28 02:12 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006464379 | External Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-27 11:55 | Bukola Olabanji | 2025-11-27 11:51 | 2025-11-27 11:59 | 459 | 2025-11-27 11:51 | 2025-11-27 11:59 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | SHORT DURATION OUTAGE
NOCINC0006472345 | Internal Reconciliation | Site Down | P3 | IHS_EKI_0923B | EK4552 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-28 12:59 | Testimony Akinyemi | 2025-11-28 12:56 | 2025-11-28 13:04 | 458 | 2025-11-28 12:56 | 2025-11-28 13:04 | 0:08 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | weak BUB GG auto restart.
NOCINC0006436178 | External Reconciliation | Site Down | P4 | IHS_DEL_0997A | DL0010 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-23 22:44 | Uthman Akinola | 2025-11-23 22:44 | 2025-11-24 00:08 | 5012 | 2025-11-24 | 2025-11-24 00:08 | 0:08 | Tyllium NGA | Equipment Repair | Passive | ACDG Gen | ACDG - AVR | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed AVR was worked on
NOCINC0006486320 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-30 11:40 | Tracy Osarumwense | 2025-11-30 11:39 | 2025-11-30 11:47 | 457 | 2025-11-30 11:39 | 2025-11-30 11:47 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006445890 | External Reconciliation | Site Down | P3 | IHS_EDO_0749A | T0218 | IBD | Asaba | Edo | 3 - Low | ED0700 | SOUTH SOUTH |  | 2025-11-25 08:03 | Azeezat Badmus | 2025-11-25 08:03 | 2025-11-25 08:10 | 457 | 2025-11-25 08:03 | 2025-11-25 08:10 | 0:08 | Huawei | Grid Supply | Passive | Grid | National Grid - Grid Outage Issue | 2 / 2 | Airtel NG, MTN NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Synchronization failure due to grid outage, DG was powered manually. (No diesel outage after validation) | Synchronization failure due to grid outage, DG was powered manually. (No diesel outage after validation)
NOCINC0006463598 | External Reconciliation | Site Down | P3 | IHS_ONT_0006B | AN0316 | ASB | Asaba | Anambra | 3 - Low | AN0588 | SOUTH EAST |  | 2025-11-27 10:10 | Akachukwu Ugwu | 2025-11-27 10:06 | 2025-11-27 10:14 | 456 | 2025-11-27 10:06 | 2025-11-27 10:14 | 0:08 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006485386 | Internal Reconciliation | Site Down | P4 | IHS_OND_0874A | T3936 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 08:44 | Ihuoma Opurum | 2025-11-30 08:44 | 2025-11-30 08:52 | 456 | 2025-11-30 08:44 | 2025-11-30 08:52 | 0:08 | IPT | Equipment Repair | Passive | DCDG Gen | DCDG - AVR | 1 / 1 | MTN NG |  | Adetunji Tosin | Fajimi Tosin | Fajimi Tosin | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG fluctuation due to faulty AVR. AVR was adjusted.
NOCINC0006440681 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 13:59 | Tracy Osarumwense | 2025-11-24 13:57 | 2025-11-24 14:05 | 456 | 2025-11-24 13:57 | 2025-11-24 14:05 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006470326 | External Reconciliation | Site Down | P1 | IHS_ANA_0809A | T4053 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 07:40 | Patrick Okoro | 2025-11-28 07:38 | 2025-11-28 07:46 | 456 | 2025-11-28 07:38 | 2025-11-28 07:46 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site cleared without intervention
NOCINC0006460575 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST |  | 2025-11-26 20:52 | Aderonke Olowojoba | 2025-11-26 20:48 | 2025-11-26 20:56 | 455 | 2025-11-26 20:48 | 2025-11-26 20:56 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006455764 | External Reconciliation | Site Down | P2 | IHS_DEL_0938A | T2914 | ASB | Asaba | Delta | 3 - Low | DL0644 | SOUTH SOUTH |  | 2025-11-26 07:51 | Ayomide Akindolie | 2025-11-26 07:48 | 2025-11-26 07:55 | 455 | 2025-11-26 07:48 | 2025-11-26 07:55 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Short duration outage
NOCINC0006456214 | External Reconciliation | Site Down | P1 | IHS_DEL_1184A | DL0559 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 09:26 | Oluwatobiloba Are | 2025-11-26 09:26 | 2025-11-26 09:34 | 455 | 2025-11-26 09:26 | 2025-11-26 09:34 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Tobore Ganyoran | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006465572 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-27 14:35 | Muhammed Hashirudeen | 2025-11-27 14:33 | 2025-11-27 14:41 | 455 | 2025-11-27 14:33 | 2025-11-27 14:41 | 0:08 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006465249 | External Reconciliation | Site Down | P3 | IHS_OSU_0073B | OS4386 | IBD | Ibadan | Osun | 3 - Low | OS0712 | WEST |  | 2025-11-27 13:54 | Titus Tosin | 2025-11-27 13:53 | 2025-11-27 14:00 | 453 | 2025-11-27 13:53 | 2025-11-27 14:00 | 0:08 | IPT | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Fuel Pump | 2 / 2 | Airtel NG, MTN NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty fuel pump was worked on | Faulty fuel pump was worked on
NOCINC0006481911 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1071A | DL0439 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 17:49 | Solomon Bankole | 2025-11-29 17:42 | 2025-11-29 17:50 | 453 | 2025-11-29 17:42 | 2025-11-29 17:50 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention | Site came up without any technical intervention
NOCINC0006452941 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 00:33 | Ayomide Akindolie | 2025-11-26 00:32 | 2025-11-26 00:40 | 453 | 2025-11-26 00:32 | 2025-11-26 00:40 | 0:08 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006470319 | External Reconciliation | Site Down | P2 | IHS_ANA_1211A | AN0767 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 07:38 | Oluwatoyin Fagite | 2025-11-28 07:35 | 2025-11-28 07:43 | 450 | 2025-11-28 07:35 | 2025-11-28 07:43 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Aneke Christian | Habib Muhammed | Habib Muhammed | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006476737 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1133A | DL0683 | ASB | Asaba | Delta | 3 - Low | DL1153 | SOUTH SOUTH | CSL Fault@2025-11-29 01:48:11@DL0683_Angazi Compound Dafiogho Ughelli | 2025-11-29 02:00 | System Administrator | 2025-11-29 01:48 | 2025-11-29 01:56 | 450 | 2025-11-29 01:48 | 2025-11-29 01:56 | 0:08 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006449435 | External Reconciliation | Site Down | P3 | IHS_EDO_0978A | ED2153 | IBD | Asaba | Edo | 3 - Low | ED0709 | SOUTH SOUTH |  | 2025-11-25 15:12 | Emmanuel Faleti | 2025-11-25 15:12 | 2025-11-25 15:19 | 449 | 2025-11-25 15:12 | 2025-11-25 15:19 | 0:07 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Temperature Sensor Switch | 2 / 2 | MTN NG, Airtel NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 2 | Faulty temperature sensor switch was worked on (No diesel outage after validation) | Faulty temperature sensor switch was worked on (No diesel outage after validation)
NOCINC0006474051 | Internal Reconciliation | Site Down | P2 | IHS_AWK_0026B | AN0740 | ASB | Asaba | Anambra | 3 - Low | AN0500 | SOUTH EAST |  | 2025-11-28 17:13 | Kehinde Akinbowale | 2025-11-28 17:09 | 2025-11-28 17:16 | 449 | 2025-11-28 17:09 | 2025-11-28 17:16 | 0:07 | Tyllium NGA | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | Moses Kenechukwu | Kenneth Ogbodo | Kenneth Ogbodo | Fady Safwat | Aliyu Garuba |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Weak DG was primed to start(No diesel outage after validation) | Weak DG was primed to start(No diesel outage after validation)
NOCINC0006443759 | External Reconciliation | Site Down | P4 | IHS_ANA_1241C | AN0956 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 20:50 | Kehinde Akinbowale | 2025-11-24 20:47 | 2025-11-24 20:55 | 449 | 2025-11-24 20:47 | 2025-11-24 20:55 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006477019 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1082A | DL0083 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-29 03:54:46@DL0083_Ivorogbor | 2025-11-29 04:09 | System Administrator | 2025-11-29 03:55 | 2025-11-29 04:02 | 445 | 2025-11-29 03:55 | 2025-11-29 04:02 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006446135 | External Reconciliation | Site Down | P2 | IHS_ANA_1426H | T4822 | ASB | Asaba | Anambra | 3 - Low | AN0021 | SOUTH EAST |  | 2025-11-25 08:58 | Oluwatoyin Fagite | 2025-11-25 08:56 | 2025-11-25 09:04 | 445 | 2025-11-25 08:56 | 2025-11-25 09:04 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | NNADOZIE CASMIR |  |  | Erik Nwodo | Nwigbo Chijioke |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006450666 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 17:56 | Oluwatomisin Sogbesan | 2025-11-25 17:53 | 2025-11-25 18:01 | 444 | 2025-11-25 17:53 | 2025-11-25 18:01 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006489158 | Internal Reconciliation | Site Down | P3 | IHS_EKI_0923B | EK4552 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-30 18:59 | Ihuoma Opurum | 2025-11-30 18:59 | 2025-11-30 19:06 | 443 | 2025-11-30 18:59 | 2025-11-30 19:06 | 0:07 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Fluctuating voltage due to zero BUB, GG autorestart
NOCINC0006449197 | External Reconciliation | Site Down | P4 | IHS_OYO_1077K | OY2888 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 14:41 | Mutmainnah Saba | 2025-11-25 14:35 | 2025-11-25 14:43 | 443 | 2025-11-25 14:35 | 2025-11-25 14:43 | 0:07 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Olaitan Olajide | Habeeb Adepoju |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | low bus voltage alarm was cleared from the control module, GG auto restart
NOCINC0006485500 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1052A | DL0317 | ASB | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 09:10 | Ayomide Akindolie | 2025-11-30 09:08 | 2025-11-30 09:15 | 443 | 2025-11-30 09:08 | 2025-11-30 09:15 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006481795 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0989A | ED2108 | IBD | Asaba | Edo | 3 - Low | ED0635 | SOUTH SOUTH |  | 2025-11-29 17:29 | Ayomide Akindolie | 2025-11-29 17:29 | 2025-11-29 17:36 | 442 | 2025-11-29 17:29 | 2025-11-29 17:36 | 0:07 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | AZUBUIKE EMEH | Shagba Terkula | Emeh Azubike | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006449941 | External Reconciliation | Site Down | P3 | IHS_EDO_1061C | ED6114 | IBD | Asaba | Edo | 3 - Low | ED0953 | SOUTH SOUTH |  | 2025-11-25 16:27 | Tracy Osarumwense | 2025-11-25 16:27 | 2025-11-25 16:34 | 442 | 2025-11-25 16:27 | 2025-11-25 16:34 | 0:07 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006460540 | External Reconciliation | Site Down | P4 | IHS_ANA_1229A | AN0565 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 20:43 | Aderonke Olowojoba | 2025-11-26 20:37 | 2025-11-26 20:44 | 441 | 2025-11-26 20:37 | 2025-11-26 20:44 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention
NOCINC0006479892 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-29 13:08 | Ayomide Akindolie | 2025-11-29 13:05 | 2025-11-29 13:13 | 441 | 2025-11-29 13:05 | 2025-11-29 13:13 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006446741 | External Reconciliation | Site Down | P1 | IHS_DEL_1017A | DL0111 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 09:55 | Oluwatobiloba Are | 2025-11-25 09:53 | 2025-11-25 10:01 | 439 | 2025-11-25 09:53 | 2025-11-25 10:01 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Short duration outage, site came up without technical intervention
NOCINC0006443779 | External Reconciliation | Site Down | P3 | IHS_OND_0726E | OD4725 | IBD | Ibadan | Osun | 3 - Low | ON0617 | WEST |  | 2025-11-24 20:54 | Maureen Uchehorke | 2025-11-24 20:54 | 2025-11-24 21:01 | 438 | 2025-11-24 20:54 | 2025-11-24 21:01 | 0:07 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Aja |  |  | Ibrahim Akinpelu | Emmanuel Aja |  | Oluwafemi Iyiola | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronisation failure due to Frozen SMU was reset
NOCINC0006477459 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0928A | T3382 | IBD | Asaba | Edo | 3 - Low | ED0544 | SOUTH SOUTH |  | 2025-11-29 06:45 | Elizabeth Apata | 2025-11-29 06:44 | 2025-11-29 06:51 | 438 | 2025-11-29 06:44 | 2025-11-29 06:51 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site restored without technical intervention.
NOCINC0006472820 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1410H | AN0648 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 14:20 | Gbemisola Adedeji | 2025-11-28 14:16 | 2025-11-28 14:23 | 438 | 2025-11-28 14:16 | 2025-11-28 14:23 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006490125 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1084K | OY4079 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 22:24 | Damilola Paseda | 2025-11-30 22:21 | 2025-11-30 22:28 | 437 | 2025-11-30 22:21 | 2025-11-30 22:28 | 0:07 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Olaitan Olajide | Habeeb Adepoju |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Low bus voltage alarm was cleared from the control module | Low bus voltage alarm was cleared from the control module
NOCINC0006441675 | External Reconciliation | Site Down | P3 | IHS_EDO_0987A | ED2044 | IBD | Asaba | Edo | 3 - Low | ED0551 | SOUTH SOUTH |  | 2025-11-24 16:10 | Evelyn Emagurehor | 2025-11-24 16:09 | 2025-11-24 16:16 | 435 | 2025-11-24 16:09 | 2025-11-24 16:16 | 0:07 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 1 / 2 | Airtel NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak Refurbished DG was primed to start to restore the site. (No diesel outage after validation). | Weak Refurbished DG was primed to start to restore the site. (No diesel outage after validation).
NOCINC0006490396 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1358B | OY1036 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 23:46 | Damilola Paseda | 2025-11-30 23:44 | 2025-11-30 23:51 | 435 | 2025-11-30 23:44 | 2025-11-30 23:51 | 0:07 | SPS | Equipment Repair | Passive | ACDG Gen | ACDG - Governor | 1 / 1 | MTN NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Faulty DG governor was worked on | Faulty DG governor was worked on
NOCINC0006462763 | External Reconciliation | Site Down | P4 | IHS_ANA_1410H | AN0648 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 07:09 | Aderonke Olowojoba | 2025-11-27 07:05 | 2025-11-27 07:12 | 435 | 2025-11-27 07:05 | 2025-11-27 07:12 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006445584 | External Reconciliation | Site Down | P4 | IHS_EDO_1259B | ED1180 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 06:40 | Azeezat Badmus | 2025-11-25 06:34 | 2025-11-25 06:42 | 434 | 2025-11-25 06:34 | 2025-11-25 06:42 | 0:07 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | site cleared with no technical intervention
NOCINC0006449730 | External Reconciliation | Site Down | P2 | IHS_WAR_0743C | DL1071 | ASB | Asaba | Delta | 3 - Low | DL1075 | SOUTH SOUTH |  | 2025-11-25 15:55 | Ezinne Ubachukwu | 2025-11-25 15:52 | 2025-11-25 15:59 | 434 | 2025-11-25 15:52 | 2025-11-25 15:59 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006487523 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0743C | DL1071 | ASB | Asaba | Delta | 3 - Low | DL1075 | SOUTH SOUTH |  | 2025-11-30 14:31 | Ezinne Ubachukwu | 2025-11-30 14:24 | 2025-11-30 14:31 | 433 | 2025-11-30 14:24 | 2025-11-30 14:31 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006462498 | External Reconciliation | Site Down | P2 | IHS_ANA_1449B | AN3476 | ASB | Asaba | Anambra | 3 - Low | AN0744 | SOUTH EAST | CSL Fault@2025-11-27 05:48:09@AN3476_Madonna University Okija | 2025-11-27 06:00 | System Administrator | 2025-11-27 05:48 | 2025-11-27 05:55 | 430 | 2025-11-27 05:48 | 2025-11-27 05:55 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention
NOCINC0006483683 | Internal Reconciliation | Site Down | P1 | IHS_WAR_0907H | DL0003 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 23:05 | Muhammed Hashirudeen | 2025-11-29 22:58 | 2025-11-29 23:06 | 430 | 2025-11-29 22:58 | 2025-11-29 23:06 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006476143 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1181H | T3376 | IBD | Asaba | Edo | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-28 22:16:32@T3376_Helios towers_Benin21 | 2025-11-28 22:32 | System Administrator | 2025-11-28 22:17 | 2025-11-28 22:24 | 430 | 2025-11-28 22:17 | 2025-11-28 22:24 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006487448 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-30 14:16 | Ayomide Akindolie | 2025-11-30 14:15 | 2025-11-30 14:22 | 429 | 2025-11-30 14:15 | 2025-11-30 14:22 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006437593 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST | NodeB Unavailable@2025-11-24 03:13:06@AN0681_U | 2025-11-24 03:44 | System Administrator | 2025-11-24 03:13 | 2025-11-24 03:20 | 428 | 2025-11-24 03:13 | 2025-11-24 03:20 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006461258 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST | NE Is Disconnected@2025-11-26 22:50:29@L4844 | 2025-11-26 23:04 | System Administrator | 2025-11-26 22:54 | 2025-11-26 23:01 | 428 | 2025-11-26 22:54 | 2025-11-26 23:01 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention
NOCINC0006437582 | External Reconciliation | Site Down | P2 | IHS_OYO_0904A | T3561 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 03:28 | Babajide Ogunsola | 2025-11-24 03:25 | 2025-11-24 03:32 | 428 | 2025-11-24 03:25 | 2025-11-24 03:32 | 0:07 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | voltage fluctuation due to absence of BUB, GG auto restart
NOCINC0006473352 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH | CSL Fault@2025-11-28 15:19:14@DL0666_Our Lady Catholic Chu | 2025-11-28 15:32 | System Administrator | 2025-11-28 15:19 | 2025-11-28 15:26 | 425 | 2025-11-28 15:19 | 2025-11-28 15:26 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006448499 | External Reconciliation | Site Down | P1 | IHS_ANA_1048A | AN0024 | ASB | Asaba | Anambra | 3 - Low | AN0523 | SOUTH EAST |  | 2025-11-25 13:22 | Aderonke Olowojoba | 2025-11-25 13:18 | 2025-11-25 13:25 | 425 | 2025-11-25 13:18 | 2025-11-25 13:25 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ugochuku Agbamuche | Ugo Agamuche | Ugo Agamuche | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006478022 | Internal Reconciliation | Site Down | P3 | IHS_ANA_0912A | T4176 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 08:55 | Kehinde Akinbowale | 2025-11-29 08:52 | 2025-11-29 08:59 | 421 | 2025-11-29 08:52 | 2025-11-29 08:59 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006441601 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-24 15:55 | Aderonke Olowojoba | 2025-11-24 15:51 | 2025-11-24 15:58 | 420 | 2025-11-24 15:51 | 2025-11-24 15:58 | 0:07 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Faulty rectifier module was reset (No diesel outage after validation)
NOCINC0006460630 | External Reconciliation | Site Down | P4 | IHS_BEN_0032V | ED5182 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 21:01 | Tracy Osarumwense | 2025-11-26 21:00 | 2025-11-26 21:07 | 420 | 2025-11-26 21:00 | 2025-11-26 21:07 | 0:07 | MPI NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Control Panel | 1 / 1 | MTN NG |  | SAMUEL ASUKWO |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed to start Alarm was cleared to restore power to site. | Failed to start Alarm was cleared to restore power to site. (No diesel outage after validation).
NOCINC0006469952 | External Reconciliation | Site Down | P1 | IHS_EDO_0953A | ED2011 | IBD | Asaba | Edo | 3 - Low | ED0890 | SOUTH SOUTH |  | 2025-11-28 06:00 | Emmanuel Faleti | 2025-11-28 05:58 | 2025-11-28 06:05 | 419 | 2025-11-28 05:58 | 2025-11-28 06:05 | 0:07 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006460882 | External Reconciliation | Site Down | P2 | IHS_OSU_0929A | OS2725 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 21:47 | Victor Otugo | 2025-11-26 21:43 | 2025-11-26 21:50 | 418 | 2025-11-26 21:43 | 2025-11-26 21:50 | 0:07 | IPT | Equipment Replacement | Passive | DCDG Gen | DCDG - Compression | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | DG lost compression, engine was swapped
NOCINC0006451262 | External Reconciliation | Site Down | P3 | IHS_OND_0726E | OD4725 | IBD | Ibadan | Osun | 3 - Low | ON0617 | WEST |  | 2025-11-25 19:54 | Mary Elaigwu | 2025-11-25 19:53 | 2025-11-25 20:00 | 418 | 2025-11-25 19:53 | 2025-11-25 20:00 | 0:07 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Aja |  |  | Ibrahim Akinpelu | Emmanuel Aja |  | Oluwafemi Iyiola | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronisation failure due to Frozen SMU, Frozen SMU was reset
NOCINC0006473508 | Internal Reconciliation | Site Down | P3 | IHS_OND_0705E | OD4731 | IBD | Ibadan | Ondo | 3 - Low | ON0812 | WEST |  | 2025-11-28 16:03 | Testimony Akinyemi | 2025-11-28 16:02 | 2025-11-28 16:09 | 418 | 2025-11-28 16:02 | 2025-11-28 16:09 | 0:07 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | SHORT DURATION OUTAGE
NOCINC0006474677 | Internal Reconciliation | Site Down | P1 | IHS_WAR_0044B | DL0446 | ASB | Asaba | Delta | 3 - Low | DL0567 | SOUTH SOUTH |  | 2025-11-28 18:38 | Quadri Ogundare | 2025-11-28 18:34 | 2025-11-28 18:41 | 417 | 2025-11-28 18:34 | 2025-11-28 18:41 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Tobore Ganyoran |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006464822 | External Reconciliation | Site Down | P3 | IHS_OYO_1414B | - | - | Ibadan | Oyo | 3 - Low | OY1366 | WEST |  | 2025-11-27 12:49 | Okusanya Joseph | 2025-11-27 12:47 | 2025-11-27 12:53 | 416 | 2025-11-27 12:47 | 2025-11-27 12:53 | 0:07 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006489568 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0926C | KW4755 | IBD | Ibadan | Kwara | 3 - Low | KW0526 | WEST | 4G ZTE Sitedown@2025-11-30 20:19:37@KW0526(40526) | 2025-11-30 20:31 | System Administrator | 2025-11-30 20:20 | 2025-11-30 20:27 | 415 | 2025-11-30 20:20 | 2025-11-30 20:27 | 0:07 | IPT | Grid Supply | Passive | Grid | National Grid - Grid Incomplete Phase | 2 / 2 | Airtel NG, MTN NG |  | David Oyebamiji |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid synchronization failure due to incomplete grid phase, Grid was restored.
NOCINC0006457932 | External Reconciliation | Site Down | P3 | IHS_ANA_0739E | - | - | Asaba | Anambra | 3 - Low | AN0732 | SOUTH EAST |  | 2025-11-26 13:40 | Oluwatoyin Fagite | 2025-11-26 13:38 | 2025-11-26 13:45 | 414 | 2025-11-26 13:38 | 2025-11-26 13:45 | 0:07 | Energy Vision Nigeria | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Geoffrrey Inalegwu | Chris Idome | Chris Idome | Nosakhare Imade | Jeremiah James |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006441344 | External Reconciliation | Site Down | P3 | IHS_ANA_1224A | AN0563 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 15:11 | Ezinne Ubachukwu | 2025-11-24 15:08 | 2025-11-24 15:15 | 414 | 2025-11-24 15:08 | 2025-11-24 15:15 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006463562 | External Reconciliation | Site Down | P1 | IHS_DEL_0711E | - | - | Asaba | Delta | 3 - Low | DL0562 | SOUTH SOUTH |  | 2025-11-27 10:05 | Mary Odefemi | 2025-11-27 10:04 | 2025-11-27 10:11 | 414 | 2025-11-27 10:04 | 2025-11-27 10:11 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006487838 | Internal Reconciliation | Site Down | P3 | IHS_ANA_0903A | T4182 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-30 14:58:41@T4182_Kings Palace Nnewi | 2025-11-30 15:16 | System Administrator | 2025-11-30 14:59 | 2025-11-30 15:06 | 413 | 2025-11-30 14:59 | 2025-11-30 15:06 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obinna Festus | Festus Obinna | Festus Obinna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006487895 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0847A | T2695 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 15:23 | Tracy Osarumwense | 2025-11-30 15:23 | 2025-11-30 15:30 | 411 | 2025-11-30 15:23 | 2025-11-30 15:30 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006485924 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-30 10:30 | Ayomide Akindolie | 2025-11-30 10:27 | 2025-11-30 10:34 | 409 | 2025-11-30 10:27 | 2025-11-30 10:34 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006465327 | External Reconciliation | Site Down | P4 | IHS_EDO_1176H | ED2068 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 14:03 | Elizabeth Apata | 2025-11-27 13:59 | 2025-11-27 14:05 | 409 | 2025-11-27 13:59 | 2025-11-27 14:05 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006443687 | External Reconciliation | Site Down | P2 | IHS_KWA_0902A | KW4577 | IBD | Ibadan | Kwara | 3 - Low | KW0457 | WEST |  | 2025-11-24 20:35 | Praise Okezie | 2025-11-24 20:35 | 2025-11-24 20:42 | 408 | 2025-11-24 20:35 | 2025-11-24 20:42 | 0:07 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006473369 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1380H | AN0130 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 15:35 | Abundance Otunola | 2025-11-28 15:31 | 2025-11-28 15:38 | 408 | 2025-11-28 15:31 | 2025-11-28 15:38 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006477855 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0953A | ED2011 | IBD | Asaba | Edo | 3 - Low | ED0890 | SOUTH SOUTH |  | 2025-11-29 08:27 | Azeezat Badmus | 2025-11-29 08:25 | 2025-11-29 08:32 | 407 | 2025-11-29 08:25 | 2025-11-29 08:32 | 0:07 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | site cleared with no technical intervention
NOCINC0006482521 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0926A | OS2709 | IBD | Ibadan | Osun | 3 - Low | OS0755 | WEST |  | 2025-11-29 19:41 | Ayodele Oludare | 2025-11-29 19:40 | 2025-11-29 19:46 | 407 | 2025-11-29 19:40 | 2025-11-29 19:46 | 0:07 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006437527 | External Reconciliation | Site Down | P4 | IHS_EDO_0849A | T3298 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 02:45 | Muhammed Hashirudeen | 2025-11-24 02:44 | 2025-11-24 02:50 | 407 | 2025-11-24 02:44 | 2025-11-24 02:50 | 0:07 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - High Engine Temp - Coolant Level Issue | 1 / 1 | MTN NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | DG high temperature due to low coolant level, coolant was added (No diesel outage after validation)
NOCINC0006460950 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST | CSL Fault@2025-11-26 21:51:17@T4844_Oyeagu Junction | 2025-11-26 22:03 | System Administrator | 2025-11-26 21:51 | 2025-11-26 21:58 | 407 | 2025-11-26 21:51 | 2025-11-26 21:58 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006442328 | External Reconciliation | Site Down | P2 | IHS_WAR_0928B | DL3323 | ASB | Asaba | Delta | 3 - Low | DL0890 | SOUTH SOUTH |  | 2025-11-24 17:01 | Ezinne Ubachukwu | 2025-11-24 16:58 | 2025-11-24 17:05 | 407 | 2025-11-24 16:58 | 2025-11-24 17:05 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006457391 | External Reconciliation | Site Down | P2 | IHS_ANA_1276C | AN0581 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 12:19 | Oluwatoyin Fagite | 2025-11-26 12:16 | 2025-11-26 12:23 | 407 | 2025-11-26 12:16 | 2025-11-26 12:23 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Sunday Kenneth | Sunday Ede | Sunday Ede | Henry Wanogho | Ifeanyi Chukusa |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006482613 | Internal Reconciliation | Site Down | P3 | IHS_OND_0726E | OD4725 | IBD | Ibadan | Osun | 3 - Low | ON0617 | WEST |  | 2025-11-29 20:00 | Testimony Akinyemi | 2025-11-29 19:57 | 2025-11-29 20:04 | 405 | 2025-11-29 19:57 | 2025-11-29 20:04 | 0:07 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Aja |  |  | Ibrahim Akinpelu | Emmanuel Aja |  | Oluwafemi Iyiola | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronisation failure due to Frozen SMU and power restored
NOCINC0006473690 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1358B | OY1036 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 16:23 | Damilola Paseda | 2025-11-28 16:18 | 2025-11-28 16:25 | 405 | 2025-11-28 16:18 | 2025-11-28 16:25 | 0:07 | SPS | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 1 / 1 | MTN NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | PPM was carried out at the site with IHSREF/251112709371057408557 | PPM was carried out at the site with IHSREF/251112709371057408557
NOCINC0006438741 | External Reconciliation | Site Down | P3 | IHS_DEL_0896A | T2777 | ASB | Asaba | Delta | 3 - Low | DL0250 | SOUTH SOUTH |  | 2025-11-24 08:58 | Ezinne Ubachukwu | 2025-11-24 08:58 | 2025-11-24 09:04 | 405 | 2025-11-24 08:58 | 2025-11-24 09:04 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006440957 | External Reconciliation | Site Down | P3 | IHS_EDO_1312B | - | - | Asaba | Edo | 3 - Low | ED0818 | SOUTH SOUTH |  | 2025-11-24 14:35 | Tracy Osarumwense | 2025-11-24 14:35 | 2025-11-24 14:42 | 404 | 2025-11-24 14:35 | 2025-11-24 14:42 | 0:07 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 2 | Site came up with no technical intervention (No diesel outage after validation) | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006472653 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-28 13:56 | Bukola Olabanji | 2025-11-28 13:54 | 2025-11-28 14:01 | 404 | 2025-11-28 13:54 | 2025-11-28 14:01 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006471427 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0947A | T2279 | ASB | Asaba | Delta | 3 - Low | DL0251 | SOUTH SOUTH |  | 2025-11-28 10:41 | Abundance Otunola | 2025-11-28 10:40 | 2025-11-28 10:47 | 404 | 2025-11-28 10:40 | 2025-11-28 10:47 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006462635 | External Reconciliation | Site Down | P1 | IHS_WAR_0728B | DL1007 | ASB | Asaba | Delta | 3 - Low | DL0727 | SOUTH SOUTH |  | 2025-11-27 06:31 | Tracy Osarumwense | 2025-11-27 06:31 | 2025-11-27 06:38 | 404 | 2025-11-27 06:31 | 2025-11-27 06:38 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006450132 | External Reconciliation | Site Down | P4 | IHS_ANA_1241C | AN0956 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 16:43 | Oluwatoyin Fagite | 2025-11-25 16:39 | 2025-11-25 16:45 | 404 | 2025-11-25 16:39 | 2025-11-25 16:45 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006467937 | External Reconciliation | Site Down | P2 | IHS_WAR_0879H | T2907 | ASB | Asaba | Delta | 3 - Low | DL0635 | SOUTH SOUTH |  | 2025-11-27 21:04 | Oluwatobiloba Are | 2025-11-27 21:04 | 2025-11-27 21:11 | 403 | 2025-11-27 21:04 | 2025-11-27 21:11 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006439271 | External Reconciliation | Site Down | P2 | IHS_EDO_0976A | ED2148 | IBD | Asaba | Edo | 3 - Low | ED0659 | SOUTH SOUTH |  | 2025-11-24 10:35 | Evelyn Emagurehor | 2025-11-24 10:33 | 2025-11-24 10:40 | 403 | 2025-11-24 10:33 | 2025-11-24 10:40 | 0:07 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Frequency | 1 / 2 | Airtel NG |  | Hammed Abubakar |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | DG underfrequency, governor was adjusted (No diesel outage after validation) | DG underfrequency, governor was adjusted (No diesel outage after validation)
NOCINC0006467414 | External Reconciliation | Site Down | P4 | IHS_OYO_0037C | OY4304 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 19:30 | Titus Tosin | 2025-11-27 19:29 | 2025-11-27 19:35 | 402 | 2025-11-27 19:29 | 2025-11-27 19:35 | 0:07 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | hybrid synchronisation failure, Dg was powered manually
NOCINC0006439267 | External Reconciliation | Site Down | P3 | IHS_EDO_1113B | ED6190 | ASB | Asaba | Edo | 3 - Low | ED0565 | SOUTH SOUTH |  | 2025-11-24 10:35 | Tracy Osarumwense | 2025-11-24 10:35 | 2025-11-24 10:42 | 402 | 2025-11-24 10:35 | 2025-11-24 10:42 | 0:07 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Samuel Asukwo |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006475061 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-28 19:46 | Bukola Olabanji | 2025-11-28 19:44 | 2025-11-28 19:51 | 401 | 2025-11-28 19:44 | 2025-11-28 19:51 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006437699 | External Reconciliation | Site Down | P3 | IHS_ANA_1054A | AN0128 | ASB | Asaba | Anambra | 3 - Low | AN0716 | SOUTH EAST | NodeB Unavailable@2025-11-24 03:59:19@AN0716_U | 2025-11-24 04:24 | System Administrator | 2025-11-24 03:59 | 2025-11-24 04:06 | 401 | 2025-11-24 03:59 | 2025-11-24 04:06 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006460497 | External Reconciliation | Site Down | P2 | IHS_DEL_0964A | DL2989 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 20:34 | Tracy Osarumwense | 2025-11-26 20:34 | 2025-11-26 20:41 | 401 | 2025-11-26 20:34 | 2025-11-26 20:41 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006475200 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0765A | T3131 | IBD | Ibadan | Kwara | 3 - Low | KW0362 | WEST |  | 2025-11-28 20:08 | Okusanya Joseph | 2025-11-28 20:08 | 2025-11-28 20:14 | 401 | 2025-11-28 20:08 | 2025-11-28 20:14 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006464649 | External Reconciliation | Site Down | P4 | IHS_EDO_1176H | ED2068 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 12:25 | Elizabeth Apata | 2025-11-27 12:22 | 2025-11-27 12:29 | 400 | 2025-11-27 12:22 | 2025-11-27 12:29 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006465447 | External Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-27 14:18 | Bukola Olabanji | 2025-11-27 14:16 | 2025-11-27 14:23 | 400 | 2025-11-27 14:16 | 2025-11-27 14:23 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006461881 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST | CSL Fault@2025-11-27 01:00:27@T4844_Oyeagu Junction | 2025-11-27 01:13 | System Administrator | 2025-11-27 01:08 | 2025-11-27 01:15 | 400 | 2025-11-27 01:08 | 2025-11-27 01:15 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006460325 | External Reconciliation | Site Down | P1 | IHS_ANA_0920A | T4844 | ASB | Asaba | Anambra | 3 - Low | AN0960 | SOUTH EAST | CSL Fault@2025-11-26 20:06:02@T4844_Oyeagu Junction | 2025-11-26 20:18 | System Administrator | 2025-11-26 20:06 | 2025-11-26 20:13 | 400 | 2025-11-26 20:06 | 2025-11-26 20:13 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006477857 | Internal Reconciliation | Site Down | P3 | IHS_OND_0705E | OD4731 | IBD | Ibadan | Ondo | 3 - Low | ON0812 | WEST |  | 2025-11-29 08:28 | Testimony Akinyemi | 2025-11-29 08:25 | 2025-11-29 08:32 | 399 | 2025-11-29 08:25 | 2025-11-29 08:32 | 0:07 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | SHORT DURATION OUTAGE
NOCINC0006483992 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0882A | T3556 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 00:37 | Mutmainnah Saba | 2025-11-30 00:33 | 2025-11-30 00:40 | 399 | 2025-11-30 00:33 | 2025-11-30 00:40 | 0:07 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Olaitan Olajide |  | Yunus Ololade | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | voltage fluctuation weak BUB on site. GG auto start.
NOCINC0006487314 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-30 13:54 | Tracy Osarumwense | 2025-11-30 13:54 | 2025-11-30 14:01 | 399 | 2025-11-30 13:54 | 2025-11-30 14:01 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006456571 | External Reconciliation | Site Down | P3 | IHS_ANA_0903A | T4182 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 10:24 | Oluwatoyin Fagite | 2025-11-26 10:23 | 2025-11-26 10:30 | 398 | 2025-11-26 10:23 | 2025-11-26 10:30 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obinna Festus | Festus Obinna | Festus Obinna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006456778 | External Reconciliation | Site Down | P2 | IHS_EDO_1193H | ED2097 | IBD | Asaba | Edo | 3 - Low | ED0498 | SOUTH SOUTH |  | 2025-11-26 11:02 | Azeezat Badmus | 2025-11-26 10:59 | 2025-11-26 11:06 | 398 | 2025-11-26 10:59 | 2025-11-26 11:06 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | OYEYODE MUIDEEN |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | site cleared with no intervention
NOCINC0006474081 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1084K | OY4079 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 17:19 | Damilola Paseda | 2025-11-28 17:17 | 2025-11-28 17:24 | 397 | 2025-11-28 17:17 | 2025-11-28 17:24 | 0:07 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Olaitan Olajide | Habeeb Adepoju |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Low voltage alarm was cleared from the control module | Low voltage alarm was cleared from the control module
NOCINC0006487058 | Internal Reconciliation | Site Down | P3 | IHS_EDO_1216B | ED6219 | IBD | Asaba | Edo | 3 - Low | ED0750 | SOUTH SOUTH |  | 2025-11-30 13:16 | Evelyn Emagurehor | 2025-11-30 13:16 | 2025-11-30 13:23 | 397 | 2025-11-30 13:16 | 2025-11-30 13:23 | 0:07 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Asukwo Effiong | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006441622 | External Reconciliation | Site Down | P2 | IHS_DEL_1175A | DL0676 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 16:01 | Ayomide Akindolie | 2025-11-24 16:01 | 2025-11-24 16:08 | 397 | 2025-11-24 16:01 | 2025-11-24 16:08 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006474385 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1152A | DL0566 | ASB | Asaba | Delta | 3 - Low | DL0820 | SOUTH SOUTH |  | 2025-11-28 18:02 | Bukola Olabanji | 2025-11-28 17:57 | 2025-11-28 18:04 | 397 | 2025-11-28 17:57 | 2025-11-28 18:04 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Kenneth Oboniye |  |  | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 2 | Short duration outage
NOCINC0006439465 | External Reconciliation | Site Down | P3 | IHS_KWA_0939C | KW6391 | IBD | Ibadan | Kwara | 3 - Low | KW0598 | WEST |  | 2025-11-24 11:12 | Precious Attah | 2025-11-24 11:11 | 2025-11-24 11:18 | 396 | 2025-11-24 11:11 | 2025-11-24 11:18 | 0:07 | IPT | Grid Supply | Passive | Grid | National Grid - Grid Outage Issue | 2 / 2 | MTN NG, Airtel NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to Grid outage issue, DG powered manually.
NOCINC0006484331 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0792C | DL1055 | ASB | Asaba | Delta | 3 - Low | DL0634 | SOUTH SOUTH | 4G ZTE Sitedown@2025-11-30 02:59:13@DL0634(80634) | 2025-11-30 03:11 | System Administrator | 2025-11-30 02:59 | 2025-11-30 03:06 | 395 | 2025-11-30 02:59 | 2025-11-30 03:06 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Kenneth Oboniye |  |  | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006442436 | External Reconciliation | Site Down | P4 | IHS_EDO_0950A | ED2018 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 17:18 | Oluwatomisin Sogbesan | 2025-11-24 17:14 | 2025-11-24 17:21 | 395 | 2025-11-24 17:14 | 2025-11-24 17:21 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006441322 | External Reconciliation | Site Down | P3 | IHS_DEL_1251B | - | - | Asaba | Delta | 3 - Low | DL0936 | SOUTH SOUTH |  | 2025-11-24 15:07 | Ayokunle Samuel | 2025-11-24 15:07 | 2025-11-24 15:14 | 394 | 2025-11-24 15:07 | 2025-11-24 15:14 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Osayamwen Eghosa |  |  | Erik Nwodo | John Wekpe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site inter-fail and clear without any technical intervention.
NOCINC0006474044 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1388H | AN0762 | ASB | Asaba | Anambra | 3 - Low | AN0380 | SOUTH EAST |  | 2025-11-28 17:10 | Abundance Otunola | 2025-11-28 17:07 | 2025-11-28 17:14 | 394 | 2025-11-28 17:07 | 2025-11-28 17:14 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006457604 | External Reconciliation | Site Down | P3 | IHS_EDO_0978A | ED2153 | IBD | Asaba | Edo | 3 - Low | ED0709 | SOUTH SOUTH |  | 2025-11-26 12:48 | Azeezat Badmus | 2025-11-26 12:46 | 2025-11-26 12:53 | 394 | 2025-11-26 12:46 | 2025-11-26 12:53 | 0:07 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 4 | site cleared with no technical intervention
NOCINC0006464113 | External Reconciliation | Site Down | P1 | IHS_EDO_1083C | ED5339 | IBD | Asaba | Edo | 3 - Low | ED0666 | SOUTH SOUTH |  | 2025-11-27 11:30 | Muhammed Hashirudeen | 2025-11-27 11:30 | 2025-11-27 11:36 | 393 | 2025-11-27 11:30 | 2025-11-27 11:36 | 0:07 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006473241 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1169A | AN0584 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 15:20 | Gbemisola Adedeji | 2025-11-28 15:13 | 2025-11-28 15:20 | 392 | 2025-11-28 15:13 | 2025-11-28 15:20 | 0:07 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006459691 | External Reconciliation | Site Down | P1 | IHS_ANA_1009A | AN4811 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 18:26 | Oluwatoyin Fagite | 2025-11-26 18:25 | 2025-11-26 18:31 | 391 | 2025-11-26 18:25 | 2025-11-26 18:31 | 0:07 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006465375 | External Reconciliation | Site Down | P4 | IHS_EDO_1101C | ED6122 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 14:10 | Bukola Olabanji | 2025-11-27 14:08 | 2025-11-27 14:15 | 390 | 2025-11-27 14:08 | 2025-11-27 14:15 | 0:06 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006437514 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-24 02:40 | Gbemisola Adedeji | 2025-11-24 02:36 | 2025-11-24 02:43 | 389 | 2025-11-24 02:36 | 2025-11-24 02:43 | 0:06 | Huawei | Fuel Outage (Probable) | Passive | ACDG Gen | ACDG - Injector Pump | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Faulty injector was worked on (No diesel outage after validation) | Faulty injector was worked on (No diesel outage after validation)
NOCINC0006464765 | External Reconciliation | Site Down | P4 | IHS_EDO_1048C | ED6125 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 12:38 | Mary Odefemi | 2025-11-27 12:32 | 2025-11-27 12:39 | 388 | 2025-11-27 12:32 | 2025-11-27 12:39 | 0:06 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006484399 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1235B | - | - | Asaba | Delta | 3 - Low | DL0956 | SOUTH SOUTH | 4G ZTE Sitedown@2025-11-30 03:12:11@DL0956(80956) | 2025-11-30 03:25 | System Administrator | 2025-11-30 03:12 | 2025-11-30 03:19 | 387 | 2025-11-30 03:12 | 2025-11-30 03:19 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Kehinde Adekanbi |  |  | Erik Nwodo | John Wekpe |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006467836 | External Reconciliation | Site Down | P1 | IHS_EDO_0958A | ED2002 | IBD | Asaba | Edo | 3 - Low | ED0454 | SOUTH SOUTH |  | 2025-11-27 20:44 | Oluwatobiloba Are | 2025-11-27 20:41 | 2025-11-27 20:48 | 387 | 2025-11-27 20:41 | 2025-11-27 20:48 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Imomoh Sylvanus |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Short duration outage, site came up without technical intervention
NOCINC0006463742 | External Reconciliation | Site Down | P3 | IHS_WAR_0751C | DL1084 | ASB | Asaba | Delta | 3 - Low | DL0625 | SOUTH SOUTH |  | 2025-11-27 10:35 | Mary Odefemi | 2025-11-27 10:35 | 2025-11-27 10:41 | 387 | 2025-11-27 10:35 | 2025-11-27 10:41 | 0:06 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Low oil pressure, oil was added (No diesel outage after validation)
NOCINC0006488334 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1214B | DL4087 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 16:35 | Ayokunle Samuel | 2025-11-30 16:30 | 2025-11-30 16:37 | 387 | 2025-11-30 16:30 | 2025-11-30 16:37 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006482917 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-29 20:47:36@T2719_30 Emevor Orogun Road | 2025-11-29 21:01 | System Administrator | 2025-11-29 20:53 | 2025-11-29 21:05 | 687 | 2025-11-29 20:58 | 2025-11-29 21:05 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006438326 | External Reconciliation | Site Down | P2 | IHS_AWK_0026B | AN0740 | ASB | Asaba | Anambra | 3 - Low | AN0500 | SOUTH EAST | CSL Fault@2025-11-24 07:30:20@AN0740_Grace Of God Mission Umuokpu | 2025-11-24 07:44 | System Administrator | 2025-11-24 07:40 | 2025-11-24 07:47 | 387 | 2025-11-24 07:40 | 2025-11-24 07:47 | 0:06 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Moses Kenechukwu | Kenneth Ogbodo | Kenneth Ogbodo | Fady Safwat | Aliyu Garuba |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Frozen rectifier module was reset (No diesel outage after validation). | Frozen rectifier module was reset (No diesel outage after validation).
NOCINC0006442705 | External Reconciliation | Site Down | P4 | IHS_EDO_1247B | ED5524 | IBD | Asaba | Edo | 3 - Low | ED1138 | SOUTH SOUTH |  | 2025-11-24 18:02 | Oluwatomisin Sogbesan | 2025-11-24 18:00 | 2025-11-24 18:06 | 386 | 2025-11-24 18:00 | 2025-11-24 18:06 | 0:06 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation). | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation).
NOCINC0006461888 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 01:16 | Tracy Osarumwense | 2025-11-27 01:16 | 2025-11-27 01:23 | 386 | 2025-11-27 01:16 | 2025-11-27 01:23 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006465691 | External Reconciliation | Site Down | P3 | IHS_ANA_1402H | AN0006 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 14:52 | Gbemisola Adedeji | 2025-11-27 14:49 | 2025-11-27 14:55 | 386 | 2025-11-27 14:49 | 2025-11-27 14:55 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006477441 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-29 06:25:26@T2719_30 Emevor Orogun Road | 2025-11-29 06:39 | System Administrator | 2025-11-29 06:35 | 2025-11-29 06:41 | 385 | 2025-11-29 06:35 | 2025-11-29 06:41 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006446525 | External Reconciliation | Site Down | P2 | IHS_ANA_1426H | T4822 | ASB | Asaba | Anambra | 3 - Low | AN0021 | SOUTH EAST |  | 2025-11-25 09:22 | Oluwatoyin Fagite | 2025-11-25 09:19 | 2025-11-25 09:25 | 384 | 2025-11-25 09:19 | 2025-11-25 09:25 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | NNADOZIE CASMIR |  |  | Erik Nwodo | Nwigbo Chijioke |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006446986 | External Reconciliation | Site Down | P1 | IHS_EDO_0953A | ED2011 | IBD | Asaba | Edo | 3 - Low | ED0890 | SOUTH SOUTH |  | 2025-11-25 10:26 | Emmanuel Faleti | 2025-11-25 10:21 | 2025-11-25 10:27 | 383 | 2025-11-25 10:21 | 2025-11-25 10:27 | 0:06 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006490286 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-30 23:01 | Praise Okezie | 2025-11-30 23:01 | 2025-11-30 23:07 | 383 | 2025-11-30 23:01 | 2025-11-30 23:07 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006443906 | External Reconciliation | Site Down | P4 | IHS_ANA_1241C | AN0956 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 21:13 | Kehinde Akinbowale | 2025-11-24 21:09 | 2025-11-24 21:16 | 382 | 2025-11-24 21:09 | 2025-11-24 21:16 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006452059 | External Reconciliation | Site Down | P3 | IHS_ANA_0739E | - | - | Asaba | Anambra | 3 - Low | AN0732 | SOUTH EAST |  | 2025-11-25 21:35 | Abundance Otunola | 2025-11-25 21:30 | 2025-11-25 21:37 | 381 | 2025-11-25 21:30 | 2025-11-25 21:37 | 0:06 | Energy Vision Nigeria | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Geoffrrey Inalegwu | Chris Idome | Chris Idome | Nosakhare Imade | Jeremiah James |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006477880 | Internal Reconciliation | Site Down | P3 | IHS_ANA_0819A | T4081 | ASB | Asaba | Anambra | 3 - Low | AN1147 | SOUTH EAST |  | 2025-11-29 08:35 | Abundance Otunola | 2025-11-29 08:33 | 2025-11-29 08:39 | 381 | 2025-11-29 08:33 | 2025-11-29 08:39 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 3 | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006457008 | External Reconciliation | Site Down | P1 | IHS_ANA_1009A | AN4811 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 11:26 | Akachukwu Ugwu | 2025-11-26 11:23 | 2025-11-26 11:30 | 381 | 2025-11-26 11:23 | 2025-11-26 11:30 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006451296 | External Reconciliation | Site Down | P2 | IHS_DEL_0964A | DL2989 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 19:58 | Tracy Osarumwense | 2025-11-25 19:58 | 2025-11-25 20:05 | 381 | 2025-11-25 19:58 | 2025-11-25 20:05 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006489168 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1247B | ED5524 | IBD | Asaba | Edo | 3 - Low | ED1138 | SOUTH SOUTH |  | 2025-11-30 19:01 | Oluwatomisin Sogbesan | 2025-11-30 18:59 | 2025-11-30 19:05 | 380 | 2025-11-30 18:59 | 2025-11-30 19:05 | 0:06 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation). | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation).
NOCINC0006465627 | External Reconciliation | Site Down | P3 | IHS_OYO_1182H | OY4345 | IBD | Ibadan | Oyo | 3 - Low | OY0986 | WEST |  | 2025-11-27 14:45 | Mutmainnah Saba | 2025-11-27 14:43 | 2025-11-27 14:49 | 379 | 2025-11-27 14:43 | 2025-11-27 14:49 | 0:06 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to weak BUB, DG powered automatically
NOCINC0006450698 | External Reconciliation | Site Down | P2 | IHS_BEN_0754E | ED2182 | IBD | Asaba | Edo | 3 - Low | ED0694 | SOUTH SOUTH |  | 2025-11-25 18:05 | Oluwatomisin Sogbesan | 2025-11-25 18:04 | 2025-11-25 18:11 | 379 | 2025-11-25 18:04 | 2025-11-25 18:11 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | EKPU SUNDAY |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006449163 | External Reconciliation | Site Down | P1 | IHS_ANA_0909A | T4088 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 14:38 | Oluwatoyin Fagite | 2025-11-25 14:36 | 2025-11-25 14:42 | 379 | 2025-11-25 14:36 | 2025-11-25 14:42 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | NNADOZIE CASMIR |  |  | Erik Nwodo | Nwigbo Chijioke |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006477816 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-29 08:17 | Mary Odefemi | 2025-11-29 08:14 | 2025-11-29 08:21 | 379 | 2025-11-29 08:14 | 2025-11-29 08:21 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006455066 | External Reconciliation | Site Down | P1 | IHS_EDO_1223B | ED2181 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 05:15 | Evelyn Emagurehor | 2025-11-26 05:13 | 2025-11-26 05:19 | 379 | 2025-11-26 05:13 | 2025-11-26 05:19 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006462372 | External Reconciliation | Site Down | P4 | IHS_EDO_0950A | ED2018 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 05:24 | Oluwatomisin Sogbesan | 2025-11-27 05:22 | 2025-11-27 05:28 | 378 | 2025-11-27 05:22 | 2025-11-27 05:28 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006463463 | External Reconciliation | Site Down | P1 | IHS_ONT_0048B | AN0726 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 09:49 | Uthman Akinola | 2025-11-27 09:49 | 2025-11-27 09:56 | 378 | 2025-11-27 09:49 | 2025-11-27 09:56 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Emmanuel Emmanuel | Henry Ubawuchi | Henry Ubawuchi | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006487088 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-30 13:21 | Tracy Osarumwense | 2025-11-30 13:19 | 2025-11-30 13:26 | 378 | 2025-11-30 13:19 | 2025-11-30 13:26 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006464061 | External Reconciliation | Site Down | P1 | IHS_DEL_1084A | DL0601 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 11:19 | Femi Olanipekun | 2025-11-27 11:17 | 2025-11-27 11:23 | 377 | 2025-11-27 11:17 | 2025-11-27 11:23 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006438230 | External Reconciliation | Site Down | P1 | IHS_ANA_1050A | AN0032 | ASB | Asaba | Anambra | 3 - Low | AN0731 | SOUTH EAST |  | 2025-11-24 07:15 | Gbemisola Adedeji | 2025-11-24 07:10 | 2025-11-24 07:16 | 375 | 2025-11-24 07:10 | 2025-11-24 07:16 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Anwah Chike |  |  | Erik Nwodo | Nwigbo Chijioke |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006466331 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-27 16:21 | Bukola Olabanji | 2025-11-27 16:18 | 2025-11-27 16:24 | 375 | 2025-11-27 16:18 | 2025-11-27 16:24 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006462901 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-27 07:22:20@T0286_Hotel Marina Off Sokoto road O | 2025-11-27 07:35 | System Administrator | 2025-11-27 07:29 | 2025-11-27 07:35 | 375 | 2025-11-27 07:29 | 2025-11-27 07:35 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006482245 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1269C | AN0044 | ASB | Asaba | Anambra | 3 - Low | AN0794 | SOUTH EAST |  | 2025-11-29 18:54 | Solomon Bankole | 2025-11-29 18:49 | 2025-11-29 18:55 | 373 | 2025-11-29 18:49 | 2025-11-29 18:55 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006460021 | External Reconciliation | Site Down | P4 | IHS_EDO_0950A | ED2018 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 19:15 | Emmanuel Faleti | 2025-11-26 19:12 | 2025-11-26 19:18 | 373 | 2025-11-26 19:12 | 2025-11-26 19:18 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006448723 | External Reconciliation | Site Down | P3 | IHS_ANA_1223A | AN0706 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 13:45 | Aderonke Olowojoba | 2025-11-25 13:42 | 2025-11-25 13:48 | 373 | 2025-11-25 13:42 | 2025-11-25 13:48 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006445377 | External Reconciliation | Site Down | P1 | IHS_OYO_1041A | OY2368 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 05:19 | Praise Okezie | 2025-11-25 05:17 | 2025-11-25 05:23 | 373 | 2025-11-25 05:17 | 2025-11-25 05:23 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Short duration outage, site was up with no intervention.
NOCINC0006445519 | External Reconciliation | Site Down | P1 | IHS_KWA_0824A | T3959 | IBD | Ibadan | Kwara | 3 - Low | KW0495 | WEST |  | 2025-11-25 06:11 | Praise Okezie | 2025-11-25 06:09 | 2025-11-25 06:15 | 372 | 2025-11-25 06:09 | 2025-11-25 06:15 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Short duration outage, site was up with no intervention.
NOCINC0006440314 | External Reconciliation | Site Down | P4 | IHS_EDO_1181H | T3376 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 13:14 | Oluwatomisin Sogbesan | 2025-11-24 13:12 | 2025-11-24 13:18 | 372 | 2025-11-24 13:12 | 2025-11-24 13:18 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006463402 | External Reconciliation | Site Down | P3 | IHS_ONT_0006B | AN0316 | ASB | Asaba | Anambra | 3 - Low | AN0588 | SOUTH EAST |  | 2025-11-27 09:41 | Akachukwu Ugwu | 2025-11-27 09:37 | 2025-11-27 09:44 | 372 | 2025-11-27 09:37 | 2025-11-27 09:44 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006483885 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0725B | DL0987 | ASB | Asaba | Delta | 3 - Low | DL0737 | SOUTH SOUTH |  | 2025-11-29 23:58 | Bukola Olabanji | 2025-11-29 23:57 | 2025-11-30 00:03 | 372 | 2025-11-29 23:57 | 2025-11-30 00:03 | 0:06 | BJ Bison NGA | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on.
NOCINC0006467568 | External Reconciliation | Site Down | P3 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-27 19:56 | Bukola Olabanji | 2025-11-27 19:49 | 2025-11-27 19:56 | 372 | 2025-11-27 19:49 | 2025-11-27 19:56 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006489301 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0823A | EK2201 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-30 19:24 | Oluwadara Bankole | 2025-11-30 19:22 | 2025-11-30 19:28 | 371 | 2025-11-30 19:22 | 2025-11-30 19:28 | 0:06 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 1 / 1 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting RCA from FSE
NOCINC0006480120 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1120A | DL0718 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 13:37 | Ayokunle Samuel | 2025-11-29 13:33 | 2025-11-29 13:39 | 371 | 2025-11-29 13:33 | 2025-11-29 13:39 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention.
NOCINC0006465539 | External Reconciliation | Site Down | P4 | IHS_ANA_1084A | AN0312 | ASB | Asaba | Anambra | 3 - Low | AN0772 | SOUTH EAST |  | 2025-11-27 14:30 | Gbemisola Adedeji | 2025-11-27 14:26 | 2025-11-27 14:33 | 371 | 2025-11-27 14:26 | 2025-11-27 14:33 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006473131 | Internal Reconciliation | Site Down | P4 | IHS_IBA_0028V | OY2880 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 15:04 | Damilola Paseda | 2025-11-28 15:00 | 2025-11-28 15:07 | 370 | 2025-11-28 15:00 | 2025-11-28 15:07 | 0:06 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Module | 1 / 1 | MTN NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to failed CSU, CSU was reset | Hybrid synchronization failure due to failed CSU, CSU was reset
NOCINC0006479880 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1084K | OY4079 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 13:06 | Damilola Paseda | 2025-11-29 13:01 | 2025-11-29 13:07 | 370 | 2025-11-29 13:01 | 2025-11-29 13:07 | 0:06 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Olaitan Olajide | Habeeb Adepoju |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Voltage fluctuation due to weak BUB, GG auto-restarted. | Voltage fluctuation due to weak BUB, GG auto-restarted.
NOCINC0006483147 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST | WCDMA BASE STATION OUT OF USE@2025-11-29 20:59:50@W_KW0477 | 2025-11-29 21:36 | System Administrator | 2025-11-29 21:00 | 2025-11-29 21:06 | 370 | 2025-11-29 21:00 | 2025-11-29 21:06 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006463452 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 09:47 | Elizabeth Apata | 2025-11-27 09:45 | 2025-11-27 09:49 | 283 | 2025-11-27 09:45 | 2025-11-27 09:51 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site restored without intervention.
NOCINC0006451325 | External Reconciliation | Site Down | P3 | IHS_OYO_1414B | - | - | Ibadan | Oyo | 3 - Low | OY1366 | WEST | WCDMA BASE STATION OUT OF USE@2025-11-25 19:43:25@W_OY1366 | 2025-11-25 20:04 | System Administrator | 2025-11-25 19:43 | 2025-11-25 19:50 | 369 | 2025-11-25 19:43 | 2025-11-25 19:50 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006438211 | External Reconciliation | Site Down | P4 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-24 07:11 | Bukola Olabanji | 2025-11-24 07:09 | 2025-11-24 07:15 | 368 | 2025-11-24 07:09 | 2025-11-24 07:15 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006441983 | External Reconciliation | Site Down | P4 | IHS_ANA_0998A | T4851 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 16:30 | Aderonke Olowojoba | 2025-11-24 16:27 | 2025-11-24 16:33 | 368 | 2025-11-24 16:27 | 2025-11-24 16:33 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Aneke Christian | Habib Muhammed | Habib Muhammed | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006471383 | Internal Reconciliation | Site Down | P3 | IHS_EKW_0004B | AN0896 | ASB | Asaba | Anambra | 3 - Low | AN0669 | SOUTH EAST |  | 2025-11-28 10:36 | Gbemisola Adedeji | 2025-11-28 10:32 | 2025-11-28 10:38 | 367 | 2025-11-28 10:32 | 2025-11-28 10:38 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Harrison Igbinedion | Harrison Igbinedion | Harrison Igbinedion | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006463098 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 08:33 | Bukola Olabanji | 2025-11-27 08:31 | 2025-11-27 08:40 | 547 | 2025-11-27 08:31 | 2025-11-27 08:37 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Short duration outage
NOCINC0006483649 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0725B | DL0987 | ASB | Asaba | Delta | 3 - Low | DL0737 | SOUTH SOUTH |  | 2025-11-29 22:56 | Bukola Olabanji | 2025-11-29 22:54 | 2025-11-29 23:00 | 367 | 2025-11-29 22:54 | 2025-11-29 23:00 | 0:06 | BJ Bison NGA | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Faulty ATS load contactor was worked on
NOCINC0006471174 | Internal Reconciliation | Site Down | P4 | IHS_OND_0830A | T3846 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 10:07 | Olawale Adeyemo | 2025-11-28 10:04 | 2025-11-28 10:10 | 367 | 2025-11-28 10:04 | 2025-11-28 10:10 | 0:06 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Start failure alarm was cleared.
NOCINC0006486637 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0835A | EK3388 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-30 12:25 | Ihuoma Opurum | 2025-11-30 12:25 | 2025-11-30 12:31 | 366 | 2025-11-30 12:25 | 2025-11-30 12:31 | 0:06 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Engine Temp - Faulty Water Pump | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | High engine temperature due to faulty water pump. Water pump was replaced.
NOCINC0006458438 | External Reconciliation | Site Down | P4 | IHS_EDO_0009B | ED5009 | IBD | Asaba | Edo | 3 - Low | - | - | CSL Fault@2025-11-26 14:45:55@ED5009_Damolua Igbanke | 2025-11-26 14:58 | System Administrator | 2025-11-26 14:53 | 2025-11-26 14:59 | 366 | 2025-11-26 14:53 | 2025-11-26 14:59 | 0:06 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | MICHAEL TONDO | Micheal Tondo | Micheal Tondo | Cornelius Yakubu | Elochukwu Umeohana |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006475139 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0736A | T3105 | IBD | Ibadan | Kwara | 3 - Low | KW0352 | WEST |  | 2025-11-28 19:59 | Okusanya Joseph | 2025-11-28 19:59 | 2025-11-28 20:05 | 365 | 2025-11-28 19:59 | 2025-11-28 20:05 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 2 | Short duration outage, site was up with no intervention.
NOCINC0006467317 | External Reconciliation | Site Down | P4 | IHS_WAR_0960B | DL0734 | ASB | Asaba | Delta | 3 - Low | - | - | eNodeB S1 Control Plane Transmission Interruption@2025-11-27 18:53:28@LDL0734 | 2025-11-27 19:08 | System Administrator | 2025-11-27 19:01 | 2025-11-27 19:07 | 365 | 2025-11-27 19:01 | 2025-11-27 19:07 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006454355 | External Reconciliation | Site Down | P4 | IHS_DEL_1218B | - | - | Asaba | Delta | 3 - Low | DL0903 | SOUTH SOUTH |  | 2025-11-26 01:16 | Ayomide Akindolie | 2025-11-26 01:16 | 2025-11-26 01:22 | 365 | 2025-11-26 01:16 | 2025-11-26 01:22 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006464044 | External Reconciliation | Site Down | P4 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-27 11:14 | Bukola Olabanji | 2025-11-27 11:13 | 2025-11-27 11:19 | 365 | 2025-11-27 11:13 | 2025-11-27 11:19 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006472112 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0911A | T3370 | IBD | Asaba | Edo | 3 - Low | ED0686 | SOUTH SOUTH |  | 2025-11-28 12:21 | Muhammed Hashirudeen | 2025-11-28 12:19 | 2025-11-28 12:25 | 364 | 2025-11-28 12:19 | 2025-11-28 12:25 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site restored without intervention.
NOCINC0006482166 | Internal Reconciliation | Site Down | P3 | IHS_EDO_1233B | ED5512 | IBD | Asaba | Edo | 3 - Low | ED0858 | SOUTH SOUTH |  | 2025-11-29 18:38 | Evelyn Emagurehor | 2025-11-29 18:37 | 2025-11-29 18:43 | 364 | 2025-11-29 18:37 | 2025-11-29 18:43 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006440954 | External Reconciliation | Site Down | P1 | IHS_ANA_1049A | AN0103 | ASB | Asaba | Anambra | 3 - Low | AN0526 | SOUTH EAST |  | 2025-11-24 14:34 | Abundance Otunola | 2025-11-24 14:32 | 2025-11-24 14:38 | 363 | 2025-11-24 14:32 | 2025-11-24 14:38 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Femi Balogun | Femi Balogun | Femi Balogun | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006465724 | External Reconciliation | Site Down | P2 | IHS_WAR_0794C | DL1109 | ASB | Asaba | Delta | 3 - Low | DL0663 | SOUTH SOUTH |  | 2025-11-27 14:58 | Bukola Olabanji | 2025-11-27 14:58 | 2025-11-27 15:04 | 362 | 2025-11-27 14:58 | 2025-11-27 15:04 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006456695 | External Reconciliation | Site Down | P2 | IHS_WAR_0059C | DL0852 | ASB | Asaba | Delta | 3 - Low | DL0572 | SOUTH SOUTH |  | 2025-11-26 10:45 | Mary Odefemi | 2025-11-26 10:44 | 2025-11-26 10:50 | 362 | 2025-11-26 10:44 | 2025-11-26 10:50 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Short duration outage
NOCINC0006458683 | External Reconciliation | Site Down | P2 | IHS_EDO_1193H | ED2097 | IBD | Asaba | Edo | 3 - Low | ED0498 | SOUTH SOUTH |  | 2025-11-26 15:34 | Emmanuel Faleti | 2025-11-26 15:33 | 2025-11-26 15:39 | 361 | 2025-11-26 15:33 | 2025-11-26 15:39 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | OYEYODE MUIDEEN |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006468746 | External Reconciliation | Site Down | P4 | IHS_OND_0830A | T3846 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 00:02 | Mary Elaigwu | 2025-11-28 00:02 | 2025-11-28 00:08 | 361 | 2025-11-28 00:02 | 2025-11-28 00:08 | 0:06 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Start failure alarm was cleared .. DCGG RESTARTED
NOCINC0006459966 | External Reconciliation | Site Down | P3 | IHS_OND_0726E | OD4725 | IBD | Ibadan | Osun | 3 - Low | ON0617 | WEST |  | 2025-11-26 19:08 | Mary Elaigwu | 2025-11-26 19:08 | 2025-11-26 19:14 | 361 | 2025-11-26 19:08 | 2025-11-26 19:14 | 0:06 | Inhouse | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | Emmanuel Aja |  |  | Ibrahim Akinpelu | Emmanuel Aja |  | Oluwafemi Iyiola | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronisation failure due to frozen SMU, SMU was reset
NOCINC0006478137 | Internal Reconciliation | Site Down | P2 | IHS_EDO_1193H | ED2097 | IBD | Asaba | Edo | 3 - Low | ED0498 | SOUTH SOUTH |  | 2025-11-29 09:19 | Evelyn Emagurehor | 2025-11-29 09:18 | 2025-11-29 09:24 | 361 | 2025-11-29 09:18 | 2025-11-29 09:24 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | OYEYODE MUIDEEN |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006475029 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0736A | T3105 | IBD | Ibadan | Kwara | 3 - Low | KW0352 | WEST |  | 2025-11-28 19:42 | Okusanya Joseph | 2025-11-28 19:42 | 2025-11-28 19:48 | 360 | 2025-11-28 19:42 | 2025-11-28 19:48 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006477588 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-29 07:22 | Mary Odefemi | 2025-11-29 07:21 | 2025-11-29 07:27 | 360 | 2025-11-29 07:21 | 2025-11-29 07:27 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006456340 | External Reconciliation | Site Down | P4 | IHS_OND_0830A | T3846 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 09:46 | Iyesioluwa Ola | 2025-11-26 09:46 | 2025-11-26 09:52 | 360 | 2025-11-26 09:46 | 2025-11-26 09:52 | 0:06 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | start failure, DCGG was restarted
NOCINC0006460689 | External Reconciliation | Site Down | P2 | IHS_DEL_0964A | DL2989 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 21:10 | Tracy Osarumwense | 2025-11-26 21:10 | 2025-11-26 21:16 | 360 | 2025-11-26 21:10 | 2025-11-26 21:16 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006478337 | Internal Reconciliation | Site Down | P2 | IHS_EDO_1193H | ED2097 | IBD | Asaba | Edo | 3 - Low | ED0498 | SOUTH SOUTH |  | 2025-11-29 09:45 | Evelyn Emagurehor | 2025-11-29 09:44 | 2025-11-29 09:50 | 360 | 2025-11-29 09:44 | 2025-11-29 09:50 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | OYEYODE MUIDEEN |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006488113 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 16:02 | Evelyn Emagurehor | 2025-11-30 16:01 | 2025-11-30 16:07 | 360 | 2025-11-30 16:01 | 2025-11-30 16:07 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006444381 | External Reconciliation | Site Down | P3 | IHS_OYO_1187H | - | - | Ibadan | Oyo | 3 - Low | OY0773 | WEST |  | 2025-11-24 22:32 | Damilola Paseda | 2025-11-24 22:26 | 2025-11-24 22:32 | 360 | 2025-11-24 22:26 | 2025-11-24 22:32 | 0:06 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Mohammed Soliu |  | Abdulraman Odunola | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006478055 | Internal Reconciliation | Site Down | P1 | IHS_EKI_0735A | T3463 | IBD | Ibadan | Ekiti | 3 - Low | EK0533 | WEST |  | 2025-11-29 09:02 | Testimony Akinyemi | 2025-11-29 09:01 | 2025-11-29 09:07 | 360 | 2025-11-29 09:01 | 2025-11-29 09:07 | 0:06 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Akinboyewa Akinola | Adebayo Babatunde |  | Abiola Adegbiji | Babalola Babajide |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | SHORT DURATION OUTAGE
NOCINC0006482996 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1334B | OY1045 | IBD | Ibadan | Oyo | 3 - Low | OY1599 | WEST |  | 2025-11-29 21:14 | Mutmainnah Saba | 2025-11-29 21:11 | 2025-11-29 21:17 | 359 | 2025-11-29 21:11 | 2025-11-29 21:17 | 0:06 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | BANKOLE SODIQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006449586 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 15:35 | Oluwatomisin Sogbesan | 2025-11-25 15:33 | 2025-11-25 15:39 | 359 | 2025-11-25 15:33 | 2025-11-25 15:39 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006471411 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0843A | T3623 | IBD | Ibadan | Osun | 3 - Low | OS0725 | WEST |  | 2025-11-28 10:40 | Mutmainnah Saba | 2025-11-28 10:38 | 2025-11-28 10:44 | 359 | 2025-11-28 10:38 | 2025-11-28 10:44 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Bayo Nathaniel |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006483691 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0874A | KW2380 | ABJ | Ibadan | Niger | 3 - Low | - | - |  | 2025-11-29 23:08 | Okusanya Joseph | 2025-11-29 23:08 | 2025-11-29 23:14 | 359 | 2025-11-29 23:08 | 2025-11-29 23:14 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Victor Agahiu |  |  | Soye West | Oboh Oseyeieomo |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006486031 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0960A | DL2994 | ASB | Asaba | Delta | 3 - Low | DL0799 | SOUTH SOUTH |  | 2025-11-30 10:58 | Ayomide Akindolie | 2025-11-30 10:56 | 2025-11-30 11:02 | 359 | 2025-11-30 10:56 | 2025-11-30 11:02 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006489290 | Internal Reconciliation | Site Down | P1 | IHS_OND_0788A | T3407/T3484 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 19:23 | Babajide Ogunsola | 2025-11-30 19:21 | 2025-11-30 19:27 | 359 | 2025-11-30 19:21 | 2025-11-30 19:27 | 0:06 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Current | 1 / 1 | MTN NG |  | Daniel Akinfenwa |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | GG Voltage fluctuation due to High current, voltage was adjusted
NOCINC0006471333 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0739E | OS4702 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 10:27 | Praise Okezie | 2025-11-28 10:25 | 2025-11-28 10:31 | 359 | 2025-11-28 10:25 | 2025-11-28 10:31 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006463465 | External Reconciliation | Site Down | P4 | IHS_DEL_1207B | DL4078 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 09:50 | Uthman Akinola | 2025-11-27 09:46 | 2025-11-27 09:52 | 358 | 2025-11-27 09:46 | 2025-11-27 09:52 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006473412 | Internal Reconciliation | Site Down | P4 | IHS_OSU_1059B | OS4807 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 15:45 | Valentine Adinnu | 2025-11-28 15:43 | 2025-11-28 15:49 | 358 | 2025-11-28 15:43 | 2025-11-28 15:49 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Tiamiyu Mustapha |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006487252 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0850A | T2740 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 13:38 | Tracy Osarumwense | 2025-11-30 13:38 | 2025-11-30 13:44 | 358 | 2025-11-30 13:38 | 2025-11-30 13:44 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kenneth Oboniye |  |  | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006458228 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 14:24 | Azeezat Badmus | 2025-11-26 14:21 | 2025-11-26 14:27 | 358 | 2025-11-26 14:21 | 2025-11-26 14:27 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | site cleared with no technical intervention
NOCINC0006478689 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1204B | DL4068 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 10:43 | Solomon Bankole | 2025-11-29 10:41 | 2025-11-29 10:47 | 358 | 2025-11-29 10:41 | 2025-11-29 10:47 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention. | Site inter failed and cleared without any technical intervention.
NOCINC0006464064 | External Reconciliation | Site Down | P2 | IHS_EDO_0747A | T0161 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 11:20 | Elizabeth Apata | 2025-11-27 11:12 | 2025-11-27 11:24 | 717 | 2025-11-27 11:18 | 2025-11-27 11:24 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006485270 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1071A | DL0439 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 08:24 | Uthman Akinola | 2025-11-30 08:22 | 2025-11-30 08:26 | 236 | 2025-11-30 08:20 | 2025-11-30 08:26 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site inter-fail and clear without any technical intervention.
NOCINC0006456578 | External Reconciliation | Site Down | P2 | IHS_EDO_1193H | ED2097 | IBD | Asaba | Edo | 3 - Low | ED0498 | SOUTH SOUTH |  | 2025-11-26 10:26 | Azeezat Badmus | 2025-11-26 10:25 | 2025-11-26 10:31 | 356 | 2025-11-26 10:25 | 2025-11-26 10:31 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | OYEYODE MUIDEEN |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006480110 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 13:35 | Ayokunle Samuel | 2025-11-29 13:32 | 2025-11-29 13:38 | 356 | 2025-11-29 13:32 | 2025-11-29 13:38 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention.
NOCINC0006439240 | External Reconciliation | Site Down | P2 | IHS_OSU_1047B | OS4769 | IBD | Ibadan | Osun | 3 - Low | OS0742 | WEST |  | 2025-11-24 10:30 | Oluwatomisin Ogunleye | 2025-11-24 10:29 | 2025-11-24 10:35 | 356 | 2025-11-24 10:29 | 2025-11-24 10:35 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Abdulsalami Onukaba Onukaba |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site restored without technical intervention
NOCINC0006450465 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 17:22 | Oluwatobiloba Are | 2025-11-25 17:22 | 2025-11-25 17:28 | 355 | 2025-11-25 17:22 | 2025-11-25 17:28 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006465286 | External Reconciliation | Site Down | P2 | IHS_EDO_1178H | ED2052 | IBD | Asaba | Edo | 3 - Low | ED0486 | SOUTH SOUTH |  | 2025-11-27 13:58 | Bukola Olabanji | 2025-11-27 13:58 | 2025-11-27 14:04 | 354 | 2025-11-27 13:58 | 2025-11-27 14:04 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Imomoh Sylvanus |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006462915 | External Reconciliation | Site Down | P4 | IHS_OYO_1011A | T3599 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 07:40 | Victor Otugo | 2025-11-27 07:37 | 2025-11-27 07:43 | 354 | 2025-11-27 07:37 | 2025-11-27 07:43 | 0:06 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Azeez Salami |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006468300 | External Reconciliation | Site Down | P3 | IHS_ANA_1316B | AN3147 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 22:08 | Oluwatoyin Fagite | 2025-11-27 22:07 | 2025-11-27 22:13 | 353 | 2025-11-27 22:07 | 2025-11-27 22:13 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006446074 | External Reconciliation | Site Down | P3 | IHS_EDO_1334B | - | - | Asaba | Edo | 3 - Low | ED0850 | SOUTH SOUTH |  | 2025-11-25 08:48 | Emmanuel Faleti | 2025-11-25 08:45 | 2025-11-25 08:51 | 352 | 2025-11-25 08:45 | 2025-11-25 08:51 | 0:06 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Mohammed Idris |  |  | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006450071 | External Reconciliation | Site Down | P4 | IHS_EKI_0771A | T3745 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-25 16:36 | Tunji Adejumo | 2025-11-25 16:36 | 2025-11-25 16:42 | 351 | 2025-11-25 16:36 | 2025-11-25 16:42 | 0:06 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006486021 | Internal Reconciliation | Site Down | P3 | IHS_OYO_0980A | T3573 | IBD | Ibadan | Oyo | 3 - Low | OY1111 | WEST |  | 2025-11-30 10:53 | Yewande Adeagbo | 2025-11-30 10:48 | 2025-11-30 10:54 | 351 | 2025-11-30 10:48 | 2025-11-30 10:54 | 0:06 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Muhammad Aliyu |  |  | Paul Akpomie | Muhammad Aliyu |  | Uche Kanu | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Short duration outage. Site was restored without intervention.
NOCINC0006451012 | External Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-25 19:03 | Marvellous Emecheta | 2025-11-25 18:58 | 2025-11-25 19:04 | 351 | 2025-11-25 18:58 | 2025-11-25 19:04 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006486853 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-30 12:49 | Tracy Osarumwense | 2025-11-30 12:48 | 2025-11-30 12:54 | 351 | 2025-11-30 12:48 | 2025-11-30 12:54 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006474968 | Internal Reconciliation | Site Down | P1 | IHS_ONT_0048B | AN0726 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 19:29 | Abundance Otunola | 2025-11-28 19:24 | 2025-11-28 19:30 | 351 | 2025-11-28 19:24 | 2025-11-28 19:30 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Emmanuel Emmanuel | Henry Ubawuchi | Henry Ubawuchi | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006443381 | External Reconciliation | Site Down | P4 | IHS_OYO_1084K | OY4079 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 19:41 | Victor Otugo | 2025-11-24 19:39 | 2025-11-24 19:44 | 350 | 2025-11-24 19:39 | 2025-11-24 19:44 | 0:06 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Olaitan Olajide | Habeeb Adepoju |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | voltage fluctuation due to weak bub at site
NOCINC0006437832 | External Reconciliation | Site Down | P2 | IHS_IBA_0764E | OY2963 | IBD | Ibadan | Oyo | 3 - Low | OY0940 | WEST |  | 2025-11-24 05:00 | Mutmainnah Saba | 2025-11-24 04:58 | 2025-11-24 05:04 | 350 | 2025-11-24 04:58 | 2025-11-24 05:04 | 0:06 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Lukman Mohammed |  | Yunus Ololade | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Short duration outage, site restored without intervention
NOCINC0006473331 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0766A | T3144 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 15:31 | Praise Okezie | 2025-11-28 15:27 | 2025-11-28 15:33 | 350 | 2025-11-28 15:27 | 2025-11-28 15:33 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006441993 | External Reconciliation | Site Down | P2 | IHS_ILO_0003B | KW2385 | IBD | Ibadan | Kwara | 3 - Low | KW0428 | WEST |  | 2025-11-24 16:31 | Precious Attah | 2025-11-24 16:30 | 2025-11-24 16:36 | 350 | 2025-11-24 16:30 | 2025-11-24 16:36 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006489323 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1071C | ED6141 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 19:34 | Evelyn Emagurehor | 2025-11-30 19:33 | 2025-11-30 19:39 | 350 | 2025-11-30 19:33 | 2025-11-30 19:39 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006446533 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 09:23 | Oluwadara Bankole | 2025-11-25 09:21 | 2025-11-25 09:27 | 349 | 2025-11-25 09:21 | 2025-11-25 09:27 | 0:06 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006483125 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1119A | AN0681 | ASB | Asaba | Anambra | 3 - Low | AN0854 | SOUTH EAST |  | 2025-11-29 21:33 | Gbemisola Adedeji | 2025-11-29 21:29 | 2025-11-29 21:35 | 349 | 2025-11-29 21:29 | 2025-11-29 21:35 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ThankGod Amadi | Femi Balogun | Femi Balogun | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006472609 | Internal Reconciliation | Site Down | P4 | IHS_ILO_0731E | KW1471 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 13:44 | Praise Okezie | 2025-11-28 13:42 | 2025-11-28 13:48 | 348 | 2025-11-28 13:42 | 2025-11-28 13:48 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006486032 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1047A | DL0417 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 10:58 | Tracy Osarumwense | 2025-11-30 10:58 | 2025-11-30 11:04 | 348 | 2025-11-30 10:58 | 2025-11-30 11:04 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006465934 | External Reconciliation | Site Down | P4 | IHS_ANA_1172A | AN0516 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 15:28 | Gbemisola Adedeji | 2025-11-27 15:25 | 2025-11-27 15:31 | 348 | 2025-11-27 15:25 | 2025-11-27 15:31 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obinna Festus | Festus Obinna | Festus Obinna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006458245 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-26 14:28 | Oluwatoyin Fagite | 2025-11-26 14:26 | 2025-11-26 14:31 | 347 | 2025-11-26 14:26 | 2025-11-26 14:31 | 0:06 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 1 | Weak DG was primed to start (No diesel outage after validation) | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006447163 | External Reconciliation | Site Down | P4 | IHS_ANA_1273C | AN0434 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 10:54 | Oluwatoyin Fagite | 2025-11-25 10:54 | 2025-11-25 11:00 | 347 | 2025-11-25 10:54 | 2025-11-25 11:00 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | NNADOZIE CASMIR |  |  | Erik Nwodo | Nwigbo Chijioke |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006475716 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1442B | AN3470 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 21:20 | Femi Olanipekun | 2025-11-28 21:20 | 2025-11-28 21:26 | 347 | 2025-11-28 21:20 | 2025-11-28 21:26 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006463249 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 09:06 | Muhammed Hashirudeen | 2025-11-27 09:04 | 2025-11-27 09:09 | 346 | 2025-11-27 09:04 | 2025-11-27 09:09 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site restored without intervention.
NOCINC0006458450 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 15:00 | Emmanuel Faleti | 2025-11-26 14:59 | 2025-11-26 15:05 | 346 | 2025-11-26 14:59 | 2025-11-26 15:05 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006458116 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-26 14:12 | Oluwatoyin Fagite | 2025-11-26 14:10 | 2025-11-26 14:16 | 346 | 2025-11-26 14:10 | 2025-11-26 14:16 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006474732 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0042B | DL0624 | ASB | Asaba | Delta | 3 - Low | DL0809 | SOUTH SOUTH |  | 2025-11-28 18:46 | Quadri Ogundare | 2025-11-28 18:45 | 2025-11-28 18:51 | 346 | 2025-11-28 18:45 | 2025-11-28 18:51 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006464047 | External Reconciliation | Site Down | P3 | IHS_IBA_0091C | OY4100 | IBD | Ibadan | Oyo | 3 - Low | OY1114 | WEST |  | 2025-11-27 11:14 | Mutmainnah Saba | 2025-11-27 11:12 | 2025-11-27 11:18 | 345 | 2025-11-27 11:12 | 2025-11-27 11:18 | 0:06 | SPS | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 2 / 2 | MTN NG, Airtel NG |  | BANKOLE SODIQ |  | Filani Oluwatobi | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty Rectifier was Worked On
NOCINC0006443330 | External Reconciliation | Site Down | P1 | IHS_EDO_0798A | T3252 | IBD | Asaba | Edo | 3 - Low | ED0184 | SOUTH SOUTH |  | 2025-11-24 19:31 | Evelyn Emagurehor | 2025-11-24 19:30 | 2025-11-24 19:36 | 345 | 2025-11-24 19:30 | 2025-11-24 19:36 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006489924 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1174A | AN0558 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 21:42 | Kehinde Akinbowale | 2025-11-30 21:39 | 2025-11-30 21:45 | 345 | 2025-11-30 21:39 | 2025-11-30 21:45 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006446606 | External Reconciliation | Site Down | P2 | IHS_IBA_0764E | OY2963 | IBD | Ibadan | Oyo | 3 - Low | OY0940 | WEST |  | 2025-11-25 09:33 | Victor Otugo | 2025-11-25 09:32 | 2025-11-25 09:38 | 345 | 2025-11-25 09:32 | 2025-11-25 09:38 | 0:06 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Lukman Mohammed |  | Yunus Ololade | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006443302 | External Reconciliation | Site Down | P2 | IHS_KWA_0823A | T3958 | IBD | Ibadan | Kwara | 3 - Low | - | - | NE Is Disconnected@2025-11-24 19:12:15@L3958 | 2025-11-24 19:26 | System Administrator | 2025-11-24 19:12 | 2025-11-24 19:18 | 345 | 2025-11-24 19:12 | 2025-11-24 19:18 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006484717 | Internal Reconciliation | Site Down | P2 | IHS_ANA_1445B | AN3482 | ASB | Asaba | Anambra | 3 - Low | AN0936 | SOUTH EAST |  | 2025-11-30 05:35 | Gbemisola Adedeji | 2025-11-30 05:30 | 2025-11-30 05:36 | 345 | 2025-11-30 05:30 | 2025-11-30 05:36 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Anwah Chike |  |  | Erik Nwodo | Nwigbo Chijioke |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006482870 | Internal Reconciliation | Site Down | P2 | IHS_EDO_1028A | ED4923 | IBD | Asaba | Edo | 3 - Low | ED1071 | South South |  | 2025-11-29 20:53 | Muhammed Hashirudeen | 2025-11-29 20:53 | 2025-11-29 20:58 | 344 | 2025-11-29 20:53 | 2025-11-29 20:58 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | MTN NG |  | EKPU SUNDAY |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006487298 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0057B | ED5096 | IBD | Asaba | Edo | 3 - Low | ED0664 | SOUTH SOUTH |  | 2025-11-30 13:48 | Evelyn Emagurehor | 2025-11-30 13:48 | 2025-11-30 13:54 | 344 | 2025-11-30 13:48 | 2025-11-30 13:54 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ismail Adeyinka |  |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006454944 | External Reconciliation | Site Down | P2 | IHS_OYO_1278H | OY4461 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 04:46 | Azeezat Adekunle | 2025-11-26 04:44 | 2025-11-26 04:50 | 344 | 2025-11-26 04:44 | 2025-11-26 04:50 | 0:06 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006461684 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 00:31 | Oluwatomisin Sogbesan | 2025-11-27 00:29 | 2025-11-27 00:35 | 344 | 2025-11-27 00:29 | 2025-11-27 00:35 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006450453 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 17:19 | Emmanuel Faleti | 2025-11-25 17:19 | 2025-11-25 17:25 | 343 | 2025-11-25 17:19 | 2025-11-25 17:25 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006461411 | External Reconciliation | Site Down | P1 | IHS_OYO_0006B | OY2982 | IBD | Ibadan | Oyo | 3 - Low | OY0755 | WEST | 4G ZTE Sitedown@2025-11-26 23:27:20@OY0755(30755) | 2025-11-26 23:40 | System Administrator | 2025-11-26 23:28 | 2025-11-26 23:33 | 343 | 2025-11-26 23:28 | 2025-11-26 23:33 | 0:06 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | Airtel NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006450710 | External Reconciliation | Site Down | P2 | IHS_EDO_1193H | ED2097 | IBD | Asaba | Edo | 3 - Low | ED0498 | SOUTH SOUTH |  | 2025-11-25 18:08 | Emmanuel Faleti | 2025-11-25 18:06 | 2025-11-25 18:12 | 343 | 2025-11-25 18:06 | 2025-11-25 18:12 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | OYEYODE MUIDEEN |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006467814 | External Reconciliation | Site Down | P3 | IHS_ANA_1061A | AN4165 | ASB | Asaba | Anambra | 3 - Low | AN0863 | SOUTH EAST |  | 2025-11-27 20:41 | Oluwatoyin Fagite | 2025-11-27 20:39 | 2025-11-27 20:44 | 342 | 2025-11-27 20:39 | 2025-11-27 20:44 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Harrison Igbinedion | Harrison Igbinedion | Harrison Igbinedion | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006451374 | External Reconciliation | Site Down | P2 | IHS_OSU_0739E | OS4702 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 20:10 | Precious Attah | 2025-11-25 20:09 | 2025-11-25 20:15 | 342 | 2025-11-25 20:09 | 2025-11-25 20:15 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006448234 | External Reconciliation | Site Down | P3 | IHS_EDO_1196H | ED5129 | IBD | Asaba | Edo | 3 - Low | ED0626 | SOUTH SOUTH |  | 2025-11-25 12:47 | Emmanuel Faleti | 2025-11-25 12:46 | 2025-11-25 12:52 | 342 | 2025-11-25 12:46 | 2025-11-25 12:52 | 0:06 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | MTN NG, Airtel NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak DG was primed to start (No diesel outage after validation) | Weak DG was primed to start (No diesel outage after validation)
NOCINC0006486570 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0798A | T3252 | IBD | Asaba | Edo | 3 - Low | ED0184 | SOUTH SOUTH |  | 2025-11-30 12:15 | Evelyn Emagurehor | 2025-11-30 12:15 | 2025-11-30 12:20 | 342 | 2025-11-30 12:15 | 2025-11-30 12:20 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006485358 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0794C | DL1109 | ASB | Asaba | Delta | 3 - Low | DL0663 | SOUTH SOUTH | NE Is Disconnected@2025-11-30 08:25:52@NDL1109 | 2025-11-30 08:40 | System Administrator | 2025-11-30 08:32 | 2025-11-30 08:32 | 1 | 2025-11-30 08:42 | 2025-11-30 08:47 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006444196 | External Reconciliation | Site Down | P4 | IHS_EDO_1247B | ED5524 | IBD | Asaba | Edo | 3 - Low | ED1138 | SOUTH SOUTH |  | 2025-11-24 21:55 | Azeezat Badmus | 2025-11-24 21:52 | 2025-11-24 21:57 | 341 | 2025-11-24 21:52 | 2025-11-24 21:57 | 0:06 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | faulty rectifier module was worked on (No diesel outage after validation)
NOCINC0006458214 | External Reconciliation | Site Down | P2 | IHS_BEN_0082C | ED5208 | IBD | Asaba | Edo | 3 - Low | ED0608 | SOUTH SOUTH |  | 2025-11-26 14:23 | Emmanuel Faleti | 2025-11-26 14:20 | 2025-11-26 14:26 | 341 | 2025-11-26 14:20 | 2025-11-26 14:26 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adeoti Ogunbiyi |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006452148 | External Reconciliation | Site Down | P2 | IHS_OYO_0740E | OY2851 | IBD | Ibadan | Oyo | 3 - Low | OY1377 | WEST |  | 2025-11-25 21:53 | Azeezat Adekunle | 2025-11-25 21:51 | 2025-11-25 21:57 | 340 | 2025-11-25 21:51 | 2025-11-25 21:57 | 0:06 | Energy Vision Nigeria | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Lawal Wahab |  |  | Oladotun Ogunleye | Banje Oluwaseun |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006436513 | External Reconciliation | Site Down | P3 | IHS_ANA_1061A | AN4165 | ASB | Asaba | Anambra | 3 - Low | AN0863 | SOUTH EAST | CSL Fault@2025-11-23 23:59:10@AN4165_Ogboji Road Ekwulobia Aguluchuk | 2025-11-24 00:11 | System Administrator | 2025-11-23 23:59 | 2025-11-24 00:06 | 390 | 2025-11-24 | 2025-11-24 00:06 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Harrison Igbinedion | Harrison Igbinedion | Harrison Igbinedion | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006487974 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0847A | T2695 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 15:36 | Tracy Osarumwense | 2025-11-30 15:36 | 2025-11-30 15:42 | 340 | 2025-11-30 15:36 | 2025-11-30 15:42 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006471607 | Internal Reconciliation | Site Down | P2 | IHS_IBA_0764E | OY2963 | IBD | Ibadan | Oyo | 3 - Low | OY0940 | WEST |  | 2025-11-28 11:02 | Mutmainnah Saba | 2025-11-28 11:00 | 2025-11-28 11:06 | 340 | 2025-11-28 11:00 | 2025-11-28 11:06 | 0:06 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Lukman Mohammed |  | Yunus Ololade | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Short duration outage, site restored without intervention
NOCINC0006462264 | External Reconciliation | Site Down | P4 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-27 04:42 | Tracy Osarumwense | 2025-11-27 04:42 | 2025-11-27 04:48 | 339 | 2025-11-27 04:42 | 2025-11-27 04:48 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006461613 | External Reconciliation | Site Down | P4 | IHS_OYO_1011A | T3599 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 00:14 | Ademola Alabi | 2025-11-27 00:14 | 2025-11-27 00:19 | 338 | 2025-11-27 00:14 | 2025-11-27 00:19 | 0:06 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Azeez Salami |  |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006487474 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0855A | T2737 | ASB | Asaba | Delta | 3 - Low | DL0243 | SOUTH SOUTH | Site Abis control link broken@2025-11-30 13:34:37@DL0243 | 2025-11-30 14:19 | System Administrator | 2025-11-30 13:35 | 2025-11-30 14:40 | 3938 | 2025-11-30 14:35 | 2025-11-30 14:40 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006468533 | External Reconciliation | Site Down | P4 | IHS_EDO_1002A | ED4937 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 22:53 | Emmanuel Faleti | 2025-11-27 22:52 | 2025-11-27 22:58 | 338 | 2025-11-27 22:52 | 2025-11-27 22:58 | 0:06 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | GODFREY NATHANIEL |  | Nathaniel Godfrey | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006438142 | External Reconciliation | Site Down | P2 | IHS_ANA_1445B | AN3482 | ASB | Asaba | Anambra | 3 - Low | AN0936 | SOUTH EAST |  | 2025-11-24 06:43 | Gbemisola Adedeji | 2025-11-24 06:39 | 2025-11-24 06:45 | 337 | 2025-11-24 06:39 | 2025-11-24 06:45 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Anwah Chike |  |  | Erik Nwodo | Nwigbo Chijioke |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006488083 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0875A | OS3995 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 15:56 | Precious Attah | 2025-11-30 15:55 | 2025-11-30 16:01 | 337 | 2025-11-30 15:55 | 2025-11-30 16:01 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006451274 | External Reconciliation | Site Down | P3 | IHS_OYO_1414B | - | - | Ibadan | Oyo | 3 - Low | OY1366 | WEST |  | 2025-11-25 19:55 | Precious Attah | 2025-11-25 19:55 | 2025-11-25 20:01 | 337 | 2025-11-25 19:55 | 2025-11-25 20:01 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | 25-11-2025 20:01:09
NOCINC0006467207 | External Reconciliation | Site Down | P4 | IHS_KWA_0768A | T3147 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 18:50 | Titus Tosin | 2025-11-27 18:46 | 2025-11-27 18:52 | 337 | 2025-11-27 18:46 | 2025-11-27 18:52 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oyenini Olalekan |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006485300 | Internal Reconciliation | Site Down | P2 | IHS_WAR_0794C | DL1109 | ASB | Asaba | Delta | 3 - Low | DL0663 | SOUTH SOUTH |  | 2025-11-30 08:31 | Tracy Osarumwense | 2025-11-30 08:26 | 2025-11-30 08:31 | 336 | 2025-11-30 08:26 | 2025-11-30 08:31 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006449718 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 15:53 | Emmanuel Faleti | 2025-11-25 15:51 | 2025-11-25 15:57 | 336 | 2025-11-25 15:51 | 2025-11-25 15:57 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006459155 | External Reconciliation | Site Down | P2 | IHS_DEL_0731E | DL1019 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-26 16:34:40@DL1019_Magnes Onyibe Street | 2025-11-26 16:47 | System Administrator | 2025-11-26 16:44 | 2025-11-26 16:49 | 336 | 2025-11-26 16:44 | 2025-11-26 16:49 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006482270 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0785A | T3163 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-29 19:00 | Azeezat Adekunle | 2025-11-29 18:59 | 2025-11-29 19:04 | 335 | 2025-11-29 18:59 | 2025-11-29 19:04 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Site came up without any technical intervention
NOCINC0006475009 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-28 19:39 | Quadri Ogundare | 2025-11-28 19:35 | 2025-11-28 19:40 | 335 | 2025-11-28 19:35 | 2025-11-28 19:40 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006451445 | External Reconciliation | Site Down | P2 | IHS_DEL_0964A | DL2989 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 20:15 | Ayomide Akindolie | 2025-11-25 20:14 | 2025-11-25 20:19 | 334 | 2025-11-25 20:14 | 2025-11-25 20:19 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006448923 | External Reconciliation | Site Down | P3 | IHS_ONT_0067B | AN0853 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 14:04 | Ezinne Ubachukwu | 2025-11-25 14:00 | 2025-11-25 14:06 | 334 | 2025-11-25 14:00 | 2025-11-25 14:06 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Idowu Dare |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006465322 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 14:02 | Elizabeth Apata | 2025-11-27 13:59 | 2025-11-27 14:04 | 333 | 2025-11-27 13:59 | 2025-11-27 14:04 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006470545 | External Reconciliation | Site Down | P2 | IHS_OND_1035C | OD6238 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 08:28 | Testimony Akinyemi | 2025-11-28 08:25 | 2025-11-28 08:31 | 333 | 2025-11-28 08:25 | 2025-11-28 08:31 | 0:06 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Anawanti Kingsley | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | SHORT DURATION OUTAGE
NOCINC0006450800 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 18:27 | Emmanuel Faleti | 2025-11-25 18:26 | 2025-11-25 18:32 | 333 | 2025-11-25 18:26 | 2025-11-25 18:32 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006464336 | External Reconciliation | Site Down | P4 | IHS_ANA_1410H | AN0648 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 11:49 | Akachukwu Ugwu | 2025-11-27 11:47 | 2025-11-27 11:52 | 332 | 2025-11-27 11:47 | 2025-11-27 11:52 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006474392 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1001A | T4870 | ASB | Asaba | Anambra | 3 - Low | AN0530 | SOUTH EAST |  | 2025-11-28 18:04 | Abundance Otunola | 2025-11-28 18:02 | 2025-11-28 18:07 | 332 | 2025-11-28 18:02 | 2025-11-28 18:07 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006478670 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0042B | OS4285 | IBD | Ibadan | Osun | 3 - Low | OS0738 | WEST |  | 2025-11-29 10:42 | Ayodele Oludare | 2025-11-29 10:40 | 2025-11-29 10:46 | 332 | 2025-11-29 10:40 | 2025-11-29 10:46 | 0:06 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006472869 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-28 14:24 | Bukola Olabanji | 2025-11-28 14:21 | 2025-11-28 14:26 | 332 | 2025-11-28 14:21 | 2025-11-28 14:26 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006442408 | External Reconciliation | Site Down | P4 | IHS_EDO_1247B | ED5524 | IBD | Asaba | Edo | 3 - Low | ED1138 | SOUTH SOUTH |  | 2025-11-24 17:10 | Oluwatomisin Sogbesan | 2025-11-24 17:10 | 2025-11-24 17:16 | 332 | 2025-11-24 17:10 | 2025-11-24 17:16 | 0:06 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation). | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation).
NOCINC0006465630 | External Reconciliation | Site Down | P1 | IHS_WAR_0869H | DL0348 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 14:46 | Bukola Olabanji | 2025-11-27 14:43 | 2025-11-27 14:48 | 332 | 2025-11-27 14:43 | 2025-11-27 14:48 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006458046 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 14:00 | Emmanuel Faleti | 2025-11-26 13:58 | 2025-11-26 14:04 | 332 | 2025-11-26 13:58 | 2025-11-26 14:04 | 0:06 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006469209 | External Reconciliation | Site Down | P1 | IHS_ONT_0048B | AN0726 | ASB | Asaba | Anambra | 3 - Low | - | - | NE Is Disconnected@2025-11-28 00:43:00@NAN0726 | 2025-11-28 00:56 | System Administrator | 2025-11-28 00:51 | 2025-11-28 00:56 | 331 | 2025-11-28 00:51 | 2025-11-28 00:56 | 0:06 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Emmanuel Emmanuel | Henry Ubawuchi | Henry Ubawuchi | Henry Wanogho | Ifeanyi Chukusa |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006457904 | External Reconciliation | Site Down | P1 | IHS_DEL_1000A | DL0101 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 13:38 | Patrick Okoro | 2025-11-26 13:35 | 2025-11-26 13:41 | 331 | 2025-11-26 13:35 | 2025-11-26 13:41 | 0:06 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Christopher Essang |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006454278 | External Reconciliation | Site Down | P4 | IHS_DEL_1218B | - | - | Asaba | Delta | 3 - Low | DL0903 | SOUTH SOUTH |  | 2025-11-26 01:07 | Ayomide Akindolie | 2025-11-26 01:07 | 2025-11-26 01:12 | 330 | 2025-11-26 01:07 | 2025-11-26 01:12 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006444480 | External Reconciliation | Site Down | P2 | IHS_KWA_0855A | KW3816 | IBD | Ibadan | Kwara | 3 - Low | KW0436 | WEST |  | 2025-11-24 22:50 | Praise Okezie | 2025-11-24 22:47 | 2025-11-24 22:52 | 330 | 2025-11-24 22:47 | 2025-11-24 22:52 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Olapade Babatunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006441698 | External Reconciliation | Site Down | P4 | IHS_OSU_1051B | OS4795 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 16:13 | Victor Otugo | 2025-11-24 16:11 | 2025-11-24 16:17 | 330 | 2025-11-24 16:11 | 2025-11-24 16:17 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without intervention
NOCINC0006489131 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1247B | ED5524 | IBD | Asaba | Edo | 3 - Low | ED1138 | SOUTH SOUTH |  | 2025-11-30 18:49 | Evelyn Emagurehor | 2025-11-30 18:48 | 2025-11-30 18:53 | 330 | 2025-11-30 18:48 | 2025-11-30 18:53 | 0:05 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier Module | 2 / 2 | MTN NG, Airtel NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation). | Failed Rectifier Module was reset to restore power to the site. (No diesel outage after validation).
NOCINC0006473395 | Internal Reconciliation | Site Down | P3 | IHS_DEL_0952A | T2607 | ASB | Asaba | Delta | 3 - Low | DL1041 | SOUTH SOUTH |  | 2025-11-28 15:41 | Uthman Akinola | 2025-11-28 15:40 | 2025-11-28 15:45 | 329 | 2025-11-28 15:40 | 2025-11-28 15:45 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Restored without any technical intervention
NOCINC0006463777 | External Reconciliation | Site Down | P1 | IHS_OYO_0902A | T3865 | IBD | Ibadan | Oyo | 3 - Low | OY0963 | WEST |  | 2025-11-27 10:41 | Sheriff Salami | 2025-11-27 10:35 | 2025-11-27 10:41 | 329 | 2025-11-27 10:35 | 2025-11-27 10:41 | 0:05 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Load Breaker | 1 / 2 | MTN NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 3 | Tripped load breaker was enabled
NOCINC0006476423 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0874A | KW2380 | ABJ | Ibadan | Niger | 3 - Low | - | - |  | 2025-11-28 23:56 | Titus Tosin | 2025-11-28 23:56 | 2025-11-29 00:01 | 328 | 2025-11-28 23:56 | 2025-11-29 00:01 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Victor Agahiu |  |  | Soye West | Oboh Oseyeieomo |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006449961 | External Reconciliation | Site Down | P3 | IHS_IBA_0091C | OY4100 | IBD | Ibadan | Oyo | 3 - Low | OY1114 | WEST |  | 2025-11-25 16:29 | Mutmainnah Saba | 2025-11-25 16:25 | 2025-11-25 16:30 | 328 | 2025-11-25 16:25 | 2025-11-25 16:30 | 0:05 | SPS | Equipment Repair | Passive | Rectifier | Rectifier Cabinet | 2 / 2 | MTN NG, Airtel NG |  | BANKOLE SODIQ |  | Filani Oluwatobi | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty Rectifier was Worked On
NOCINC0006446101 | External Reconciliation | Site Down | P3 | IHS_OYO_1355B | OY1073 | IBD | Ibadan | Oyo | 3 - Low | OY1240 | WEST |  | 2025-11-25 08:54 | Victor Otugo | 2025-11-25 08:52 | 2025-11-25 08:58 | 328 | 2025-11-25 08:52 | 2025-11-25 08:58 | 0:05 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Throttle Motor | 2 / 2 | Airtel NG, MTN NG |  | Samuel Olaobaju | Yusuf Gyang |  | Abiola Adegbiji | Habeeb Adepoju |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Blocked throttle mixer was cleared
NOCINC0006479889 | Internal Reconciliation | Site Down | P4 | IHS_PAT_0001B | KW4586 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-29 13:07 | Ayodele Oludare | 2025-11-29 13:02 | 2025-11-29 13:07 | 328 | 2025-11-29 13:02 | 2025-11-29 13:07 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006478543 | Internal Reconciliation | Site Down | P1 | IHS_OYO_1023A | OY2861 | IBD | Ibadan | Oyo | 3 - Low | OY1060 | WEST |  | 2025-11-29 10:25 | Aishat Oyedeji | 2025-11-29 10:25 | 2025-11-29 10:30 | 328 | 2025-11-29 10:25 | 2025-11-29 10:30 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention
NOCINC0006441593 | External Reconciliation | Site Down | P1 | IHS_ANA_1388H | AN0762 | ASB | Asaba | Anambra | 3 - Low | AN0380 | SOUTH EAST |  | 2025-11-24 15:54 | Ezinne Ubachukwu | 2025-11-24 15:51 | 2025-11-24 15:57 | 327 | 2025-11-24 15:51 | 2025-11-24 15:57 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006449510 | External Reconciliation | Site Down | P2 | IHS_EKI_0856A | EK2285 | IBD | Ibadan | Ekiti | 3 - Low | EK0401 | WEST |  | 2025-11-25 15:24 | Oluwadara Bankole | 2025-11-25 15:22 | 2025-11-25 15:27 | 327 | 2025-11-25 15:22 | 2025-11-25 15:27 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Onewokae Ajiri |  |  | Ibrahim Akinpelu | Onewokae Ajiri |  | Sheriff Bolajoko | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006448241 | External Reconciliation | Site Down | P4 | IHS_ANA_1229A | AN0565 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 12:48 | Oluwatoyin Fagite | 2025-11-25 12:47 | 2025-11-25 12:52 | 327 | 2025-11-25 12:47 | 2025-11-25 12:52 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006469656 | External Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 03:47 | Oluwatobiloba Are | 2025-11-28 03:47 | 2025-11-28 03:52 | 327 | 2025-11-28 03:47 | 2025-11-28 03:52 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006463653 | External Reconciliation | Site Down | P3 | IHS_ONT_0006B | AN0316 | ASB | Asaba | Anambra | 3 - Low | AN0588 | SOUTH EAST |  | 2025-11-27 10:21 | Gbemisola Adedeji | 2025-11-27 10:19 | 2025-11-27 10:24 | 327 | 2025-11-27 10:19 | 2025-11-27 10:24 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006489324 | Internal Reconciliation | Site Down | P1 | IHS_AGB_0004B | DL0002 | ASB | Asaba | Delta | 3 - Low | DL0412 | SOUTH SOUTH |  | 2025-11-30 19:34 | Ezinne Ubachukwu | 2025-11-30 19:30 | 2025-11-30 19:35 | 326 | 2025-11-30 19:30 | 2025-11-30 19:35 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006457962 | External Reconciliation | Site Down | P1 | IHS_DEL_1020A | DL0113 | ASB | Asaba | Delta | 3 - Low | DL0742 | SOUTH SOUTH | CSL Fault@2025-11-26 13:34:52@DL0113_Sokobulu | 2025-11-26 13:47 | System Administrator | 2025-11-26 13:35 | 2025-11-26 13:40 | 326 | 2025-11-26 13:35 | 2025-11-26 13:40 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006462257 | External Reconciliation | Site Down | P2 | IHS_KWA_0767A | T3145 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 04:38 | Precious Attah | 2025-11-27 04:36 | 2025-11-27 04:41 | 326 | 2025-11-27 04:36 | 2025-11-27 04:41 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006483348 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-29 21:48:46@T2719_30 Emevor Orogun Road | 2025-11-29 22:02 | System Administrator | 2025-11-29 21:55 | 2025-11-29 22:00 | 326 | 2025-11-29 21:55 | 2025-11-29 22:00 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006478471 | Internal Reconciliation | Site Down | P3 | IHS_ANA_0903A | T4182 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 10:10 | Abundance Otunola | 2025-11-29 10:08 | 2025-11-29 10:13 | 325 | 2025-11-29 10:08 | 2025-11-29 10:13 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obinna Festus | Festus Obinna | Festus Obinna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006486971 | Internal Reconciliation | Site Down | P2 | IHS_OND_0934A | OD2516 | IBD | Ibadan | Ondo | 3 - Low | ON0578 | WEST |  | 2025-11-30 13:15 | Ihuoma Opurum | 2025-11-30 13:15 | 2025-11-30 13:20 | 325 | 2025-11-30 13:15 | 2025-11-30 13:20 | 0:05 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Anawanti Kingsley |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was restored without intervention.
NOCINC0006487576 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-30 14:41 | Oluwadara Bankole | 2025-11-30 14:38 | 2025-11-30 14:44 | 324 | 2025-11-30 14:38 | 2025-11-30 14:44 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006462850 | External Reconciliation | Site Down | P3 | IHS_EDO_1184H | ED2105 | IBD | Asaba | Edo | 3 - Low | ED0862 | SOUTH SOUTH |  | 2025-11-27 07:28 | Oluwatomisin Sogbesan | 2025-11-27 07:27 | 2025-11-27 07:32 | 324 | 2025-11-27 07:27 | 2025-11-27 07:32 | 0:05 | Huawei | Equipment Repair | Passive | Infrastructure | Armoured Cable | 2 / 2 | MTN NG, Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Burnt load cable was worked on and re-terminated (No diesel outage after validation)
NOCINC0006443817 | External Reconciliation | Site Down | P3 | IHS_ANA_1224A | AN0563 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 21:00 | Solomon Bankole | 2025-11-24 21:00 | 2025-11-24 21:05 | 324 | 2025-11-24 21:00 | 2025-11-24 21:05 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention | Site came up without any technical intervention
NOCINC0006448413 | External Reconciliation | Site Down | P3 | IHS_IBA_0708E | - | - | Ibadan | Oyo | 3 - Low | OY1157 | WEST |  | 2025-11-25 13:13 | Victor Otugo | 2025-11-25 13:08 | 2025-11-25 13:13 | 323 | 2025-11-25 13:08 | 2025-11-25 13:13 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Azeez Yusuf | John Eze | John Eze | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Short duration outage, Site came up without intervention
NOCINC0006440628 | External Reconciliation | Site Down | P1 | IHS_WAR_0944B | DL3327 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 13:48 | Ezinne Ubachukwu | 2025-11-24 13:45 | 2025-11-24 13:50 | 323 | 2025-11-24 13:45 | 2025-11-24 13:50 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006480054 | Internal Reconciliation | Site Down | P4 | IHS_OND_0830A | T3846 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 13:28 | Maureen Uchehorke | 2025-11-29 13:25 | 2025-11-29 13:31 | 322 | 2025-11-29 13:25 | 2025-11-29 13:31 | 0:05 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Start failure. DCGG was restarted
NOCINC0006480689 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1141A | DL0630 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 14:46 | Quadri Ogundare | 2025-11-29 14:44 | 2025-11-29 14:49 | 322 | 2025-11-29 14:44 | 2025-11-29 14:49 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006465710 | External Reconciliation | Site Down | P3 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-27 14:55 | Mary Odefemi | 2025-11-27 14:55 | 2025-11-27 15:00 | 321 | 2025-11-27 14:55 | 2025-11-27 15:00 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 3 | Short duration outage
NOCINC0006485281 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1212B | DL4085 | ASB | Asaba | Delta | 3 - Low | DL1034 | SOUTH SOUTH |  | 2025-11-30 08:27 | Tracy Osarumwense | 2025-11-30 08:22 | 2025-11-30 08:27 | 321 | 2025-11-30 08:22 | 2025-11-30 08:27 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006445354 | External Reconciliation | Site Down | P1 | IHS_OYO_0911A | T3989 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 05:05 | Praise Okezie | 2025-11-25 05:05 | 2025-11-25 05:10 | 321 | 2025-11-25 05:05 | 2025-11-25 05:10 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006459335 | External Reconciliation | Site Down | P4 | IHS_ANA_1229A | AN0565 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 17:19 | Oluwatoyin Fagite | 2025-11-26 17:18 | 2025-11-26 17:23 | 320 | 2025-11-26 17:18 | 2025-11-26 17:23 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006461135 | External Reconciliation | Site Down | P2 | IHS_IBA_0764E | OY2963 | IBD | Ibadan | Oyo | 3 - Low | OY0940 | WEST |  | 2025-11-26 22:33 | Victor Otugo | 2025-11-26 22:32 | 2025-11-26 22:38 | 320 | 2025-11-26 22:32 | 2025-11-26 22:38 | 0:05 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Lukman Mohammed |  | Yunus Ololade | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006451705 | External Reconciliation | Site Down | P4 | IHS_OYO_1085K | OY4080 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 20:35 | Aishat Oyedeji | 2025-11-25 20:28 | 2025-11-25 20:33 | 320 | 2025-11-25 20:28 | 2025-11-25 20:33 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Bayo Nathaniel |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, no intervention
NOCINC0006462654 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 06:39 | Oluwadara Bankole | 2025-11-27 06:36 | 2025-11-27 06:41 | 319 | 2025-11-27 06:36 | 2025-11-27 06:41 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006463941 | External Reconciliation | Site Down | P1 | IHS_ASA_0702E | - | - | Asaba | Delta | 3 - Low | DL0690 | SOUTH SOUTH |  | 2025-11-27 11:05 | Femi Olanipekun | 2025-11-27 11:05 | 2025-11-27 11:10 | 319 | 2025-11-27 11:05 | 2025-11-27 11:10 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Victor Ezeh |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006487736 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1404H | AN0523 | ASB | Asaba | Anambra | 3 - Low | AN0851 | SOUTH EAST |  | 2025-11-30 15:02 | Aderonke Olowojoba | 2025-11-30 14:59 | 2025-11-30 15:04 | 319 | 2025-11-30 14:59 | 2025-11-30 15:04 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006478488 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1020A | DL0113 | ASB | Asaba | Delta | 3 - Low | DL0742 | SOUTH SOUTH |  | 2025-11-29 10:13 | Ayomide Akindolie | 2025-11-29 10:12 | 2025-11-29 10:17 | 319 | 2025-11-29 10:12 | 2025-11-29 10:17 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006447380 | External Reconciliation | Site Down | P3 | IHS_ILO_0047B | KW1212 | IBD | Ibadan | Kwara | 3 - Low | KW0311 | WEST |  | 2025-11-25 11:07 | Mutmainnah Saba | 2025-11-25 10:58 | 2025-11-25 11:05 | 406 | 2025-11-25 11:00 | 2025-11-25 11:05 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mohammed Soliu |  | Abdulraman Odunola | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006471630 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0856A | T3588 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 11:06 | Damilola Paseda | 2025-11-28 11:04 | 2025-11-28 11:10 | 318 | 2025-11-28 11:04 | 2025-11-28 11:10 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006472860 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1324B | OY1034 | IBD | Ibadan | Oyo | 3 - Low | OY1686 | WEST |  | 2025-11-28 14:23 | Damilola Paseda | 2025-11-28 14:22 | 2025-11-28 14:27 | 318 | 2025-11-28 14:22 | 2025-11-28 14:27 | 0:05 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 2 / 2 | MTN NG, Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Voltage fluctuation due to weak BUB, GG auto-restarted. | Voltage fluctuation due to weak BUB, GG auto-restarted.
NOCINC0006457933 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 13:40 | Oluwatobiloba Are | 2025-11-26 13:40 | 2025-11-26 13:46 | 318 | 2025-11-26 13:40 | 2025-11-26 13:46 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Short duration outage, site came up without technical intervention
NOCINC0006439191 | External Reconciliation | Site Down | P2 | IHS_OYO_0810A | T3002 | IBD | Ibadan | Oyo | 3 - Low | OY1028 | WEST | 4G ZTE Sitedown@2025-11-24 10:03:26@OY1028(31028) | 2025-11-24 10:16 | System Administrator | 2025-11-24 10:03 | 2025-11-24 10:09 | 318 | 2025-11-24 10:03 | 2025-11-24 10:09 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mosunmola Christopher |  |  | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, no intervention
NOCINC0006437657 | External Reconciliation | Site Down | P2 | IHS_KWA_0767A | T3145 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 04:12 | Okusanya Joseph | 2025-11-24 04:11 | 2025-11-24 04:17 | 318 | 2025-11-24 04:11 | 2025-11-24 04:17 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006480139 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 13:40 | Ayomide Akindolie | 2025-11-29 13:39 | 2025-11-29 13:44 | 317 | 2025-11-29 13:39 | 2025-11-29 13:44 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006488019 | Internal Reconciliation | Site Down | P4 | IHS_OND_0830A | T3846 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 15:42 | Yewande Adeagbo | 2025-11-30 15:41 | 2025-11-30 15:46 | 316 | 2025-11-30 15:41 | 2025-11-30 15:46 | 0:05 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | start failure alarm was cleared and DG powered manually
NOCINC0006463533 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 10:00 | Muhammed Hashirudeen | 2025-11-27 10:00 | 2025-11-27 10:05 | 316 | 2025-11-27 10:00 | 2025-11-27 10:05 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site restored without intervention.
NOCINC0006447934 | External Reconciliation | Site Down | P3 | IHS_OYO_1435B | OY4955 | - | Ibadan | Oyo | 3 - Low | OY1460 | WEST |  | 2025-11-25 12:10 | Marvellous Emecheta | 2025-11-25 12:10 | 2025-11-25 12:15 | 316 | 2025-11-25 12:10 | 2025-11-25 12:15 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Alaba |  |  | Paul Akpomie | Oluwaseun Alaba |  | Luke Eke | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006467601 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 20:02 | Muhammed Hashirudeen | 2025-11-27 20:02 | 2025-11-27 20:07 | 316 | 2025-11-27 20:02 | 2025-11-27 20:07 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site restored without intervention.
NOCINC0006462205 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-27 04:09 | Precious Attah | 2025-11-27 04:09 | 2025-11-27 04:14 | 315 | 2025-11-27 04:09 | 2025-11-27 04:14 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006473208 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0766A | T3144 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 15:14 | Praise Okezie | 2025-11-28 15:10 | 2025-11-28 15:15 | 315 | 2025-11-28 15:10 | 2025-11-28 15:15 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006470928 | External Reconciliation | Site Down | P3 | IHS_OND_1046B | OD6258 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 09:28 | Maureen Uchehorke | 2025-11-28 09:26 | 2025-11-28 09:31 | 315 | 2025-11-28 09:26 | 2025-11-28 09:31 | 0:05 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Anawanti Kingsley | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Voltage fluctuations due to absence of BUB at site, GG auto restart
NOCINC0006461652 | External Reconciliation | Site Down | P1 | IHS_OSU_0903A | OS3648 | IBD | Ibadan | Osun | 3 - Low | OS0695 | WEST |  | 2025-11-27 00:23 | Victor Otugo | 2025-11-27 00:19 | 2025-11-27 00:24 | 314 | 2025-11-27 00:19 | 2025-11-27 00:24 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006439633 | External Reconciliation | Site Down | P1 | IHS_EDO_0798A | T3252 | IBD | Asaba | Edo | 3 - Low | ED0184 | SOUTH SOUTH | 4G ZTE Sitedown@2025-11-24 11:29:56@ED0184(50184) | 2025-11-24 11:49 | System Administrator | 2025-11-24 11:30 | 2025-11-24 11:35 | 314 | 2025-11-24 11:30 | 2025-11-24 11:35 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006471108 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1040A | AN0030 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 09:54 | Uthman Akinola | 2025-11-28 09:53 | 2025-11-28 09:58 | 314 | 2025-11-28 09:53 | 2025-11-28 09:58 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006490128 | Internal Reconciliation | Site Down | P3 | IHS_OND_0998A | OD4708 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 22:24 | Maureen Uchehorke | 2025-11-30 22:21 | 2025-11-30 22:26 | 313 | 2025-11-30 22:21 | 2025-11-30 22:26 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Sola Oluwarotimi |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify | 2 | Short duration outage
NOCINC0006482276 | Internal Reconciliation | Site Down | P3 | IHS_IBA_0007B | - | - | Ibadan | Oyo | 3 - Low | OY0623 | WEST |  | 2025-11-29 19:01 | Damilola Paseda | 2025-11-29 18:56 | 2025-11-29 19:01 | 313 | 2025-11-29 18:56 | 2025-11-29 19:01 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Aramide Kazeem |  | Aramide Kazeem | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006465390 | External Reconciliation | Site Down | P2 | IHS_KWA_0769A | T3140 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 14:11 | Okusanya Joseph | 2025-11-27 14:10 | 2025-11-27 14:16 | 313 | 2025-11-27 14:10 | 2025-11-27 14:16 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006470741 | External Reconciliation | Site Down | P3 | IHS_EDO_0899A | T3326 | IBD | Asaba | Edo | 3 - Low | ED0182 | SOUTH SOUTH |  | 2025-11-28 09:04 | Muhammed Hashirudeen | 2025-11-28 09:04 | 2025-11-28 09:09 | 312 | 2025-11-28 09:04 | 2025-11-28 09:09 | 0:05 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | OMOKHAFE JULIUS | Julius Godwin | Julius Godwin | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006456638 | External Reconciliation | Site Down | P4 | IHS_ONT_0029B | AN0598 | ASB | Asaba | Anambra | 3 - Low | AN1076 | SOUTH EAST |  | 2025-11-26 10:36 | Akachukwu Ugwu | 2025-11-26 10:33 | 2025-11-26 10:38 | 312 | 2025-11-26 10:33 | 2025-11-26 10:38 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Femi Balogun | Femi Balogun | Femi Balogun | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006451202 | External Reconciliation | Site Down | P1 | IHS_OSU_0810A | T3095 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 19:39 | Marvellous Emecheta | 2025-11-25 19:37 | 2025-11-25 19:42 | 311 | 2025-11-25 19:37 | 2025-11-25 19:42 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 5 | Short duration outage, site was up with no intervention.
NOCINC0006446809 | External Reconciliation | Site Down | P2 | IHS_OYO_1278H | OY4461 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 10:06 | Precious Attah | 2025-11-25 10:05 | 2025-11-25 10:10 | 311 | 2025-11-25 10:05 | 2025-11-25 10:10 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006438451 | External Reconciliation | Site Down | P4 | IHS_DEL_0968A | DL0008 | ASB | Asaba | Delta | 3 - Low | DL0930 | SOUTH SOUTH |  | 2025-11-24 08:17 | Uthman Akinola | 2025-11-24 08:16 | 2025-11-24 08:22 | 311 | 2025-11-24 08:16 | 2025-11-24 08:22 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006472952 | Internal Reconciliation | Site Down | P3 | IHS_EKI_0005B | EK2239 | IBD | Ibadan | Ekiti | 3 - Low | EK0430 | WEST | CSL Fault@2025-11-28 14:27:34@EK2239_Odo Oro-Ekiti | 2025-11-28 14:40 | System Administrator | 2025-11-28 14:38 | 2025-11-28 14:43 | 310 | 2025-11-28 14:38 | 2025-11-28 14:43 | 0:05 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Under Voltage | 2 / 2 | MTN NG, Airtel NG |  | Oluwafemi Oluwasegun |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | DG under voltage alarm was cleared
NOCINC0006479882 | Internal Reconciliation | Site Down | P4 | IHS_PAT_0003B | KW4587 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-29 13:06 | Ayodele Oludare | 2025-11-29 13:02 | 2025-11-29 13:07 | 310 | 2025-11-29 13:02 | 2025-11-29 13:07 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | site came up without intervention
NOCINC0006449274 | External Reconciliation | Site Down | P4 | IHS_ANA_0941A | T4819 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-25 14:35:38@T4819_Community Secondary Sch Ichida | 2025-11-25 14:51 | System Administrator | 2025-11-25 14:43 | 2025-11-25 14:49 | 310 | 2025-11-25 14:43 | 2025-11-25 14:49 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006470852 | External Reconciliation | Site Down | P1 | IHS_DEL_0711E | - | - | Asaba | Delta | 3 - Low | DL0562 | SOUTH SOUTH |  | 2025-11-28 09:14 | Quadri Ogundare | 2025-11-28 09:14 | 2025-11-28 09:20 | 309 | 2025-11-28 09:14 | 2025-11-28 09:20 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006468133 | External Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 21:44 | Oluwatobiloba Are | 2025-11-27 21:43 | 2025-11-27 21:48 | 309 | 2025-11-27 21:43 | 2025-11-27 21:48 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006444251 | External Reconciliation | Site Down | P1 | IHS_OYO_0006B | OY2982 | IBD | Ibadan | Oyo | 3 - Low | OY0755 | WEST | 4G ZTE Sitedown@2025-11-24 21:27:16@OY0755(30755) | 2025-11-24 22:07 | System Administrator | 2025-11-24 21:27 | 2025-11-24 21:33 | 309 | 2025-11-24 21:27 | 2025-11-24 21:33 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | Airtel NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006473451 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0911A | T2775 | ASB | Asaba | Delta | 3 - Low | DL0560 | SOUTH SOUTH |  | 2025-11-28 15:52 | Quadri Ogundare | 2025-11-28 15:51 | 2025-11-28 15:56 | 309 | 2025-11-28 15:51 | 2025-11-28 15:56 | 0:05 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Water Pump | 2 / 2 | Airtel NG, MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify | 1 | Faulty water pump was replaced | Faulty water pump was replaced
NOCINC0006478734 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-29 10:49 | Valentine Adinnu | 2025-11-29 10:47 | 2025-11-29 10:52 | 308 | 2025-11-29 10:47 | 2025-11-29 10:52 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short Duration Outage
NOCINC0006487842 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1182H | OY4345 | IBD | Ibadan | Oyo | 3 - Low | OY0986 | WEST |  | 2025-11-30 15:17 | Aishat Oyedeji | 2025-11-30 15:17 | 2025-11-30 15:22 | 308 | 2025-11-30 15:17 | 2025-11-30 15:22 | 0:05 | SPS | Equipment Repair | Passive | Hybrid | Hybrid Software | 2 / 2 | MTN NG, Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization failure due to frozen CSU, CSU was reset | Hybrid synchronization failure due to frozen CSU, CSU was reset
NOCINC0006449590 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 15:36 | Oluwadara Bankole | 2025-11-25 15:32 | 2025-11-25 15:38 | 308 | 2025-11-25 15:32 | 2025-11-25 15:38 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | No passive issue at site, Voltage/Current Evidence confirmed attached | No passive issue at site, Voltage/Current Evidence confirmed attached
NOCINC0006470924 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 09:27 | Bukola Olabanji | 2025-11-28 09:26 | 2025-11-28 09:31 | 308 | 2025-11-28 09:26 | 2025-11-28 09:31 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Short duration outage
NOCINC0006467059 | External Reconciliation | Site Down | P2 | IHS_OSU_0042B | OS4285 | IBD | Ibadan | Osun | 3 - Low | OS0738 | WEST |  | 2025-11-27 18:25 | Titus Tosin | 2025-11-27 18:25 | 2025-11-27 18:30 | 307 | 2025-11-27 18:25 | 2025-11-27 18:30 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006448325 | External Reconciliation | Site Down | P3 | IHS_BEN_0015V | ED5180 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 12:58 | Emmanuel Faleti | 2025-11-25 12:58 | 2025-11-25 13:03 | 307 | 2025-11-25 12:58 | 2025-11-25 13:03 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ismail Adeyinka |  |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006448364 | External Reconciliation | Site Down | P2 | IHS_OYO_0810A | T3002 | IBD | Ibadan | Oyo | 3 - Low | OY1028 | WEST | 4G ZTE Sitedown@2025-11-25 12:51:52@OY1028(31028) | 2025-11-25 13:04 | System Administrator | 2025-11-25 12:52 | 2025-11-25 12:57 | 307 | 2025-11-25 12:52 | 2025-11-25 12:57 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mosunmola Christopher |  |  | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006458405 | External Reconciliation | Site Down | P2 | IHS_BEN_0067C | ED4972 | IBD | Asaba | Edo | 3 - Low | ED0993 | SOUTH SOUTH |  | 2025-11-26 14:53 | Emmanuel Faleti | 2025-11-26 14:52 | 2025-11-26 14:57 | 306 | 2025-11-26 14:52 | 2025-11-26 14:57 | 0:05 | MPI NGA | Equipment Replacement | Passive | Planned Activity | Planned Activity - Passive | 1 / 2 | MTN NG |  | Edwin Emehian |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | RMS planned activity with ref IHS_BEN_0067C IHSREF/25112605091562367817 SARID0009050771 | RMS planned activity with ref IHS_BEN_0067C IHSREF/25112605091562367817 SARID0009050771
NOCINC0006490158 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0875A | OS3995 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-30 22:31 | Praise Okezie | 2025-11-30 22:28 | 2025-11-30 22:33 | 306 | 2025-11-30 22:28 | 2025-11-30 22:33 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006467518 | External Reconciliation | Site Down | P2 | IHS_EDO_1028A | ED4923 | IBD | Asaba | Edo | 3 - Low | ED1071 | South South |  | 2025-11-27 19:48 | Muhammed Hashirudeen | 2025-11-27 19:47 | 2025-11-27 19:52 | 306 | 2025-11-27 19:47 | 2025-11-27 19:52 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | MTN NG |  | EKPU SUNDAY |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006455291 | External Reconciliation | Site Down | P2 | IHS_IBA_0764E | OY2963 | IBD | Ibadan | Oyo | 3 - Low | OY0940 | WEST |  | 2025-11-26 06:24 | Aishat Oyedeji | 2025-11-26 06:22 | 2025-11-26 06:27 | 306 | 2025-11-26 06:22 | 2025-11-26 06:27 | 0:05 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Lukman Mohammed |  | Yunus Ololade | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Short duration outage, no intervention
NOCINC0006459571 | External Reconciliation | Site Down | P1 | IHS_KWA_0749A | T3115 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-26 18:02 | Titus Tosin | 2025-11-26 17:58 | 2025-11-26 18:03 | 306 | 2025-11-26 17:58 | 2025-11-26 18:03 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006479677 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-29 12:41 | Valentine Adinnu | 2025-11-29 12:37 | 2025-11-29 12:42 | 305 | 2025-11-29 12:37 | 2025-11-29 12:42 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006446603 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 09:33 | Oluwadara Bankole | 2025-11-25 09:30 | 2025-11-25 09:35 | 305 | 2025-11-25 09:30 | 2025-11-25 09:35 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006470459 | External Reconciliation | Site Down | P3 | IHS_OSU_0049B | OS2681 | IBD | Ibadan | Osun | 3 - Low | OS0831 | WEST | Huawei 2G SiteDown@2025-11-28 07:53:10@OS2681_Odode Ila Orangun | 2025-11-28 08:06 | System Administrator | 2025-11-28 07:58 | 2025-11-28 08:03 | 304 | 2025-11-28 07:58 | 2025-11-28 08:03 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short outage duration, Site restored with no intervention
NOCINC0006477682 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1011A | T4869 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 07:41 | Akachukwu Ugwu | 2025-11-29 07:39 | 2025-11-29 07:44 | 304 | 2025-11-29 07:39 | 2025-11-29 07:44 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006473253 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1009A | AN4811 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 15:22 | Gbemisola Adedeji | 2025-11-28 15:21 | 2025-11-28 15:26 | 304 | 2025-11-28 15:21 | 2025-11-28 15:26 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Alechenu Samuel | Chris Idome | Chris Idome | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006472659 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 13:56 | Bukola Olabanji | 2025-11-28 13:53 | 2025-11-28 13:58 | 304 | 2025-11-28 13:53 | 2025-11-28 13:58 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006447929 | External Reconciliation | Site Down | P1 | IHS_OYO_0882A | T3556 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 12:09 | Mutmainnah Saba | 2025-11-25 12:07 | 2025-11-25 12:12 | 304 | 2025-11-25 12:07 | 2025-11-25 12:12 | 0:05 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Olaitan Olajide |  | Yunus Ololade | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | voltage fluctuation due to weak at site
NOCINC0006458009 | External Reconciliation | Site Down | P3 | IHS_ANA_1223A | AN0706 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 13:55 | Oluwatoyin Fagite | 2025-11-26 13:53 | 2025-11-26 13:58 | 303 | 2025-11-26 13:53 | 2025-11-26 13:58 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006450846 | External Reconciliation | Site Down | P4 | IHS_DEL_0905A | T2768 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 18:34 | Ezinne Ubachukwu | 2025-11-25 18:33 | 2025-11-25 18:38 | 303 | 2025-11-25 18:33 | 2025-11-25 18:38 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006474320 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1453B | OY1054 | IBD | Ibadan | Oyo | 3 - Low | OY0942 | WEST |  | 2025-11-28 17:51 | Mutmainnah Saba | 2025-11-28 17:48 | 2025-11-28 17:53 | 303 | 2025-11-28 17:48 | 2025-11-28 17:53 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | BASHIR ABDULRASAQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006462429 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 05:39 | Oluwadara Bankole | 2025-11-27 05:35 | 2025-11-27 05:40 | 303 | 2025-11-27 05:35 | 2025-11-27 05:40 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006444515 | External Reconciliation | Site Down | P4 | IHS_ANA_0967A | T4101 | ASB | Asaba | Anambra | 3 - Low | AN1074 | SOUTH EAST |  | 2025-11-24 23:00 | Solomon Bankole | 2025-11-24 22:59 | 2025-11-24 23:04 | 302 | 2025-11-24 22:59 | 2025-11-24 23:04 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without any technical intervention | Site came up without any technical intervention
NOCINC0006458369 | External Reconciliation | Site Down | P3 | IHS_OND_1046B | OD6258 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 14:49 | Mary Elaigwu | 2025-11-26 14:48 | 2025-11-26 14:53 | 302 | 2025-11-26 14:48 | 2025-11-26 14:53 | 0:05 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Anawanti Kingsley | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Voltage fluctuation due to weak BUB, GG auto restart
NOCINC0006480045 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1019A | DL0304 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 13:27 | Ayokunle Samuel | 2025-11-29 13:24 | 2025-11-29 13:29 | 302 | 2025-11-29 13:24 | 2025-11-29 13:29 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention. | Site inter failed and cleared without any technical intervention.
NOCINC0006470600 | External Reconciliation | Site Down | P1 | IHS_ANA_0825A | T4032 | ASB | Asaba | Anambra | 3 - Low | AN0418 | SOUTH EAST |  | 2025-11-28 08:38 | Uthman Akinola | 2025-11-28 08:36 | 2025-11-28 08:41 | 301 | 2025-11-28 08:36 | 2025-11-28 08:41 | 0:05 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Low Oil Pressure | 2 / 2 | Airtel NG, MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | low oil pressure, oil top up done(no diesel outage after validation)
NOCINC0006465529 | External Reconciliation | Site Down | P3 | IHS_WAR_0071C | DL0939 | ASB | Asaba | Delta | 3 - Low | DL0688 | SOUTH SOUTH |  | 2025-11-27 14:28 | Mary Odefemi | 2025-11-27 14:28 | 2025-11-27 14:33 | 301 | 2025-11-27 14:28 | 2025-11-27 14:33 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Kevwe Oshoture |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006488128 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1151A | DL0675 | ASB | Asaba | Delta | 3 - Low | DL0761 | SOUTH SOUTH |  | 2025-11-30 16:04 | Ayomide Akindolie | 2025-11-30 16:02 | 2025-11-30 16:07 | 301 | 2025-11-30 16:02 | 2025-11-30 16:07 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006461680 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 00:27 | Oluwadara Bankole | 2025-11-27 00:25 | 2025-11-27 00:30 | 301 | 2025-11-27 00:25 | 2025-11-27 00:30 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006470495 | External Reconciliation | Site Down | P1 | IHS_EDO_0892A | T3361 | IBD | Asaba | Edo | 3 - Low | ED0449 | SOUTH SOUTH |  | 2025-11-28 08:15 | Emmanuel Faleti | 2025-11-28 08:14 | 2025-11-28 08:20 | 301 | 2025-11-28 08:14 | 2025-11-28 08:20 | 0:05 | Huawei | Equipment Replacement | Passive | Planned Activity | Generator Servicing | 2 / 2 | Airtel NG, MTN NG |  | Imomoh Sylvanus |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | PPM was carried out on site (No diesel outage after validation) | PPM was carried out on site (No diesel outage after validation)
NOCINC0006441717 | External Reconciliation | Site Down | P2 | IHS_OSU_0042B | OS4285 | IBD | Ibadan | Osun | 3 - Low | OS0738 | WEST |  | 2025-11-24 16:17 | Azeezat Adekunle | 2025-11-24 16:17 | 2025-11-24 16:22 | 300 | 2025-11-24 16:17 | 2025-11-24 16:22 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006470415 | External Reconciliation | Site Down | P2 | IHS_OYO_0932A | T3873 | IBD | Ibadan | Oyo | 3 - Low | OY1125 | WEST |  | 2025-11-28 07:56 | Ifechi Ugwueze | 2025-11-28 07:50 | 2025-11-28 07:54 | 241 | 2025-11-28 07:49 | 2025-11-28 07:54 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site was restored without intervention
NOCINC0006466600 | External Reconciliation | Site Down | P3 | IHS_OYO_0963A | T3808 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-27 17:06 | Sheriff Salami | 2025-11-27 17:03 | 2025-11-27 17:08 | 300 | 2025-11-27 17:03 | 2025-11-27 17:08 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short outage duration, Site restored with no intervention
NOCINC0006456597 | External Reconciliation | Site Down | P1 | IHS_OYO_1028A | OY2882 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 10:29 | Ifechi Ugwueze | 2025-11-26 10:26 | 2025-11-26 10:31 | 273 | 2025-11-26 10:26 | 2025-11-26 10:31 | 0:05 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Adewale Balogun | Ogunjemilua Adeniyi |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Site was restored without intervention
NOCINC0006471186 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0061B | OS4254 | IBD | Ibadan | Osun | 3 - Low | OS0698 | WEST |  | 2025-11-28 10:09 | Mutmainnah Saba | 2025-11-28 10:03 | 2025-11-28 10:08 | 300 | 2025-11-28 10:03 | 2025-11-28 10:08 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ABDULAZEEZ SODIQ | Biola Oyenuga | Biola Oyenuga | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006478375 | Internal Reconciliation | Site Down | P4 | IHS_OND_1104B | OD6250 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-29 09:51 | Testimony Akinyemi | 2025-11-29 09:49 | 2025-11-29 09:54 | 300 | 2025-11-29 09:49 | 2025-11-29 09:54 | 0:05 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Anawanti Kingsley | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | SHORT DURATION OUTAGE
NOCINC0006448914 | External Reconciliation | Site Down | P2 | IHS_OSU_0866A | T3624 | IBD | Ibadan | Osun | 3 - Low | OS0626 | WEST |  | 2025-11-25 14:01 | Marvellous Emecheta | 2025-11-25 14:00 | 2025-11-25 14:05 | 300 | 2025-11-25 14:00 | 2025-11-25 14:05 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Adejumobi Tunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006440663 | External Reconciliation | Site Down | P1 | IHS_DEL_0854A | T2730 | ASB | Asaba | Delta | 3 - Low | - | - | gNodeB Out of Service@2025-11-24 13:41:07@N2730 | 2025-11-24 13:55 | System Administrator | 2025-11-24 13:41 | 2025-11-24 13:46 | 300 | 2025-11-24 13:41 | 2025-11-24 13:46 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Gabriel Akhamiogu |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter-fail and clear without any technical intervention.
NOCINC0006488067 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0822A | T4069/T6508 | ASB | Asaba | Anambra | 3 - Low | AN0427 | SOUTH EAST |  | 2025-11-30 15:54 | Aderonke Olowojoba | 2025-11-30 15:52 | 2025-11-30 15:57 | 300 | 2025-11-30 15:52 | 2025-11-30 15:57 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Obinna Clinton |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006460645 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-26 21:03 | Oluwatomisin Sogbesan | 2025-11-26 21:00 | 2025-11-26 21:05 | 300 | 2025-11-26 21:00 | 2025-11-26 21:05 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006452033 | External Reconciliation | Site Down | P3 | IHS_OYO_1414B | - | - | Ibadan | Oyo | 3 - Low | OY1366 | WEST |  | 2025-11-25 21:30 | Azeezat Adekunle | 2025-11-25 21:25 | 2025-11-25 21:30 | 300 | 2025-11-25 21:25 | 2025-11-25 21:30 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006482165 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-29 18:38 | Valentine Adinnu | 2025-11-29 18:34 | 2025-11-29 18:39 | 300 | 2025-11-29 18:34 | 2025-11-29 18:39 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006449413 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 15:08 | Emmanuel Faleti | 2025-11-25 15:08 | 2025-11-25 15:13 | 299 | 2025-11-25 15:08 | 2025-11-25 15:13 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006447632 | External Reconciliation | Site Down | P4 | IHS_EDO_1048C | ED6125 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 11:26 | Tracy Osarumwense | 2025-11-25 11:26 | 2025-11-25 11:31 | 299 | 2025-11-25 11:26 | 2025-11-25 11:31 | 0:05 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006465851 | External Reconciliation | Site Down | P3 | IHS_OSU_0895A | T3488 | IBD | Ibadan | Osun | 3 - Low | OS0732 | WEST |  | 2025-11-27 15:18 | Sheriff Salami | 2025-11-27 15:13 | 2025-11-27 15:18 | 299 | 2025-11-27 15:13 | 2025-11-27 15:18 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Zechariah Akinbulejo | Opeyemi Ajibola | Opeyemi Ajibola | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short outage duration, Site restored with no intervention
NOCINC0006456762 | External Reconciliation | Site Down | P2 | IHS_OYO_0810A | T3002 | IBD | Ibadan | Oyo | 3 - Low | OY1028 | WEST | 4G ZTE Sitedown@2025-11-26 10:46:11@OY1028(31028) | 2025-11-26 10:58 | System Administrator | 2025-11-26 10:46 | 2025-11-26 10:51 | 299 | 2025-11-26 10:46 | 2025-11-26 10:51 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mosunmola Christopher |  |  | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006437718 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 04:31 | Muhammed Hashirudeen | 2025-11-24 04:31 | 2025-11-24 04:36 | 299 | 2025-11-24 04:31 | 2025-11-24 04:36 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Site restored without intervention.
NOCINC0006465369 | External Reconciliation | Site Down | P1 | IHS_ANA_1291C | AN0923 | ASB | Asaba | Anambra | 3 - Low | AN0724 | SOUTH EAST |  | 2025-11-27 14:08 | Gbemisola Adedeji | 2025-11-27 14:05 | 2025-11-27 14:10 | 298 | 2025-11-27 14:05 | 2025-11-27 14:10 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ugwuja Chinonso |  |  | Erik Nwodo | Nwigbo Chijioke |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006466267 | External Reconciliation | Site Down | P1 | IHS_DEL_0794A | T2669 | ASB | Asaba | Delta | 3 - Low | DL0516 | SOUTH SOUTH |  | 2025-11-27 16:11 | Bukola Olabanji | 2025-11-27 16:09 | 2025-11-27 16:14 | 298 | 2025-11-27 16:09 | 2025-11-27 16:14 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | KELECHI LEWIS | Francis Omojevwe | Francis Omojevwe | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006482635 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0798A | T3252 | IBD | Asaba | Edo | 3 - Low | ED0184 | SOUTH SOUTH | 4G ZTE Sitedown@2025-11-29 19:51:07@ED0184(50184) | 2025-11-29 20:04 | System Administrator | 2025-11-29 19:51 | 2025-11-29 19:56 | 297 | 2025-11-29 19:51 | 2025-11-29 19:56 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared with no technical intervention
NOCINC0006463132 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-27 08:28:05@T0286_Hotel Marina Off Sokoto road O | 2025-11-27 08:41 | System Administrator | 2025-11-27 08:38 | 2025-11-27 08:46 | 477 | 2025-11-27 08:41 | 2025-11-27 08:46 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006487214 | Internal Reconciliation | Site Down | P1 | IHS_OND_0034B | OD4824 | IBD | Ibadan | Ondo | 3 - Low | ON0567 | WEST |  | 2025-11-30 13:32 | Ihuoma Opurum | 2025-11-30 13:31 | 2025-11-30 13:36 | 296 | 2025-11-30 13:31 | 2025-11-30 13:36 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Daudu Usman |  |  | Soye West | Goddey Nwokedigbo Peter |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage. Site was restored without intervention.
NOCINC0006439055 | External Reconciliation | Site Down | P4 | IHS_OSU_0732E | OS4698 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-24 09:46 | Azeezat Adekunle | 2025-11-24 09:44 | 2025-11-24 09:49 | 296 | 2025-11-24 09:44 | 2025-11-24 09:49 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006479799 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1049A | AN0103 | ASB | Asaba | Anambra | 3 - Low | AN0526 | SOUTH EAST |  | 2025-11-29 12:56 | Abundance Otunola | 2025-11-29 12:55 | 2025-11-29 13:00 | 296 | 2025-11-29 12:55 | 2025-11-29 13:00 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Femi Balogun | Femi Balogun | Femi Balogun | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006484975 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0932A | T3873 | IBD | Ibadan | Oyo | 3 - Low | OY1125 | WEST | The link between the server and the ME is broken@2025-11-30 06:40:44@OY1125(31125) | 2025-11-30 07:04 | System Administrator | 2025-11-30 06:41 | 2025-11-30 06:46 | 296 | 2025-11-30 06:41 | 2025-11-30 06:46 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006457764 | External Reconciliation | Site Down | P3 | IHS_OYO_0049C | OY4195 | IBD | Ibadan | Oyo | 3 - Low | OY1434 | WEST |  | 2025-11-26 13:11 | Titus Tosin | 2025-11-26 13:11 | 2025-11-26 13:15 | 269 | 2025-11-26 13:11 | 2025-11-26 13:16 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Olapo Adebunmi |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006480262 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0914A | T3791 | IBD | Asaba | Edo | 3 - Low | ED1074 | SOUTH SOUTH |  | 2025-11-29 13:52 | Azeezat Badmus | 2025-11-29 13:50 | 2025-11-29 13:55 | 295 | 2025-11-29 13:50 | 2025-11-29 13:55 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006441528 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 15:41 | Oluwatomisin Sogbesan | 2025-11-24 15:39 | 2025-11-24 15:44 | 295 | 2025-11-24 15:39 | 2025-11-24 15:44 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006466788 | External Reconciliation | Site Down | P3 | IHS_EDO_1184H | ED2105 | IBD | Asaba | Edo | 3 - Low | ED0862 | SOUTH SOUTH |  | 2025-11-27 17:35 | Elizabeth Apata | 2025-11-27 17:32 | 2025-11-27 17:37 | 295 | 2025-11-27 17:32 | 2025-11-27 17:37 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006482263 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0893A | T3570 | IBD | Ibadan | Oyo | 3 - Low | OY0127 | WEST |  | 2025-11-29 18:59 | Valentine Adinnu | 2025-11-29 18:56 | 2025-11-29 19:01 | 294 | 2025-11-29 18:56 | 2025-11-29 19:01 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Effiong Asukwo |  |  | Paul Akpomie | Effiong Asukwo |  | Victor Olanrewaju | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 4 | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006485707 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0798A | T3252 | IBD | Asaba | Edo | 3 - Low | ED0184 | SOUTH SOUTH | 4G ZTE Sitedown@2025-11-30 09:29:41@ED0184(50184) | 2025-11-30 09:43 | System Administrator | 2025-11-30 09:30 | 2025-11-30 09:35 | 294 | 2025-11-30 09:30 | 2025-11-30 09:35 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006446621 | External Reconciliation | Site Down | P2 | IHS_OYO_1108C | OY4428 | IBD | Ibadan | Oyo | 3 - Low | OY1225 | WEST |  | 2025-11-25 09:36 | Victor Otugo | 2025-11-25 09:33 | 2025-11-25 09:37 | 294 | 2025-11-25 09:33 | 2025-11-25 09:37 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006465169 | External Reconciliation | Site Down | P2 | IHS_ILO_0003B | KW2385 | IBD | Ibadan | Kwara | 3 - Low | KW0428 | WEST |  | 2025-11-27 13:40 | Okusanya Joseph | 2025-11-27 13:39 | 2025-11-27 13:44 | 293 | 2025-11-27 13:39 | 2025-11-27 13:44 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006456706 | External Reconciliation | Site Down | P3 | IHS_EDO_0906A | T3377 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 10:47 | Azeezat Badmus | 2025-11-26 10:46 | 2025-11-26 10:51 | 293 | 2025-11-26 10:46 | 2025-11-26 10:51 | 0:05 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed to start alarm was cleared (No diesel outage after validation) | Failed to start alarm was cleared (No diesel outage after validation)
NOCINC0006458404 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-26 14:53 | Akachukwu Ugwu | 2025-11-26 14:53 | 2025-11-26 14:53 | 52 | 2025-11-26 14:49 | 2025-11-26 14:53 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006470930 | External Reconciliation | Site Down | P1 | IHS_OYO_0006B | OY2982 | IBD | Ibadan | Oyo | 3 - Low | OY0755 | WEST | 4G ZTE Sitedown@2025-11-28 09:15:55@OY0755(30755) | 2025-11-28 09:28 | System Administrator | 2025-11-28 09:16 | 2025-11-28 09:21 | 292 | 2025-11-28 09:16 | 2025-11-28 09:21 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | Airtel NG |  | Mosunmola Christopher |  | Oluwasegun Adebayo | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006487594 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1324B | OY1034 | IBD | Ibadan | Oyo | 3 - Low | OY1686 | WEST |  | 2025-11-30 14:43 | Victor Otugo | 2025-11-30 14:42 | 2025-11-30 14:46 | 291 | 2025-11-30 14:42 | 2025-11-30 14:46 | 0:05 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 2 / 2 | MTN NG, Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Voltage fluctuation due to weak bub at site
NOCINC0006466638 | External Reconciliation | Site Down | P3 | IHS_ANA_1224A | AN0563 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 17:10 | Femi Olanipekun | 2025-11-27 17:10 | 2025-11-27 17:15 | 290 | 2025-11-27 17:10 | 2025-11-27 17:15 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006450910 | External Reconciliation | Site Down | P2 | IHS_DEL_0877A | T2772 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 18:45 | Tracy Osarumwense | 2025-11-25 18:45 | 2025-11-25 18:49 | 290 | 2025-11-25 18:45 | 2025-11-25 18:49 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006462804 | External Reconciliation | Site Down | P2 | IHS_KWA_0767A | T3145 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 07:18 | Precious Attah | 2025-11-27 07:17 | 2025-11-27 07:21 | 290 | 2025-11-27 07:17 | 2025-11-27 07:21 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006444145 | External Reconciliation | Site Down | P3 | IHS_OYO_1118C | OY6537 | IBD | Ibadan | Oyo | 3 - Low | OY1490 | WEST |  | 2025-11-24 21:52 | Valentine Adinnu | 2025-11-24 21:49 | 2025-11-24 21:54 | 288 | 2025-11-24 21:49 | 2025-11-24 21:54 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006481635 | Internal Reconciliation | Site Down | P1 | IHS_ILO_0702E | KW3800 | IBD | Ibadan | Kwara | 3 - Low | KW0402 | WEST |  | 2025-11-29 17:09 | Ayodele Oludare | 2025-11-29 17:07 | 2025-11-29 17:12 | 287 | 2025-11-29 17:07 | 2025-11-29 17:12 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Patrick Kwasi |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Site came up without any technical intervention
NOCINC0006447856 | External Reconciliation | Site Down | P2 | IHS_OSU_0849A | OS3974 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 11:59 | Marvellous Emecheta | 2025-11-25 11:57 | 2025-11-25 12:01 | 287 | 2025-11-25 11:57 | 2025-11-25 12:01 | 0:05 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ajibade Sikiru |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Short duration outage, site was up with no intervention.
NOCINC0006462938 | External Reconciliation | Site Down | P2 | IHS_OYO_1342B | OY1037 | IBD | Ibadan | Oyo | 3 - Low | OY1185 | WEST |  | 2025-11-27 07:48 | Victor Otugo | 2025-11-27 07:44 | 2025-11-27 07:48 | 287 | 2025-11-27 07:44 | 2025-11-27 07:48 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006466174 | External Reconciliation | Site Down | P2 | IHS_AWK_0026B | AN0740 | ASB | Asaba | Anambra | 3 - Low | AN0500 | SOUTH EAST |  | 2025-11-27 15:58 | Gbemisola Adedeji | 2025-11-27 15:55 | 2025-11-27 16:00 | 286 | 2025-11-27 15:55 | 2025-11-27 16:00 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Moses Kenechukwu | Kenneth Ogbodo | Kenneth Ogbodo | Fady Safwat | Aliyu Garuba |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006449049 | External Reconciliation | Site Down | P1 | IHS_DEL_1127A | DL0578 | ASB | Asaba | Delta | 3 - Low | DL1184 | SOUTH SOUTH |  | 2025-11-25 14:26 | Oluwatobiloba Are | 2025-11-25 14:26 | 2025-11-25 14:31 | 286 | 2025-11-25 14:26 | 2025-11-25 14:31 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Kenneth Oboniye |  |  | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006448494 | External Reconciliation | Site Down | P4 | IHS_EDO_1066C | ED6132 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 13:22 | Oluwatomisin Sogbesan | 2025-11-25 13:20 | 2025-11-25 13:25 | 286 | 2025-11-25 13:20 | 2025-11-25 13:25 | 0:05 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006489054 | Internal Reconciliation | Site Down | P1 | IHS_WAR_0869H | DL0348 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 18:31 | Tracy Osarumwense | 2025-11-30 18:29 | 2025-11-30 18:33 | 286 | 2025-11-30 18:29 | 2025-11-30 18:33 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006489977 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0828A | T2692 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 21:54 | Quadri Ogundare | 2025-11-30 21:54 | 2025-11-30 21:59 | 286 | 2025-11-30 21:54 | 2025-11-30 21:59 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 6 | Site cleared without any technical intervention
NOCINC0006481873 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0726E | T3055 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 17:39 | Aishat Oyedeji | 2025-11-29 17:37 | 2025-11-29 17:41 | 285 | 2025-11-29 17:37 | 2025-11-29 17:41 | 0:05 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  | Solomon Apute | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, no intervention
NOCINC0006467979 | External Reconciliation | Site Down | P3 | IHS_ANA_1224A | AN0563 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 21:14 | Patrick Okoro | 2025-11-27 21:14 | 2025-11-27 21:19 | 285 | 2025-11-27 21:14 | 2025-11-27 21:19 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006465392 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 14:12 | Elizabeth Apata | 2025-11-27 14:10 | 2025-11-27 14:14 | 285 | 2025-11-27 14:10 | 2025-11-27 14:14 | 0:05 | Huawei | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Frozen Orion CSU was reset (No diesel outage after validation)
NOCINC0006470650 | External Reconciliation | Site Down | P1 | IHS_ANA_0908A | T4099 | ASB | Asaba | Anambra | 3 - Low | AN0964 | SOUTH EAST |  | 2025-11-28 08:50 | Gbemisola Adedeji | 2025-11-28 08:47 | 2025-11-28 08:52 | 284 | 2025-11-28 08:47 | 2025-11-28 08:52 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006450403 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 17:09 | Oluwadara Bankole | 2025-11-25 17:07 | 2025-11-25 17:12 | 284 | 2025-11-25 17:07 | 2025-11-25 17:12 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006441027 | External Reconciliation | Site Down | P1 | IHS_SAP_0005B | DL0717 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 14:46 | Tracy Osarumwense | 2025-11-24 14:41 | 2025-11-24 14:45 | 284 | 2025-11-24 14:41 | 2025-11-24 14:45 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006478013 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1120A | DL0718 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 08:52 | Solomon Bankole | 2025-11-29 08:51 | 2025-11-29 08:56 | 284 | 2025-11-29 08:51 | 2025-11-29 08:56 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without any technical intervention | Site came up without any technical intervention
NOCINC0006460831 | External Reconciliation | Site Down | P4 | IHS_OYO_1077K | OY2888 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 21:37 | Victor Otugo | 2025-11-26 21:34 | 2025-11-26 21:39 | 284 | 2025-11-26 21:34 | 2025-11-26 21:39 | 0:05 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Bus Voltage | 1 / 1 | MTN NG |  | Olaitan Olajide | Habeeb Adepoju |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | low bus voltage alarm was cleared from the control module.
NOCINC0006488040 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0847A | T2695 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 15:49 | Tracy Osarumwense | 2025-11-30 15:49 | 2025-11-30 15:53 | 283 | 2025-11-30 15:49 | 2025-11-30 15:53 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006443405 | External Reconciliation | Site Down | P3 | IHS_OSU_0009B | OS2689 | IBD | Ibadan | Osun | 3 - Low | OS0690 | WEST |  | 2025-11-24 19:48 | Hardy Oko | 2025-11-24 19:45 | 2025-11-24 19:49 | 283 | 2025-11-24 19:45 | 2025-11-24 19:49 | 0:05 | Energy Vision Nigeria | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Abiola Olanilokun |  |  | Oladotun Ogunleye | Osas Sunday |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006464851 | External Reconciliation | Site Down | P1 | IHS_DEL_0906A | T2725 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 12:53 | Femi Olanipekun | 2025-11-27 12:53 | 2025-11-27 12:57 | 283 | 2025-11-27 12:53 | 2025-11-27 12:57 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 6 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006480752 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0768A | T3147 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-29 14:58 | Ayodele Oludare | 2025-11-29 14:58 | 2025-11-29 15:02 | 283 | 2025-11-29 14:58 | 2025-11-29 15:02 | 0:05 | Huawei | Grid Supply | Passive | Grid | National Grid - Unstable Grid Supply Issue | 1 / 1 | MTN NG |  | Oyenini Olalekan |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Grid to DG synchronization failure due to unstable grid supply, DG was Powered manually
NOCINC0006449347 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 15:03 | Emmanuel Faleti | 2025-11-25 15:01 | 2025-11-25 15:06 | 282 | 2025-11-25 15:01 | 2025-11-25 15:06 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006458611 | External Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-26 15:21 | Marvellous Emecheta | 2025-11-26 15:19 | 2025-11-26 15:24 | 282 | 2025-11-26 15:19 | 2025-11-26 15:24 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006448276 | External Reconciliation | Site Down | P1 | IHS_WAR_0006B | DL0089 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 12:53 | Tracy Osarumwense | 2025-11-25 12:51 | 2025-11-25 12:56 | 282 | 2025-11-25 12:51 | 2025-11-25 12:56 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006463494 | External Reconciliation | Site Down | P3 | IHS_ONT_0006B | AN0316 | ASB | Asaba | Anambra | 3 - Low | AN0588 | SOUTH EAST |  | 2025-11-27 09:53 | Akachukwu Ugwu | 2025-11-27 09:51 | 2025-11-27 09:55 | 282 | 2025-11-27 09:51 | 2025-11-27 09:55 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006465695 | External Reconciliation | Site Down | P4 | IHS_OSU_0075B | OS4391 | IBD | Ibadan | Osun | 3 - Low | OS0757 | WEST |  | 2025-11-27 14:52 | Oluwatomisin Ogunleye | 2025-11-27 14:50 | 2025-11-27 14:55 | 282 | 2025-11-27 14:50 | 2025-11-27 14:55 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Abdulsalami Onukaba Onukaba |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site restored without technical intervention
NOCINC0006441600 | External Reconciliation | Site Down | P3 | IHS_OSU_0988C | OS4729 | IBD | Ibadan | Osun | 3 - Low | OS0941 | WEST |  | 2025-11-24 15:55 | Azeezat Adekunle | 2025-11-24 15:51 | 2025-11-24 15:56 | 281 | 2025-11-24 15:51 | 2025-11-24 15:56 | 0:05 | Energy Vision Nigeria | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Osas Sunday |  |  | Oladotun Ogunleye | Osas Sunday |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006462458 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 05:49 | Oluwadara Bankole | 2025-11-27 05:46 | 2025-11-27 05:50 | 281 | 2025-11-27 05:46 | 2025-11-27 05:50 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006449301 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 14:54 | Emmanuel Faleti | 2025-11-25 14:53 | 2025-11-25 14:58 | 281 | 2025-11-25 14:53 | 2025-11-25 14:58 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006467912 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 20:57 | Tunji Adejumo | 2025-11-27 20:56 | 2025-11-27 21:01 | 281 | 2025-11-27 20:56 | 2025-11-27 21:01 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006486944 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1190A | DL0432 | ASB | Asaba | Delta | 3 - Low | DL0565 | SOUTH SOUTH |  | 2025-11-30 13:09 | Ayomide Akindolie | 2025-11-30 13:09 | 2025-11-30 13:14 | 280 | 2025-11-30 13:09 | 2025-11-30 13:14 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006464895 | External Reconciliation | Site Down | P3 | IHS_ANA_1223A | AN0706 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 12:57 | Akachukwu Ugwu | 2025-11-27 12:52 | 2025-11-27 12:57 | 280 | 2025-11-27 12:52 | 2025-11-27 12:57 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006463655 | External Reconciliation | Site Down | P2 | IHS_DEL_1034A | DL0318 | ASB | Asaba | Delta | 3 - Low | DL0721 | SOUTH SOUTH |  | 2025-11-27 10:22 | Femi Olanipekun | 2025-11-27 10:22 | 2025-11-27 10:26 | 280 | 2025-11-27 10:22 | 2025-11-27 10:26 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Gabriel Akhamiogu |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006472619 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0832A | KW2329 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 13:46 | Praise Okezie | 2025-11-28 13:43 | 2025-11-28 13:48 | 280 | 2025-11-28 13:43 | 2025-11-28 13:48 | 0:05 | Energy Vision Nigeria | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Abubakar Saheed |  |  | Nosakhare Imade | Sani Nasir |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006476404 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0874A | KW2380 | ABJ | Ibadan | Niger | 3 - Low | - | - |  | 2025-11-28 23:44 | Titus Tosin | 2025-11-28 23:44 | 2025-11-28 23:49 | 279 | 2025-11-28 23:44 | 2025-11-28 23:49 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Victor Agahiu |  |  | Soye West | Oboh Oseyeieomo |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006461527 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 00:07 | Oluwadara Bankole | 2025-11-27 00:05 | 2025-11-27 00:09 | 279 | 2025-11-27 00:05 | 2025-11-27 00:09 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006483931 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0878A | T3596 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-30 00:14 | Okusanya Joseph | 2025-11-30 00:11 | 2025-11-30 00:16 | 279 | 2025-11-30 00:11 | 2025-11-30 00:16 | 0:05 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006451438 | External Reconciliation | Site Down | P2 | IHS_ILO_0003B | KW2385 | IBD | Ibadan | Kwara | 3 - Low | KW0428 | WEST |  | 2025-11-25 20:14 | Precious Attah | 2025-11-25 20:13 | 2025-11-25 20:18 | 279 | 2025-11-25 20:13 | 2025-11-25 20:18 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006457258 | External Reconciliation | Site Down | P4 | IHS_KWA_0904A | KW4575 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-26 11:53 | Titus Tosin | 2025-11-26 11:48 | 2025-11-26 11:53 | 277 | 2025-11-26 11:48 | 2025-11-26 11:53 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site restored without technical intervention
NOCINC0006488280 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0857A | T3581 | IBD | Ibadan | Oyo | 3 - Low | OY1146 | WEST |  | 2025-11-30 16:25 | Aishat Oyedeji | 2025-11-30 16:25 | 2025-11-30 16:29 | 277 | 2025-11-30 16:25 | 2025-11-30 16:29 | 0:05 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Azeez Salami | Samuel Olaobaju |  | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 10 | Short duration outage, no intervention
NOCINC0006471572 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1044A | DL0415 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 10:59 | Quadri Ogundare | 2025-11-28 10:57 | 2025-11-28 11:01 | 277 | 2025-11-28 10:57 | 2025-11-28 11:01 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site cleared without any technical intervention
NOCINC0006441463 | External Reconciliation | Site Down | P3 | IHS_ANA_1223A | AN0706 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 15:31 | Aderonke Olowojoba | 2025-11-24 15:27 | 2025-11-24 15:32 | 276 | 2025-11-24 15:27 | 2025-11-24 15:32 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006460786 | External Reconciliation | Site Down | P2 | IHS_DEL_0964A | DL2989 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 21:27 | Tracy Osarumwense | 2025-11-26 21:27 | 2025-11-26 21:31 | 276 | 2025-11-26 21:27 | 2025-11-26 21:31 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006462570 | External Reconciliation | Site Down | P4 | IHS_ANA_1174A | AN0558 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-27 06:04:35@AN0558_Ebenato Amichi | 2025-11-27 06:18 | System Administrator | 2025-11-27 06:16 | 2025-11-27 06:20 | 275 | 2025-11-27 06:16 | 2025-11-27 06:20 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006443765 | External Reconciliation | Site Down | P2 | IHS_OYO_1183H | OY2646 | IBD | Ibadan | Oyo | 3 - Low | OY1430 | WEST |  | 2025-11-24 20:52 | Damilola Paseda | 2025-11-24 20:51 | 2025-11-24 20:55 | 274 | 2025-11-24 20:51 | 2025-11-24 20:55 | 0:05 | SPS | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | Oremade Yusuf |  | Iyiola Azeez | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on | Faulty ATS contactor was worked on
NOCINC0006444757 | External Reconciliation | Site Down | P4 | IHS_KWA_1010B | KW6413 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 00:23 | Praise Okezie | 2025-11-25 00:21 | 2025-11-25 00:26 | 274 | 2025-11-25 00:21 | 2025-11-25 00:26 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Olapade Babatunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006446993 | External Reconciliation | Site Down | P3 | IHS_ANA_1286C | AN3020 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 10:28 | Oluwatoyin Fagite | 2025-11-25 10:26 | 2025-11-25 10:31 | 274 | 2025-11-25 10:26 | 2025-11-25 10:31 | 0:05 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukanwa Reginald | Ukanwa Karachi | Ukanwa Karachi | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006476083 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0922A | T4179 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 22:21 | Akachukwu Ugwu | 2025-11-28 22:19 | 2025-11-28 22:24 | 274 | 2025-11-28 22:19 | 2025-11-28 22:24 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006488786 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 17:48 | Oluwatomisin Sogbesan | 2025-11-30 17:46 | 2025-11-30 17:51 | 273 | 2025-11-30 17:46 | 2025-11-30 17:51 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006474549 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-28 18:24 | Quadri Ogundare | 2025-11-28 18:24 | 2025-11-28 18:28 | 273 | 2025-11-28 18:24 | 2025-11-28 18:28 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006487112 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0870A | T2742 | ASB | Asaba | Delta | 3 - Low | DL1269 | SOUTH SOUTH |  | 2025-11-30 13:26 | Ayomide Akindolie | 2025-11-30 13:26 | 2025-11-30 13:30 | 273 | 2025-11-30 13:26 | 2025-11-30 13:30 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006440642 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-24 13:50 | Tracy Osarumwense | 2025-11-24 13:49 | 2025-11-24 13:54 | 273 | 2025-11-24 13:49 | 2025-11-24 13:54 | 0:05 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006482777 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0875A | OS3995 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-29 20:35 | Okusanya Joseph | 2025-11-29 20:34 | 2025-11-29 20:39 | 273 | 2025-11-29 20:34 | 2025-11-29 20:39 | 0:05 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006469630 | External Reconciliation | Site Down | P4 | IHS_DEL_1235B | - | - | Asaba | Delta | 3 - Low | DL0956 | SOUTH SOUTH | 4G ZTE Sitedown@2025-11-28 03:19:29@DL0956(80956) | 2025-11-28 03:31 | System Administrator | 2025-11-28 03:19 | 2025-11-28 03:24 | 273 | 2025-11-28 03:19 | 2025-11-28 03:24 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Kehinde Adekanbi |  |  | Erik Nwodo | John Wekpe |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006446670 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 09:42 | Oluwadara Bankole | 2025-11-25 09:40 | 2025-11-25 09:44 | 273 | 2025-11-25 09:40 | 2025-11-25 09:44 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006462573 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 06:19 | Oluwadara Bankole | 2025-11-27 06:16 | 2025-11-27 06:20 | 272 | 2025-11-27 06:16 | 2025-11-27 06:20 | 0:05 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006475100 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0765A | T3131 | IBD | Ibadan | Kwara | 3 - Low | KW0362 | WEST |  | 2025-11-28 19:52 | Okusanya Joseph | 2025-11-28 19:52 | 2025-11-28 19:56 | 271 | 2025-11-28 19:52 | 2025-11-28 19:56 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006446702 | External Reconciliation | Site Down | P1 | IHS_EDO_0866A | T3317 | IBD | Asaba | Edo | 3 - Low | ED0177 | SOUTH SOUTH |  | 2025-11-25 09:48 | Oluwatomisin Sogbesan | 2025-11-25 09:45 | 2025-11-25 09:50 | 271 | 2025-11-25 09:45 | 2025-11-25 09:50 | 0:05 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adekoya Adetunji |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006463397 | External Reconciliation | Site Down | P2 | IHS_OSU_0089C | OS4333 | IBD | Ibadan | Osun | 3 - Low | OS0974 | WEST |  | 2025-11-27 09:40 | Oluwatomisin Ogunleye | 2025-11-27 09:37 | 2025-11-27 09:42 | 270 | 2025-11-27 09:37 | 2025-11-27 09:42 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adejumobi Tunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Short duration outage, site restored without technical intervention
NOCINC0006463442 | External Reconciliation | Site Down | P4 | IHS_OYO_1453B | OY1054 | IBD | Ibadan | Oyo | 3 - Low | OY0942 | WEST |  | 2025-11-27 09:46 | Bosede Kutelu | 2025-11-27 09:43 | 2025-11-27 09:48 | 270 | 2025-11-27 09:43 | 2025-11-27 09:48 | 0:04 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | BASHIR ABDULRASAQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006462148 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-27 03:44 | Precious Attah | 2025-11-27 03:42 | 2025-11-27 03:46 | 270 | 2025-11-27 03:42 | 2025-11-27 03:46 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006461426 | External Reconciliation | Site Down | P3 | IHS_OYO_0046C | OY4165 | IBD | Ibadan | Oyo | 3 - Low | OY1036 | WEST |  | 2025-11-26 23:46 | Victor Otugo | 2025-11-26 23:43 | 2025-11-26 23:47 | 270 | 2025-11-26 23:43 | 2025-11-26 23:47 | 0:04 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olaitan Olajide | John Eze | John Eze | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006477633 | Internal Reconciliation | Site Down | P1 | IHS_ANA_1011A | T4869 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 07:29 | Akachukwu Ugwu | 2025-11-29 07:28 | 2025-11-29 07:32 | 269 | 2025-11-29 07:28 | 2025-11-29 07:32 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006477418 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1174A | AN0558 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 06:33 | Akachukwu Ugwu | 2025-11-29 06:31 | 2025-11-29 06:36 | 269 | 2025-11-29 06:31 | 2025-11-29 06:36 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006456192 | External Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-26 09:22 | Marvellous Emecheta | 2025-11-26 09:19 | 2025-11-26 09:23 | 269 | 2025-11-26 09:19 | 2025-11-26 09:23 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006450304 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 16:53 | Emmanuel Faleti | 2025-11-25 16:53 | 2025-11-25 16:57 | 269 | 2025-11-25 16:53 | 2025-11-25 16:57 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006465410 | External Reconciliation | Site Down | P1 | IHS_DEL_0711E | - | - | Asaba | Delta | 3 - Low | DL0562 | SOUTH SOUTH |  | 2025-11-27 14:15 | Mary Odefemi | 2025-11-27 14:15 | 2025-11-27 14:19 | 269 | 2025-11-27 14:15 | 2025-11-27 14:19 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006482078 | Internal Reconciliation | Site Down | P3 | IHS_EDO_1106C | ED5327 | IBD | Asaba | Edo | 3 - Low | ED0632 | SOUTH SOUTH |  | 2025-11-29 18:23 | Azeezat Badmus | 2025-11-29 18:22 | 2025-11-29 18:26 | 269 | 2025-11-29 18:22 | 2025-11-29 18:26 | 0:04 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 2 | Airtel NG |  | EKPU SUNDAY | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Hybrid synchronization delay. DG powered automatically (No diesel outage after validation)
NOCINC0006459784 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 18:41 | Azeezat Badmus | 2025-11-26 18:39 | 2025-11-26 18:44 | 268 | 2025-11-26 18:39 | 2025-11-26 18:44 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | site cleared with no technical intervention
NOCINC0006466020 | External Reconciliation | Site Down | P4 | IHS_ANA_0912A | T4176 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 15:35 | Gbemisola Adedeji | 2025-11-27 15:34 | 2025-11-27 15:38 | 268 | 2025-11-27 15:34 | 2025-11-27 15:38 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006478074 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0738E | OS2707 | IBD | Ibadan | Osun | 3 - Low | OS0934 | WEST |  | 2025-11-29 09:07 | Ayodele Oludare | 2025-11-29 09:05 | 2025-11-29 09:10 | 268 | 2025-11-29 09:05 | 2025-11-29 09:10 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006466774 | External Reconciliation | Site Down | P4 | IHS_KWA_0768A | T3147 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 17:31 | Okusanya Joseph | 2025-11-27 17:31 | 2025-11-27 17:36 | 268 | 2025-11-27 17:31 | 2025-11-27 17:36 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oyenini Olalekan |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006461673 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 00:24 | Oluwatomisin Sogbesan | 2025-11-27 00:21 | 2025-11-27 00:25 | 267 | 2025-11-27 00:21 | 2025-11-27 00:25 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006459854 | External Reconciliation | Site Down | P2 | IHS_KWA_0767A | T3145 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-26 18:51 | Titus Tosin | 2025-11-26 18:51 | 2025-11-26 18:55 | 267 | 2025-11-26 18:51 | 2025-11-26 18:55 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006486173 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1129A | DL0674 | ASB | Asaba | Delta | 3 - Low | DL1031 | SOUTH SOUTH |  | 2025-11-30 11:15 | Ayomide Akindolie | 2025-11-30 11:15 | 2025-11-30 11:20 | 266 | 2025-11-30 11:15 | 2025-11-30 11:20 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006441720 | External Reconciliation | Site Down | P2 | IHS_ILO_0003B | KW2385 | IBD | Ibadan | Kwara | 3 - Low | KW0428 | WEST |  | 2025-11-24 16:18 | Azeezat Adekunle | 2025-11-24 16:17 | 2025-11-24 16:21 | 266 | 2025-11-24 16:17 | 2025-11-24 16:21 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006489420 | Internal Reconciliation | Site Down | P4 | IHS_EDO_1071C | ED6141 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 19:56 | Evelyn Emagurehor | 2025-11-30 19:54 | 2025-11-30 19:59 | 265 | 2025-11-30 19:54 | 2025-11-30 19:59 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006448531 | External Reconciliation | Site Down | P2 | IHS_DEL_0829A | T2689 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 13:26 | Ezinne Ubachukwu | 2025-11-25 13:23 | 2025-11-25 13:28 | 265 | 2025-11-25 13:23 | 2025-11-25 13:28 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Wisdom Chukwudi |  |  | Akanbi Oluwafemi | Elochukwu Umeohana |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006461154 | External Reconciliation | Site Down | P2 | IHS_EDO_0734E | ED5189 | IBD | Asaba | Edo | 3 - Low | ED0645 | SOUTH SOUTH |  | 2025-11-26 22:37 | Oluwatomisin Sogbesan | 2025-11-26 22:37 | 2025-11-26 22:41 | 264 | 2025-11-26 22:37 | 2025-11-26 22:41 | 0:04 | Huawei | Equipment Replacement | Passive | ACDG Gen | ACDG - Compression | 2 / 2 | Airtel NG, MTN NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Weak Dg primed to start (No diesel outage after validation) | Weak Dg primed to start (No diesel outage after validation)
NOCINC0006465157 | External Reconciliation | Site Down | P1 | IHS_DEL_0940A | T2439 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 13:37 | Bukola Olabanji | 2025-11-27 13:34 | 2025-11-27 13:39 | 264 | 2025-11-27 13:34 | 2025-11-27 13:39 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | SHORT DURATION OUTAGE
NOCINC0006443333 | External Reconciliation | Site Down | P2 | IHS_KWA_0902A | KW4577 | IBD | Ibadan | Kwara | 3 - Low | KW0457 | WEST |  | 2025-11-24 19:33 | Precious Attah | 2025-11-24 19:32 | 2025-11-24 19:36 | 264 | 2025-11-24 19:32 | 2025-11-24 19:36 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Site came up without any technical intervention
NOCINC0006476619 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1324B | OY1034 | IBD | Ibadan | Oyo | 3 - Low | OY1686 | WEST |  | 2025-11-29 01:10 | Bosede Kutelu | 2025-11-29 01:08 | 2025-11-29 01:12 | 263 | 2025-11-29 01:08 | 2025-11-29 01:12 | 0:04 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006474038 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0914A | T3791 | IBD | Asaba | Edo | 3 - Low | ED1074 | SOUTH SOUTH |  | 2025-11-28 17:10 | Muhammed Hashirudeen | 2025-11-28 17:07 | 2025-11-28 17:12 | 263 | 2025-11-28 17:07 | 2025-11-28 17:12 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006466986 | External Reconciliation | Site Down | P3 | IHS_SAP_0007B | DL0491 | ASB | Asaba | Delta | 3 - Low | DL0913 | SOUTH SOUTH |  | 2025-11-27 18:10 | Mary Odefemi | 2025-11-27 18:10 | 2025-11-27 18:14 | 263 | 2025-11-27 18:10 | 2025-11-27 18:14 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006457227 | External Reconciliation | Site Down | P3 | IHS_OYO_0925A | T3872 | IBD | Ibadan | Oyo | 3 - Low | OY1270 | WEST |  | 2025-11-26 11:51 | Titus Tosin | 2025-11-26 11:49 | 2025-11-26 11:54 | 262 | 2025-11-26 11:49 | 2025-11-26 11:54 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Fatunwase Samuel |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify | 1 | Short duration outage. Site was up with no intervention
NOCINC0006460018 | External Reconciliation | Site Down | P2 | IHS_OYO_1342B | OY1037 | IBD | Ibadan | Oyo | 3 - Low | OY1185 | WEST |  | 2025-11-26 19:14 | Bosede Kutelu | 2025-11-26 19:14 | 2025-11-26 19:18 | 268 | 2025-11-26 19:14 | 2025-11-26 19:18 | 0:04 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006471546 | Internal Reconciliation | Site Down | P4 | IHS_OND_0848A | T3949 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 10:53 | Olawale Adeyemo | 2025-11-28 10:50 | 2025-11-28 10:54 | 262 | 2025-11-28 10:50 | 2025-11-28 10:54 | 0:04 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Start Failure | 1 / 1 | MTN NG |  | Marvellous Oyefeso | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | DG start failure alarm was cleared
NOCINC0006449816 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - | CSL Fault@2025-11-25 15:51:51@T3263_BDPA_Benin | 2025-11-25 16:05 | System Administrator | 2025-11-25 16:03 | 2025-11-25 16:07 | 261 | 2025-11-25 16:03 | 2025-11-25 16:07 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006462298 | External Reconciliation | Site Down | P2 | IHS_KWA_0767A | T3145 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 04:59 | Precious Attah | 2025-11-27 04:59 | 2025-11-27 05:03 | 260 | 2025-11-27 04:59 | 2025-11-27 05:03 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Moses Adedigba |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006486869 | Internal Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-30 12:53 | Tracy Osarumwense | 2025-11-30 12:50 | 2025-11-30 12:55 | 260 | 2025-11-30 12:50 | 2025-11-30 12:55 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006443735 | External Reconciliation | Site Down | P4 | IHS_KWA_0903A | KW4576 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 20:45 | Praise Okezie | 2025-11-24 20:42 | 2025-11-24 20:47 | 259 | 2025-11-24 20:42 | 2025-11-24 20:47 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006440176 | External Reconciliation | Site Down | P1 | IHS_ONT_0072B | AN0873 | ASB | Asaba | Anambra | 3 - Low | AN0675 | SOUTH EAST |  | 2025-11-24 13:06 | Ezinne Ubachukwu | 2025-11-24 13:05 | 2025-11-24 13:09 | 259 | 2025-11-24 13:05 | 2025-11-24 13:09 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006446755 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 09:58 | Tunji Adejumo | 2025-11-25 09:57 | 2025-11-25 10:02 | 259 | 2025-11-25 09:57 | 2025-11-25 10:02 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006441666 | External Reconciliation | Site Down | P4 | IHS_EDO_1233B | ED5512 | IBD | Asaba | Edo | 3 - Low | ED0858 | SOUTH SOUTH |  | 2025-11-24 16:08 | Evelyn Emagurehor | 2025-11-24 16:08 | 2025-11-24 16:12 | 259 | 2025-11-24 16:08 | 2025-11-24 16:12 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ismail Adeyinka | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006484324 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0870A | T2742 | ASB | Asaba | Delta | 3 - Low | DL1269 | SOUTH SOUTH |  | 2025-11-30 03:06 | Bukola Olabanji | 2025-11-30 03:04 | 2025-11-30 03:08 | 259 | 2025-11-30 03:04 | 2025-11-30 03:08 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006445483 | External Reconciliation | Site Down | P3 | IHS_OYO_0965A | T3822 | IBD | Ibadan | Oyo | 3 - Low | OY1123 | WEST |  | 2025-11-25 05:59 | Valentine Adinnu | 2025-11-25 05:57 | 2025-11-25 06:01 | 259 | 2025-11-25 05:57 | 2025-11-25 06:01 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Alaba |  |  | Paul Akpomie | Oluwaseun Alaba |  | Luke Eke | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006450691 | External Reconciliation | Site Down | P3 | IHS_BEN_0015V | ED5180 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 18:04 | Oluwatomisin Sogbesan | 2025-11-25 18:04 | 2025-11-25 18:06 | 139 | 2025-11-25 18:02 | 2025-11-25 18:06 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ismail Adeyinka |  |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006459149 | External Reconciliation | Site Down | P3 | IHS_OND_1046B | OD6258 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 16:45 | Mary Elaigwu | 2025-11-26 16:43 | 2025-11-26 16:47 | 258 | 2025-11-26 16:43 | 2025-11-26 16:47 | 0:04 | Biswal | Equipment Repair | Passive | DCGG Gen | DCGG - Gen Voltage | 1 / 1 | MTN NG |  | Anawanti Kingsley | Isah Ahmed |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Fluntuating voltage due to weak BUB | Fluctuating voltage due to weak bub
NOCINC0006461911 | External Reconciliation | Site Down | P1 | IHS_OSU_0903A | OS3648 | IBD | Ibadan | Osun | 3 - Low | OS0695 | WEST |  | 2025-11-27 01:36 | Victor Otugo | 2025-11-27 01:29 | 2025-11-27 01:33 | 258 | 2025-11-27 01:29 | 2025-11-27 01:33 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006463546 | External Reconciliation | Site Down | P2 | IHS_OYO_1342B | OY1037 | IBD | Ibadan | Oyo | 3 - Low | OY1185 | WEST |  | 2025-11-27 10:02 | Bosede Kutelu | 2025-11-27 09:59 | 2025-11-27 10:03 | 258 | 2025-11-27 09:59 | 2025-11-27 10:03 | 0:04 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006447084 | External Reconciliation | Site Down | P3 | IHS_DEL_1236B | - | - | Asaba | Delta | 3 - Low | DL0945 | SOUTH SOUTH |  | 2025-11-25 10:39 | Tracy Osarumwense | 2025-11-25 10:39 | 2025-11-25 10:43 | 258 | 2025-11-25 10:39 | 2025-11-25 10:43 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Kehinde Adekanbi |  |  | Erik Nwodo | John Wekpe |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006459587 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-26 18:05 | Tunji Adejumo | 2025-11-26 18:04 | 2025-11-26 18:08 | 258 | 2025-11-26 18:04 | 2025-11-26 18:08 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006447800 | External Reconciliation | Site Down | P3 | IHS_ANA_1223A | AN0706 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 11:51 | Oluwatoyin Fagite | 2025-11-25 11:48 | 2025-11-25 11:53 | 257 | 2025-11-25 11:48 | 2025-11-25 11:53 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006481446 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0704E | ED2050 | IBD | Asaba | Edo | 3 - Low | ED0482 | SOUTH SOUTH |  | 2025-11-29 16:40 | Azeezat Badmus | 2025-11-29 16:40 | 2025-11-29 16:44 | 257 | 2025-11-29 16:40 | 2025-11-29 16:44 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | EKPU SUNDAY |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | site cleared with no technical intervention
NOCINC0006449784 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 16:01 | Tunji Adejumo | 2025-11-25 16:00 | 2025-11-25 16:04 | 257 | 2025-11-25 16:00 | 2025-11-25 16:04 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006447877 | External Reconciliation | Site Down | P2 | IHS_OYO_0003B | - | - | Ibadan | Oyo | 3 - Low | OY1230 | WEST | Cascaded Incident from TTO6730956 - Cascade Removed From TTO6730956 | 2025-11-25 12:01 | Victor Otugo | 2025-11-25 11:57 | 2025-11-25 12:02 | 257 | 2025-11-25 11:57 | 2025-11-25 12:02 | 0:04 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 4 | Airtel NG |  | Adebiyi Ridwan |  |  | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006438261 | External Reconciliation | Site Down | P2 | IHS_OYO_0856A | T3588 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 07:23 | Okusanya Joseph | 2025-11-24 07:22 | 2025-11-24 07:27 | 257 | 2025-11-24 07:22 | 2025-11-24 07:27 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006481112 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-29 15:51 | Favour Ahize | 2025-11-29 15:48 | 2025-11-29 15:52 | 256 | 2025-11-29 15:48 | 2025-11-29 15:52 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short Duration Outage
NOCINC0006465726 | External Reconciliation | Site Down | P4 | IHS_ANA_0985A | T4171 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-27 14:45:39@T4171_Adumike s plot | 2025-11-27 14:58 | System Administrator | 2025-11-27 14:51 | 2025-11-27 14:55 | 256 | 2025-11-27 14:51 | 2025-11-27 14:55 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006465700 | External Reconciliation | Site Down | P4 | IHS_ANA_1066A | AN0089 | ASB | Asaba | Anambra | 3 - Low | AN1122 | SOUTH EAST |  | 2025-11-27 14:54 | Gbemisola Adedeji | 2025-11-27 14:51 | 2025-11-27 14:55 | 256 | 2025-11-27 14:51 | 2025-11-27 14:55 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Adams Uthman | Adams Uthman | Adams Uthman | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006439433 | External Reconciliation | Site Down | P3 | IHS_OYO_0017B | OY4082 | IBD | Ibadan | Oyo | 3 - Low | OY1149 | WEST |  | 2025-11-24 11:07 | Victor Otugo | 2025-11-24 11:05 | 2025-11-24 11:09 | 256 | 2025-11-24 11:05 | 2025-11-24 11:09 | 0:04 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Aramide Kazeem |  | Aramide Kazeem | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention
NOCINC0006448146 | External Reconciliation | Site Down | P1 | IHS_ANA_1048A | AN0024 | ASB | Asaba | Anambra | 3 - Low | AN0523 | SOUTH EAST |  | 2025-11-25 12:36 | Oluwatoyin Fagite | 2025-11-25 12:34 | 2025-11-25 12:38 | 255 | 2025-11-25 12:34 | 2025-11-25 12:38 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ugochuku Agbamuche | Ugo Agamuche | Ugo Agamuche | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006485268 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1095A | DL0508 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 08:24 | Uthman Akinola | 2025-11-30 08:22 | 2025-11-30 08:26 | 255 | 2025-11-30 08:22 | 2025-11-30 08:26 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site inter-fail and clear without any technical intervention. | Site inter-fail and clear without any technical intervention.
NOCINC0006451105 | External Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-25 19:09 | Marvellous Emecheta | 2025-11-25 19:05 | 2025-11-25 19:09 | 254 | 2025-11-25 19:05 | 2025-11-25 19:09 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006467365 | External Reconciliation | Site Down | P1 | IHS_OYO_0806A | T3020 | IBD | Ibadan | Oyo | 3 - Low | OY1607 | WEST |  | 2025-11-27 19:17 | Bosede Kutelu | 2025-11-27 19:13 | 2025-11-27 19:17 | 253 | 2025-11-27 19:13 | 2025-11-27 19:17 | 0:04 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006464233 | External Reconciliation | Site Down | P4 | IHS_EDO_1255B | ED5539 | IBD | Asaba | Edo | 3 - Low | ED1140 | SOUTH SOUTH |  | 2025-11-27 11:35 | Elizabeth Apata | 2025-11-27 11:33 | 2025-11-27 11:38 | 253 | 2025-11-27 11:33 | 2025-11-27 11:38 | 0:04 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | Airtel NG, MTN NG |  | Kazeem Ajiboye |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006470253 | External Reconciliation | Site Down | P1 | IHS_DEL_1034A | DL0318 | ASB | Asaba | Delta | 3 - Low | DL0721 | SOUTH SOUTH |  | 2025-11-28 07:13 | Patrick Okoro | 2025-11-28 07:13 | 2025-11-28 07:17 | 252 | 2025-11-28 07:13 | 2025-11-28 07:17 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Gabriel Akhamiogu |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site cleared without intervention | Site cleared without intervention
NOCINC0006473836 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0042B | OS4285 | IBD | Ibadan | Osun | 3 - Low | OS0738 | WEST |  | 2025-11-28 16:44 | Okusanya Joseph | 2025-11-28 16:44 | 2025-11-28 16:48 | 252 | 2025-11-28 16:44 | 2025-11-28 16:48 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006443722 | External Reconciliation | Site Down | P4 | IHS_WAR_0766C | DL0543 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 20:42 | Quadri Ogundare | 2025-11-24 20:42 | 2025-11-24 20:46 | 252 | 2025-11-24 20:42 | 2025-11-24 20:46 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006468308 | External Reconciliation | Site Down | P2 | IHS_DEL_1026A | DL0309 | ASB | Asaba | Delta | 3 - Low | DL1020 | SOUTH SOUTH |  | 2025-11-27 22:10 | Patrick Okoro | 2025-11-27 22:09 | 2025-11-27 22:13 | 252 | 2025-11-27 22:09 | 2025-11-27 22:13 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | MTN NG |  | Gabriel Akhamiogu |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006449912 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 16:22 | Tunji Adejumo | 2025-11-25 16:21 | 2025-11-25 16:25 | 251 | 2025-11-25 16:21 | 2025-11-25 16:25 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006488463 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1445B | - | - | Ibadan | Oyo | 3 - Low | OY1535 | WEST |  | 2025-11-30 16:57 | Aishat Oyedeji | 2025-11-30 16:56 | 2025-11-30 17:00 | 250 | 2025-11-30 16:56 | 2025-11-30 17:00 | 0:04 | Energy Vision Nigeria | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adewole Olumuyiwa |  |  | Oladotun Ogunleye | Banje Oluwaseun |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006440170 | External Reconciliation | Site Down | P2 | IHS_OYO_1278H | OY4461 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 13:06 | Azeezat Adekunle | 2025-11-24 13:06 | 2025-11-24 13:10 | 250 | 2025-11-24 13:06 | 2025-11-24 13:10 | 0:04 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006487244 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-30 13:35 | Favour Ahize | 2025-11-30 13:32 | 2025-11-30 13:36 | 250 | 2025-11-30 13:32 | 2025-11-30 13:36 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short Duration Outage
NOCINC0006487907 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1023A | DL0328 | ASB | Asaba | Delta | 3 - Low | DL1072 | SOUTH SOUTH | Cascaded Incident from TTO6775346 - Cascade Removed From TTO6775346 | 2025-11-30 15:25 | Tracy Osarumwense | 2025-11-30 15:23 | 2025-11-30 15:27 | 250 | 2025-11-30 15:23 | 2025-11-30 15:27 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention. Site came up without technical intervention.
NOCINC0006468098 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 21:36 | Tunji Adejumo | 2025-11-27 21:34 | 2025-11-27 21:38 | 250 | 2025-11-27 21:34 | 2025-11-27 21:38 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006479048 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1160A | DL0489 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 11:28 | Quadri Ogundare | 2025-11-29 11:27 | 2025-11-29 11:31 | 249 | 2025-11-29 11:27 | 2025-11-29 11:31 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006448656 | External Reconciliation | Site Down | P3 | IHS_EKW_0002B | AN0663 | ASB | Asaba | Anambra | 3 - Low | AN0616 | SOUTH EAST |  | 2025-11-25 13:41 | Oluwatoyin Fagite | 2025-11-25 13:37 | 2025-11-25 13:41 | 248 | 2025-11-25 13:37 | 2025-11-25 13:41 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Harrison Igbinedion | Harrison Igbinedion | Harrison Igbinedion | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006459309 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 17:12 | Oluwatobiloba Are | 2025-11-26 17:08 | 2025-11-26 17:12 | 248 | 2025-11-26 17:08 | 2025-11-26 17:12 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006457862 | External Reconciliation | Site Down | P1 | IHS_OYO_0806A | T3020 | IBD | Ibadan | Oyo | 3 - Low | OY1607 | WEST |  | 2025-11-26 13:30 | Bosede Kutelu | 2025-11-26 13:28 | 2025-11-26 13:32 | 248 | 2025-11-26 13:28 | 2025-11-26 13:32 | 0:04 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006487595 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0778C | DL0666 | ASB | Asaba | Delta | 3 - Low | DL0561 | SOUTH SOUTH |  | 2025-11-30 14:43 | Tracy Osarumwense | 2025-11-30 14:43 | 2025-11-30 14:47 | 248 | 2025-11-30 14:43 | 2025-11-30 14:47 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006438089 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-24 06:30 | Okusanya Joseph | 2025-11-24 06:28 | 2025-11-24 06:32 | 248 | 2025-11-24 06:28 | 2025-11-24 06:32 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006473538 | Internal Reconciliation | Site Down | P1 | IHS_OSU_0780A | T3090 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 16:05 | Damilola Paseda | 2025-11-28 16:04 | 2025-11-28 16:08 | 248 | 2025-11-28 16:04 | 2025-11-28 16:08 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006468464 | External Reconciliation | Site Down | P1 | IHS_OYO_0908A | T3862 | IBD | Ibadan | Oyo | 3 - Low | OY0975 | WEST | Cascaded Incident from TTO6753670 - Cascade Removed From TTO6753670 | 2025-11-27 22:37 | Ifechi Ugwueze | 2025-11-27 22:33 | 2025-11-27 22:37 | 248 | 2025-11-27 22:33 | 2025-11-27 22:37 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Samuel Dada |  |  | Paul Akpomie | Samuel Dada |  | Abayomi Adeniyi | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006439118 | External Reconciliation | Site Down | P4 | IHS_DEL_1204B | DL4068 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 09:58 | Ezinne Ubachukwu | 2025-11-24 09:55 | 2025-11-24 09:59 | 248 | 2025-11-24 09:55 | 2025-11-24 09:59 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006436683 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-24 00:39 | Ayodele Oludare | 2025-11-24 00:36 | 2025-11-24 00:40 | 247 | 2025-11-24 00:36 | 2025-11-24 00:40 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | site came up without intervention
NOCINC0006463575 | External Reconciliation | Site Down | P1 | IHS_EDO_0936A | ED2004 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 10:08 | Muhammed Hashirudeen | 2025-11-27 10:07 | 2025-11-27 10:11 | 246 | 2025-11-27 10:07 | 2025-11-27 10:11 | 0:04 | Huawei | Equipment Repair | Passive | Hybrid | Hybrid Software | 1 / 1 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Hybrid synchronization failure. DG powered manually. (No diesel outage after validation)
NOCINC0006467949 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 21:07 | Tunji Adejumo | 2025-11-27 21:06 | 2025-11-27 21:10 | 246 | 2025-11-27 21:06 | 2025-11-27 21:10 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006487869 | Internal Reconciliation | Site Down | P1 | IHS_OSU_0969A | OS2662 | IBD | Ibadan | Osun | 3 - Low | OS0685 | WEST |  | 2025-11-30 15:19 | Precious Attah | 2025-11-30 15:19 | 2025-11-30 15:23 | 246 | 2025-11-30 15:19 | 2025-11-30 15:23 | 0:04 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Generator Faulty | 2 / 2 | MTN NG, Airtel NG |  | Tobiloba Oladejo |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Suspected passive Issue on site, Awaiting update from FSE
NOCINC0006488937 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 18:09 | Evelyn Emagurehor | 2025-11-30 18:09 | 2025-11-30 18:13 | 245 | 2025-11-30 18:09 | 2025-11-30 18:13 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006461910 | External Reconciliation | Site Down | P4 | IHS_OND_0716E | OD6010 | IBD | Ibadan | Ondo | 3 - Low | ON0832 | WEST |  | 2025-11-27 01:34 | Oluwadara Bankole | 2025-11-27 01:32 | 2025-11-27 01:36 | 244 | 2025-11-27 01:32 | 2025-11-27 01:36 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Sanusi Idowu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006466895 | External Reconciliation | Site Down | P4 | IHS_DEL_0710E | DL0584 | ASB | Asaba | Delta | 3 - Low | DL1140 | SOUTH SOUTH |  | 2025-11-27 17:53 | Mary Odefemi | 2025-11-27 17:53 | 2025-11-27 17:57 | 244 | 2025-11-27 17:53 | 2025-11-27 17:57 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006483006 | Internal Reconciliation | Site Down | P2 | IHS_AWK_0002B | AN3769 | ASB | Asaba | Anambra | 3 - Low | AN0451 | SOUTH EAST |  | 2025-11-29 21:15 | Gbemisola Adedeji | 2025-11-29 21:12 | 2025-11-29 21:16 | 243 | 2025-11-29 21:12 | 2025-11-29 21:16 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ugwuja Chinonso |  |  | Erik Nwodo | Nwigbo Chijioke |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006465397 | External Reconciliation | Site Down | P2 | IHS_OYO_0810A | T3002 | IBD | Ibadan | Oyo | 3 - Low | OY1028 | WEST | 4G ZTE Sitedown@2025-11-27 14:00:14@OY1028(31028) | 2025-11-27 14:13 | System Administrator | 2025-11-27 14:00 | 2025-11-27 14:04 | 242 | 2025-11-27 14:00 | 2025-11-27 14:04 | 0:04 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mosunmola Christopher |  |  | Ridwan Adepoju | Ahmed Ibrahim |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006480440 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1190A | DL0432 | ASB | Asaba | Delta | 3 - Low | DL0565 | SOUTH SOUTH |  | 2025-11-29 14:14 | Ayomide Akindolie | 2025-11-29 14:14 | 2025-11-29 14:18 | 242 | 2025-11-29 14:14 | 2025-11-29 14:18 | 0:04 | BJ Bison NGA | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited (No diesel outage after validation) | Failed charging alternator was excited (No diesel outage after validation)
NOCINC0006480783 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-29 15:02 | Ayomide Akindolie | 2025-11-29 15:01 | 2025-11-29 15:05 | 241 | 2025-11-29 15:01 | 2025-11-29 15:05 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006478072 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-29 09:07 | Favour Ahize | 2025-11-29 09:04 | 2025-11-29 09:08 | 241 | 2025-11-29 09:04 | 2025-11-29 09:08 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short Duration Outage
NOCINC0006450911 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 18:45 | Emmanuel Faleti | 2025-11-25 18:44 | 2025-11-25 18:48 | 241 | 2025-11-25 18:44 | 2025-11-25 18:48 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006481363 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0704E | ED2050 | IBD | Asaba | Edo | 3 - Low | ED0482 | SOUTH SOUTH |  | 2025-11-29 16:28 | Evelyn Emagurehor | 2025-11-29 16:26 | 2025-11-29 16:30 | 241 | 2025-11-29 16:26 | 2025-11-29 16:30 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | EKPU SUNDAY |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006455975 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 08:35 | Oluwatobiloba Are | 2025-11-26 08:34 | 2025-11-26 08:38 | 241 | 2025-11-26 08:34 | 2025-11-26 08:38 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Short duration outage, site came up without technical intervention
NOCINC0006461522 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-27 00:06 | Precious Attah | 2025-11-27 00:05 | 2025-11-27 00:09 | 240 | 2025-11-27 00:05 | 2025-11-27 00:09 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006481997 | Internal Reconciliation | Site Down | P3 | IHS_OYO_0954A | T3659 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 18:05 | Testimony Akinyemi | 2025-11-29 18:02 | 2025-11-29 18:06 | 240 | 2025-11-29 18:02 | 2025-11-29 18:06 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Muhammad Aliyu |  |  | Paul Akpomie | Muhammad Aliyu |  | Uche Kanu | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify | 1 | SHORT DURATION OUTAGE
NOCINC0006468054 | External Reconciliation | Site Down | P4 | IHS_DEL_1078A | DL0413 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 21:29 | Patrick Okoro | 2025-11-27 21:28 | 2025-11-27 21:31 | 191 | 2025-11-27 21:27 | 2025-11-27 21:31 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006449466 | External Reconciliation | Site Down | P4 | IHS_ANA_0967A | T4101 | ASB | Asaba | Anambra | 3 - Low | AN1074 | SOUTH EAST |  | 2025-11-25 15:17 | Ezinne Ubachukwu | 2025-11-25 15:16 | 2025-11-25 15:20 | 240 | 2025-11-25 15:16 | 2025-11-25 15:20 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Usman Bala |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006454448 | External Reconciliation | Site Down | P3 | IHS_OND_0056B | OD4760 | IBD | Ibadan | Ondo | 3 - Low | ON0600 | WEST |  | 2025-11-26 01:22 | Testimony Akinyemi | 2025-11-26 01:19 | 2025-11-26 01:23 | 240 | 2025-11-26 01:19 | 2025-11-26 01:23 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Sanusi Idowu |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | short duration outage
NOCINC0006445999 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 08:34 | Ezinne Ubachukwu | 2025-11-25 08:32 | 2025-11-25 08:36 | 239 | 2025-11-25 08:32 | 2025-11-25 08:36 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006471538 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0770A | T3143 | IBD | Ibadan | Kwara | 3 - Low | KW0568 | WEST |  | 2025-11-28 10:52 | Okusanya Joseph | 2025-11-28 10:52 | 2025-11-28 10:53 | 77 | 2025-11-28 10:52 | 2025-11-28 10:56 | 0:04 | IPT | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | Airtel NG, MTN NG |  | Abdulrasaq Yusuf |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006465609 | External Reconciliation | Site Down | P1 | IHS_DEL_0945A | T4110 | ASB | Asaba | Delta | 3 - Low | DL0641 | SOUTH SOUTH |  | 2025-11-27 14:42 | Femi Olanipekun | 2025-11-27 14:42 | 2025-11-27 14:46 | 239 | 2025-11-27 14:42 | 2025-11-27 14:46 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | MTN NG |  | Gabriel Akhamiogu |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006445431 | External Reconciliation | Site Down | P2 | IHS_OND_0809A | T3451 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-25 05:44 | Maureen Uchehorke | 2025-11-25 05:44 | 2025-11-25 05:48 | 239 | 2025-11-25 05:44 | 2025-11-25 05:48 | 0:04 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Anawanti Kingsley |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Joshua Afolayan | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006465849 | External Reconciliation | Site Down | P3 | IHS_ANA_1316B | AN3147 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 15:18 | Gbemisola Adedeji | 2025-11-27 15:15 | 2025-11-27 15:19 | 239 | 2025-11-27 15:15 | 2025-11-27 15:19 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006486212 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1142A | DL0762 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 11:23 | Ezinne Ubachukwu | 2025-11-30 11:19 | 2025-11-30 11:23 | 239 | 2025-11-30 11:19 | 2025-11-30 11:23 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006489422 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 19:56 | Tracy Osarumwense | 2025-11-30 19:54 | 2025-11-30 19:58 | 239 | 2025-11-30 19:54 | 2025-11-30 19:58 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006459646 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-26 18:18 | Tunji Adejumo | 2025-11-26 18:18 | 2025-11-26 18:22 | 239 | 2025-11-26 18:18 | 2025-11-26 18:22 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006451034 | External Reconciliation | Site Down | P1 | IHS_WAR_0740C | DL1063 | ASB | Asaba | Delta | 3 - Low | DL0937 | SOUTH SOUTH |  | 2025-11-25 19:05 | Ezinne Ubachukwu | 2025-11-25 19:03 | 2025-11-25 19:07 | 239 | 2025-11-25 19:03 | 2025-11-25 19:07 | 0:04 | Tyllium NGA | Equipment Repair | Passive | Rectifier | Rectifier - Controller Failure | 2 / 2 | Airtel NG, MTN NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Frozen orion was reset (No diesel outage after validation) | Frozen orion was rest (No diesel outage after validation)
NOCINC0006466381 | External Reconciliation | Site Down | P1 | IHS_ONT_0021B | AN0403 | ASB | Asaba | Anambra | 3 - Low | AN0619 | SOUTH EAST |  | 2025-11-27 16:29 | Femi Olanipekun | 2025-11-27 16:28 | 2025-11-27 16:32 | 238 | 2025-11-27 16:28 | 2025-11-27 16:32 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Amadi Fabian | Tijani Haruna | Tijani Haruna | Henry Wanogho | Ifeanyi Chukusa |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006446180 | External Reconciliation | Site Down | P1 | IHS_DEL_1053A | DL0414 | ASB | Asaba | Delta | 3 - Low | DL0724 | SOUTH SOUTH |  | 2025-11-25 09:03 | Tracy Osarumwense | 2025-11-25 09:03 | 2025-11-25 09:07 | 237 | 2025-11-25 09:03 | 2025-11-25 09:07 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006451896 | External Reconciliation | Site Down | P4 | IHS_OYO_0975A | T3575 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 21:03 | Ihuoma Opurum | 2025-11-25 21:01 | 2025-11-25 21:05 | 237 | 2025-11-25 21:01 | 2025-11-25 21:05 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Muhammad Aliyu |  |  | Paul Akpomie | Muhammad Aliyu |  | Uche Kanu | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site was restored without intervention.
NOCINC0006450536 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 17:33 | Emmanuel Faleti | 2025-11-25 17:32 | 2025-11-25 17:36 | 237 | 2025-11-25 17:32 | 2025-11-25 17:36 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006446490 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 09:17 | Oluwadara Bankole | 2025-11-25 09:13 | 2025-11-25 09:17 | 237 | 2025-11-25 09:13 | 2025-11-25 09:17 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006449649 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 15:44 | Oluwadara Bankole | 2025-11-25 15:43 | 2025-11-25 15:47 | 237 | 2025-11-25 15:43 | 2025-11-25 15:47 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006462167 | External Reconciliation | Site Down | P3 | IHS_OYO_1417B | - | - | Ibadan | Oyo | 3 - Low | OY1310 | WEST |  | 2025-11-27 03:50 | Victor Otugo | 2025-11-27 03:49 | 2025-11-27 03:53 | 237 | 2025-11-27 03:49 | 2025-11-27 03:53 | 0:04 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Enoch Fidelis |  |  | Abiola Adegbiji | Habeeb Adepoju |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006441036 | External Reconciliation | Site Down | P1 | IHS_DEL_0774A | T2613 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 14:47 | Tracy Osarumwense | 2025-11-24 14:46 | 2025-11-24 14:50 | 235 | 2025-11-24 14:46 | 2025-11-24 14:50 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006457141 | External Reconciliation | Site Down | P2 | IHS_OND_0971A | OD4735 | IBD | Ibadan | Ondo | 3 - Low | ON0729 | WEST |  | 2025-11-26 11:42 | Iyesioluwa Ola | 2025-11-26 11:41 | 2025-11-26 11:45 | 235 | 2025-11-26 11:41 | 2025-11-26 11:45 | 0:04 | Inhouse | Equipment Repair | Passive | ACDG Gen | ACDG - Charging Alternator | 2 / 2 | MTN NG, Airtel NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Failed charging alternator was excited
NOCINC0006445363 | External Reconciliation | Site Down | P1 | IHS_OYO_0911A | T3989 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 05:13 | Praise Okezie | 2025-11-25 05:12 | 2025-11-25 05:16 | 235 | 2025-11-25 05:12 | 2025-11-25 05:16 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Short duration outage, site was up with no intervention.
NOCINC0006460000 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-26 19:12 | Tunji Adejumo | 2025-11-26 19:11 | 2025-11-26 19:15 | 235 | 2025-11-26 19:11 | 2025-11-26 19:15 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006459892 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-26 18:59 | Tunji Adejumo | 2025-11-26 18:58 | 2025-11-26 19:02 | 235 | 2025-11-26 18:58 | 2025-11-26 19:02 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006438281 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-24 07:30 | Okusanya Joseph | 2025-11-24 07:28 | 2025-11-24 07:32 | 235 | 2025-11-24 07:28 | 2025-11-24 07:32 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006463540 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-27 10:01 | Bukola Olabanji | 2025-11-27 10:00 | 2025-11-27 10:04 | 234 | 2025-11-27 10:00 | 2025-11-27 10:04 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006488038 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-30 15:48 | Favour Ahize | 2025-11-30 15:46 | 2025-11-30 15:50 | 234 | 2025-11-30 15:46 | 2025-11-30 15:50 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short Duration Outage
NOCINC0006467981 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 21:15 | Tunji Adejumo | 2025-11-27 21:14 | 2025-11-27 21:18 | 233 | 2025-11-27 21:14 | 2025-11-27 21:18 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006471379 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1066A | AN0089 | ASB | Asaba | Anambra | 3 - Low | AN1122 | SOUTH EAST |  | 2025-11-28 10:35 | Gbemisola Adedeji | 2025-11-28 10:32 | 2025-11-28 10:36 | 233 | 2025-11-28 10:32 | 2025-11-28 10:36 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Adams Uthman | Adams Uthman | Adams Uthman | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006461087 | External Reconciliation | Site Down | P3 | IHS_OSU_0843A | T3623 | IBD | Ibadan | Osun | 3 - Low | OS0725 | WEST |  | 2025-11-26 22:19 | Hardy Oko | 2025-11-26 22:17 | 2025-11-26 22:21 | 233 | 2025-11-26 22:17 | 2025-11-26 22:21 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Bayo Nathaniel |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006489794 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0940A | T2439 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 21:17 | Quadri Ogundare | 2025-11-30 21:17 | 2025-11-30 21:21 | 233 | 2025-11-30 21:17 | 2025-11-30 21:21 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site cleared without any intervention
NOCINC0006448482 | External Reconciliation | Site Down | P3 | IHS_ILO_0048B | KW1403 | IBD | Ibadan | Kwara | 3 - Low | KW0312 | WEST |  | 2025-11-25 13:19 | Mutmainnah Saba | 2025-11-25 13:14 | 2025-11-25 13:18 | 232 | 2025-11-25 13:14 | 2025-11-25 13:18 | 0:04 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mohammed Soliu |  |  | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006476627 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-29 01:13 | Ihuoma Opurum | 2025-11-29 01:10 | 2025-11-29 01:14 | 232 | 2025-11-29 01:10 | 2025-11-29 01:14 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was restored without intervention.
NOCINC0006447388 | External Reconciliation | Site Down | P1 | IHS_DEL_1026A | DL0309 | ASB | Asaba | Delta | 3 - Low | DL1020 | SOUTH SOUTH |  | 2025-11-25 11:09 | Ezinne Ubachukwu | 2025-11-25 11:07 | 2025-11-25 11:11 | 231 | 2025-11-25 11:07 | 2025-11-25 11:11 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | MTN NG |  | Gabriel Akhamiogu |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006450408 | External Reconciliation | Site Down | P4 | IHS_KWA_0903A | KW4576 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 17:10 | Precious Attah | 2025-11-25 17:08 | 2025-11-25 17:12 | 231 | 2025-11-25 17:08 | 2025-11-25 17:12 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006448229 | External Reconciliation | Site Down | P4 | IHS_KWA_1024C | KW6468 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 12:46 | Precious Attah | 2025-11-25 12:46 | 2025-11-25 12:50 | 231 | 2025-11-25 12:46 | 2025-11-25 12:50 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006467426 | External Reconciliation | Site Down | P3 | IHS_ANA_1061A | AN4165 | ASB | Asaba | Anambra | 3 - Low | AN0863 | SOUTH EAST |  | 2025-11-27 19:33 | Akachukwu Ugwu | 2025-11-27 19:31 | 2025-11-27 19:34 | 231 | 2025-11-27 19:31 | 2025-11-27 19:34 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Harrison Igbinedion | Harrison Igbinedion | Harrison Igbinedion | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006449505 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 15:24 | Emmanuel Faleti | 2025-11-25 15:23 | 2025-11-25 15:27 | 230 | 2025-11-25 15:23 | 2025-11-25 15:27 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006450586 | External Reconciliation | Site Down | P4 | IHS_EDO_1048C | ED6125 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 17:42 | Tracy Osarumwense | 2025-11-25 17:42 | 2025-11-25 17:45 | 230 | 2025-11-25 17:42 | 2025-11-25 17:45 | 0:04 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006470557 | External Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 08:30 | Bukola Olabanji | 2025-11-28 08:27 | 2025-11-28 08:31 | 230 | 2025-11-28 08:27 | 2025-11-28 08:31 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006458010 | External Reconciliation | Site Down | P3 | IHS_OYO_1120C | OY6533 | IBD | Ibadan | Oyo | 3 - Low | OY1144 | WEST |  | 2025-11-26 13:55 | Marvellous Emecheta | 2025-11-26 13:54 | 2025-11-26 13:58 | 229 | 2025-11-26 13:54 | 2025-11-26 13:58 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006479978 | Internal Reconciliation | Site Down | P4 | IHS_PAT_0002B | KW4563 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-29 13:18 | Ayodele Oludare | 2025-11-29 13:16 | 2025-11-29 13:20 | 229 | 2025-11-29 13:16 | 2025-11-29 13:20 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | site came up without intervention
NOCINC0006479422 | Internal Reconciliation | Site Down | P4 | IHS_OND_0032B | OD2436 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-29 12:08 | Maureen Uchehorke | 2025-11-29 12:07 | 2025-11-29 12:11 | 229 | 2025-11-29 12:07 | 2025-11-29 12:11 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Abdulsalami Onukaba Onukaba |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006466973 | External Reconciliation | Site Down | P4 | IHS_KWA_0884A | KW2372 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 18:06 | Abisoye Olaleye | 2025-11-27 18:02 | 2025-11-27 18:06 | 229 | 2025-11-27 18:02 | 2025-11-27 18:06 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adelola Dagunduro |  |  | Paul Akpomie | Adelola Dagunduro |  | Rilwan Akeem | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was restored without technical intervention
NOCINC0006483770 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0855A | KW3816 | IBD | Ibadan | Kwara | 3 - Low | KW0436 | WEST |  | 2025-11-29 23:26 | Okusanya Joseph | 2025-11-29 23:26 | 2025-11-29 23:30 | 229 | 2025-11-29 23:26 | 2025-11-29 23:30 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Olapade Babatunde |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006437663 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 04:13 | Muhammed Hashirudeen | 2025-11-24 04:13 | 2025-11-24 04:17 | 227 | 2025-11-24 04:13 | 2025-11-24 04:17 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site restored without intervention.
NOCINC0006450483 | External Reconciliation | Site Down | P3 | IHS_WAR_0931B | DL3321 | ASB | Asaba | Delta | 3 - Low | DL0845 | SOUTH SOUTH |  | 2025-11-25 17:24 | Oluwatobiloba Are | 2025-11-25 17:21 | 2025-11-25 17:25 | 227 | 2025-11-25 17:21 | 2025-11-25 17:25 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006449684 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 15:51 | Oluwadara Bankole | 2025-11-25 15:51 | 2025-11-25 15:55 | 226 | 2025-11-25 15:51 | 2025-11-25 15:55 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006459614 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-26 18:12 | Tunji Adejumo | 2025-11-26 18:10 | 2025-11-26 18:14 | 225 | 2025-11-26 18:10 | 2025-11-26 18:14 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006442935 | External Reconciliation | Site Down | P4 | IHS_EDO_1106C | ED5327 | IBD | Asaba | Edo | 3 - Low | ED0632 | SOUTH SOUTH |  | 2025-11-24 18:27 | Evelyn Emagurehor | 2025-11-24 18:26 | 2025-11-24 18:30 | 224 | 2025-11-24 18:26 | 2025-11-24 18:30 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | EKPU SUNDAY | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006461396 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-26 23:35 | Oluwadara Bankole | 2025-11-26 23:33 | 2025-11-26 23:36 | 224 | 2025-11-26 23:33 | 2025-11-26 23:36 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006457377 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-26 12:18 | Tunji Adejumo | 2025-11-26 12:17 | 2025-11-26 12:21 | 224 | 2025-11-26 12:17 | 2025-11-26 12:21 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006466582 | External Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 17:03 | Femi Olanipekun | 2025-11-27 17:03 | 2025-11-27 17:07 | 223 | 2025-11-27 17:03 | 2025-11-27 17:07 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006441558 | External Reconciliation | Site Down | P2 | IHS_KWA_0902A | KW4577 | IBD | Ibadan | Kwara | 3 - Low | KW0457 | WEST |  | 2025-11-24 15:47 | Azeezat Adekunle | 2025-11-24 15:46 | 2025-11-24 15:50 | 222 | 2025-11-24 15:46 | 2025-11-24 15:50 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Site came up without any technical intervention
NOCINC0006485194 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0908A | T4099 | ASB | Asaba | Anambra | 3 - Low | AN0964 | SOUTH EAST |  | 2025-11-30 08:03 | Gbemisola Adedeji | 2025-11-30 08:01 | 2025-11-30 08:04 | 222 | 2025-11-30 08:01 | 2025-11-30 08:04 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006473924 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1273C | AN0434 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 16:54 | Kehinde Akinbowale | 2025-11-28 16:51 | 2025-11-28 16:55 | 222 | 2025-11-28 16:51 | 2025-11-28 16:55 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | NNADOZIE CASMIR |  |  | Erik Nwodo | Nwigbo Chijioke |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006477881 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 08:35 | Ayomide Akindolie | 2025-11-29 08:34 | 2025-11-29 08:38 | 222 | 2025-11-29 08:34 | 2025-11-29 08:38 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006442825 | External Reconciliation | Site Down | P4 | IHS_DEL_1210B | DL4082 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 18:14 | Ezinne Ubachukwu | 2025-11-24 18:10 | 2025-11-24 18:14 | 222 | 2025-11-24 18:10 | 2025-11-24 18:14 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Osayamwen Eghosa |  |  | Erik Nwodo | John Wekpe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006484847 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0966A | T2440 | PHC | Asaba | Delta | 3 - Low | - | - | ZTE 3G SiteDown@2025-11-30 06:17:13@T2440 | 2025-11-30 06:30 | System Administrator | 2025-11-30 06:27 | 2025-11-30 06:31 | 221 | 2025-11-30 06:27 | 2025-11-30 06:31 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006464363 | External Reconciliation | Site Down | P3 | IHS_ANA_1223A | AN0706 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 11:54 | Gbemisola Adedeji | 2025-11-27 11:52 | 2025-11-27 11:55 | 221 | 2025-11-27 11:52 | 2025-11-27 11:55 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006439313 | External Reconciliation | Site Down | P3 | IHS_EDO_1321B | - | - | Asaba | Edo | 3 - Low | ED0833 | SOUTH SOUTH |  | 2025-11-24 10:41 | Evelyn Emagurehor | 2025-11-24 10:39 | 2025-11-24 10:43 | 221 | 2025-11-24 10:39 | 2025-11-24 10:43 | 0:04 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Asukwo Effiong | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006485957 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1142A | DL0762 | ASB | Asaba | Delta | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-30 10:25:26@ | 2025-11-30 10:38 | System Administrator | 2025-11-30 10:25 | 2025-11-30 10:29 | 221 | 2025-11-30 10:25 | 2025-11-30 10:29 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter-fail and clear without any technical intervention.
NOCINC0006479207 | Internal Reconciliation | Site Down | P1 | IHS_KWA_0963H | KW4970 | - | Ibadan | Kwara | 3 - Low | KW0053 | WEST |  | 2025-11-29 11:41 | Ayodele Oludare | 2025-11-29 11:39 | 2025-11-29 11:43 | 220 | 2025-11-29 11:39 | 2025-11-29 11:43 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oyenini Olalekan |  |  | Soye West | Goddey Nwokedigbo Peter |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | site came up without intervention
NOCINC0006489013 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 18:23 | Oluwatomisin Sogbesan | 2025-11-30 18:23 | 2025-11-30 18:26 | 220 | 2025-11-30 18:23 | 2025-11-30 18:26 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006449571 | External Reconciliation | Site Down | P3 | IHS_OSU_0063B | OS2656 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 15:33 | Hardy Oko | 2025-11-25 15:31 | 2025-11-25 15:34 | 219 | 2025-11-25 15:31 | 2025-11-25 15:34 | 0:04 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Abdulsalami Onukaba Onukaba |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006488468 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0914A | OS2618 | IBD | Ibadan | Osun | 3 - Low | OS0679 | WEST |  | 2025-11-30 16:58 | Precious Attah | 2025-11-30 16:57 | 2025-11-30 17:00 | 219 | 2025-11-30 16:57 | 2025-11-30 17:00 | 0:04 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ben Johnson-Nsikan |  |  | Abiola Adegbiji | Babalola Babajide |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006458842 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 15:50 | Azeezat Badmus | 2025-11-26 15:50 | 2025-11-26 15:54 | 219 | 2025-11-26 15:50 | 2025-11-26 15:54 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | site cleared with no intervention
NOCINC0006466183 | External Reconciliation | Site Down | P4 | IHS_ANA_1476B | AN3662 | ASB | Asaba | Anambra | 3 - Low | AN0867 | SOUTH EAST |  | 2025-11-27 15:59 | Gbemisola Adedeji | 2025-11-27 15:57 | 2025-11-27 16:01 | 218 | 2025-11-27 15:57 | 2025-11-27 16:01 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Moses Kenechukwu | Kenneth Ogbodo | Kenneth Ogbodo | Fady Safwat | Aliyu Garuba |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006465038 | External Reconciliation | Site Down | P1 | IHS_ANA_1269C | AN0044 | ASB | Asaba | Anambra | 3 - Low | AN0794 | SOUTH EAST |  | 2025-11-27 13:21 | Uthman Akinola | 2025-11-27 13:21 | 2025-11-27 13:25 | 218 | 2025-11-27 13:21 | 2025-11-27 13:25 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006483663 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 22:59 | Muhammed Hashirudeen | 2025-11-29 22:56 | 2025-11-29 22:59 | 217 | 2025-11-29 22:56 | 2025-11-29 22:59 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006485663 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0844A | DL2931 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 09:38 | Tracy Osarumwense | 2025-11-30 09:35 | 2025-11-30 09:39 | 217 | 2025-11-30 09:35 | 2025-11-30 09:39 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 14 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006483914 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-29 23:53:31@T2719_30 Emevor Orogun Road | 2025-11-30 00:08 | System Administrator | 2025-11-29 23:59 | 2025-11-30 00:02 | 217 | 2025-11-29 23:59 | 2025-11-30 00:02 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006480369 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0894A | T4121 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-29 14:04 | Kehinde Akinbowale | 2025-11-29 14:02 | 2025-11-29 14:05 | 217 | 2025-11-29 14:02 | 2025-11-29 14:05 | 0:04 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adams Uthman | Adams Uthman | Adams Uthman | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006464706 | External Reconciliation | Site Down | P1 | IHS_ANA_0897A | T4009 | ASB | Asaba | Anambra | 3 - Low | AN0422 | SOUTH EAST | NE Is Disconnected@2025-11-27 12:09:44@AN0422 | 2025-11-27 12:31 | System Administrator | 2025-11-27 12:10 | 2025-11-27 12:13 | 217 | 2025-11-27 12:10 | 2025-11-27 12:13 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Idowu Dare |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006437626 | External Reconciliation | Site Down | P3 | IHS_ANA_1061A | AN4165 | ASB | Asaba | Anambra | 3 - Low | AN0863 | SOUTH EAST | CSL Fault@2025-11-24 03:39:20@AN4165_Ogboji Road Ekwulobia Aguluchuk | 2025-11-24 03:53 | System Administrator | 2025-11-24 03:48 | 2025-11-24 03:52 | 217 | 2025-11-24 03:48 | 2025-11-24 03:52 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Harrison Igbinedion | Harrison Igbinedion | Harrison Igbinedion | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006485703 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0962A | DL2995 | ASB | Asaba | Delta | 3 - Low | DL0729 | SOUTH SOUTH |  | 2025-11-30 09:43 | Tracy Osarumwense | 2025-11-30 09:41 | 2025-11-30 09:44 | 217 | 2025-11-30 09:41 | 2025-11-30 09:44 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006472291 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0906A | OS3650 | IBD | Ibadan | Osun | 3 - Low | OS0598 | WEST |  | 2025-11-28 12:51 | Valentine Adinnu | 2025-11-28 12:44 | 2025-11-28 12:48 | 216 | 2025-11-28 12:44 | 2025-11-28 12:48 | 0:04 | Huawei | Equipment Repair | Passive | ACDG Gen | ACDG - Load Contactor | 1 / 2 | Airtel NG |  | Olamilekan Akinwale |  |  | Soye West | Ugwu Samuel Nnamdi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Faulty load contactor was replaced | Faulty load contactor was replaced
NOCINC0006487116 | Internal Reconciliation | Site Down | P2 | IHS_OND_0934A | OD2516 | IBD | Ibadan | Ondo | 3 - Low | ON0578 | WEST |  | 2025-11-30 13:27 | Ihuoma Opurum | 2025-11-30 13:26 | 2025-11-30 13:30 | 215 | 2025-11-30 13:26 | 2025-11-30 13:30 | 0:04 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Anawanti Kingsley |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was restored without intervention.
NOCINC0006445860 | External Reconciliation | Site Down | P1 | IHS_ANA_0805A | T4035 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 07:55 | Kehinde Akinbowale | 2025-11-25 07:52 | 2025-11-25 07:56 | 215 | 2025-11-25 07:52 | 2025-11-25 07:56 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006466326 | External Reconciliation | Site Down | P3 | IHS_DEL_1218B | - | - | Asaba | Delta | 3 - Low | DL0903 | SOUTH SOUTH |  | 2025-11-27 16:20 | Mary Odefemi | 2025-11-27 16:20 | 2025-11-27 16:23 | 215 | 2025-11-27 16:20 | 2025-11-27 16:23 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006490422 | Resolved | Site Down | P4 | IHS_EDO_0927A | T3268 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 23:58 | Azeezat Badmus | 2025-11-30 23:56 | 2025-12-01 00:24 | 1639 | 2025-11-30 23:56 | 2025-12-01 | 0:04 | Huawei | Grid Supply | Passive | POFC | POFC - Grid | 1 / 1 | MTN NG |  | Ismail Adeyinka | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | POFC: Site is affected by ED4860. (No diesel outage after validation)
NOCINC0006448849 | External Reconciliation | Site Down | P4 | IHS_WAR_0776C | DL0650 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 13:55 | Tracy Osarumwense | 2025-11-25 13:55 | 2025-11-25 13:58 | 214 | 2025-11-25 13:55 | 2025-11-25 13:58 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006487731 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-30 15:01 | Oluwadara Bankole | 2025-11-30 15:01 | 2025-11-30 15:04 | 213 | 2025-11-30 15:01 | 2025-11-30 15:04 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006462981 | External Reconciliation | Site Down | P2 | IHS_EKI_0856A | EK2285 | IBD | Ibadan | Ekiti | 3 - Low | EK0401 | WEST |  | 2025-11-27 08:03 | Oluwadara Bankole | 2025-11-27 08:00 | 2025-11-27 08:03 | 213 | 2025-11-27 08:00 | 2025-11-27 08:03 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Onewokae Ajiri |  |  | Ibrahim Akinpelu | Onewokae Ajiri |  | Sheriff Bolajoko | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006446705 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 09:48 | Tunji Adejumo | 2025-11-25 09:48 | 2025-11-25 09:52 | 213 | 2025-11-25 09:48 | 2025-11-25 09:52 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006468051 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-27 21:28 | Tunji Adejumo | 2025-11-27 21:27 | 2025-11-27 21:30 | 213 | 2025-11-27 21:27 | 2025-11-27 21:30 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006447111 | External Reconciliation | Site Down | P1 | IHS_EDO_0808A | T3232 | IBD | Asaba | Edo | 3 - Low | ED0739 | SOUTH SOUTH |  | 2025-11-25 10:45 | Oluwatomisin Sogbesan | 2025-11-25 10:45 | 2025-11-25 10:48 | 213 | 2025-11-25 10:45 | 2025-11-25 10:48 | 0:04 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 4 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006467037 | External Reconciliation | Site Down | P3 | IHS_EDO_1106C | ED5327 | IBD | Asaba | Edo | 3 - Low | ED0632 | SOUTH SOUTH |  | 2025-11-27 18:19 | Muhammed Hashirudeen | 2025-11-27 18:19 | 2025-11-27 18:23 | 213 | 2025-11-27 18:19 | 2025-11-27 18:23 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | EKPU SUNDAY | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006469665 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-28 03:53 | Tunji Adejumo | 2025-11-28 03:52 | 2025-11-28 03:55 | 212 | 2025-11-28 03:52 | 2025-11-28 03:55 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006487105 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0970A | T3827 | IBD | Ibadan | Oyo | 3 - Low | OY1352 | WEST |  | 2025-11-30 13:24 | Favour Ahize | 2025-11-30 13:20 | 2025-11-30 13:23 | 212 | 2025-11-30 13:20 | 2025-11-30 13:23 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short Duration Outage
NOCINC0006442861 | External Reconciliation | Site Down | P2 | IHS_DEL_1087A | DL0700 | ASB | Asaba | Delta | 3 - Low | DL0770 | SOUTH SOUTH |  | 2025-11-24 18:16 | Tracy Osarumwense | 2025-11-24 18:15 | 2025-11-24 18:18 | 212 | 2025-11-24 18:15 | 2025-11-24 18:18 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006484956 | Internal Reconciliation | Site Down | P2 | IHS_ONT_0014V | - | - | Asaba | Anambra | 3 - Low | AN0468 | SOUTH EAST | 4G Site Down@2025-11-30 06:38:14@AN0468_L | 2025-11-30 06:55 | System Administrator | 2025-11-30 06:38 | 2025-11-30 06:59 | 1231 | 2025-11-30 06:55 | 2025-11-30 06:59 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006442667 | External Reconciliation | Site Down | P2 | IHS_OYO_1278H | OY4461 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 17:56 | Precious Attah | 2025-11-24 17:56 | 2025-11-24 17:59 | 211 | 2025-11-24 17:56 | 2025-11-24 17:59 | 0:04 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006452219 | External Reconciliation | Site Down | P2 | IHS_DEL_0966A | T2440 | PHC | Asaba | Delta | 3 - Low | - | - | The link between the server and the ME is broken@2025-11-25 21:59:19@T2440 | 2025-11-25 22:12 | System Administrator | 2025-11-25 22:08 | 2025-11-25 22:25 | 1050 | 2025-11-25 22:22 | 2025-11-25 22:25 | 0:04 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006467226 | External Reconciliation | Site Down | P3 | IHS_EKI_0885C | EK6322 | IBD | Ibadan | Ekiti | 3 - Low | EK0442 | WEST |  | 2025-11-27 18:50 | Kandervil Uwah | 2025-11-27 18:47 | 2025-11-27 18:50 | 210 | 2025-11-27 18:47 | 2025-11-27 18:50 | 0:04 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site was up without intervention
NOCINC0006464901 | External Reconciliation | Site Down | P1 | IHS_ANA_1399H | AN0602 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 12:58 | Akachukwu Ugwu | 2025-11-27 12:55 | 2025-11-27 12:58 | 210 | 2025-11-27 12:55 | 2025-11-27 12:58 | 0:04 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006458249 | External Reconciliation | Site Down | P2 | IHS_OSU_0042B | OS4285 | IBD | Ibadan | Osun | 3 - Low | OS0738 | WEST |  | 2025-11-26 14:29 | Titus Tosin | 2025-11-26 14:29 | 2025-11-26 14:32 | 209 | 2025-11-26 14:29 | 2025-11-26 14:32 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006436500 | External Reconciliation | Site Down | P2 | IHS_OYO_1278H | OY4461 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-24 00:06 | Okusanya Joseph | 2025-11-24 00:05 | 2025-11-24 00:08 | 209 | 2025-11-24 00:05 | 2025-11-24 00:08 | 0:03 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006461486 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-26 23:57 | Precious Attah | 2025-11-26 23:56 | 2025-11-27 | 209 | 2025-11-26 23:56 | 2025-11-27 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006440185 | External Reconciliation | Site Down | P1 | IHS_DEL_0886A | T2716 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 13:07 | Tracy Osarumwense | 2025-11-24 13:07 | 2025-11-24 13:11 | 209 | 2025-11-24 13:07 | 2025-11-24 13:11 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006456678 | External Reconciliation | Site Down | P1 | IHS_EDO_0996A | ED4860 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 10:43 | Emmanuel Faleti | 2025-11-26 10:42 | 2025-11-26 10:46 | 209 | 2025-11-26 10:42 | 2025-11-26 10:46 | 0:03 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on (No diesel outage after validation)
NOCINC0006477823 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1002A | DL0086 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 08:20 | Ayokunle Samuel | 2025-11-29 08:16 | 2025-11-29 08:22 | 388 | 2025-11-29 08:19 | 2025-11-29 08:22 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Monday Agha | Igwe Samuel | Igwe Samuel | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention. | Site inter failed and cleared without any technical intervention.
NOCINC0006484027 | Internal Reconciliation | Site Down | P2 | IHS_EDO_0921A | T3795 | IBD | Asaba | Edo | 3 - Low | ED0683 | SOUTH SOUTH |  | 2025-11-30 00:59 | Muhammed Hashirudeen | 2025-11-30 00:56 | 2025-11-30 01:00 | 208 | 2025-11-30 00:56 | 2025-11-30 01:00 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006459064 | External Reconciliation | Site Down | P2 | IHS_IBA_0764E | OY2963 | IBD | Ibadan | Oyo | 3 - Low | OY0940 | WEST |  | 2025-11-26 16:31 | Bosede Kutelu | 2025-11-26 16:28 | 2025-11-26 16:31 | 208 | 2025-11-26 16:28 | 2025-11-26 16:31 | 0:03 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Lukman Mohammed |  | Yunus Ololade | Abiola Adegbiji | Habeeb Adepoju |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Short duration outage. Site was up with no intervention
NOCINC0006487285 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1218B | - | - | Asaba | Delta | 3 - Low | DL0903 | SOUTH SOUTH |  | 2025-11-30 13:47 | Tracy Osarumwense | 2025-11-30 13:47 | 2025-11-30 13:50 | 208 | 2025-11-30 13:47 | 2025-11-30 13:50 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006481467 | Internal Reconciliation | Site Down | P1 | IHS_OSU_0797A | T3032 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-29 16:42 | Favour Ahize | 2025-11-29 16:39 | 2025-11-29 16:43 | 207 | 2025-11-29 16:39 | 2025-11-29 16:43 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | John Olasupo |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short Duration Outage
NOCINC0006451281 | External Reconciliation | Site Down | P3 | IHS_LFG_0001B | KW4585 | IBD | Ibadan | Kwara | 3 - Low | KW0412 | WEST |  | 2025-11-25 19:57 | Precious Attah | 2025-11-25 19:54 | 2025-11-25 19:58 | 207 | 2025-11-25 19:54 | 2025-11-25 19:58 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006452925 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 00:25 | Ayomide Akindolie | 2025-11-26 00:24 | 2025-11-26 00:28 | 207 | 2025-11-26 00:24 | 2025-11-26 00:28 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006443215 | External Reconciliation | Site Down | P2 | IHS_KWA_0902A | KW4577 | IBD | Ibadan | Kwara | 3 - Low | KW0457 | WEST |  | 2025-11-24 19:11 | Precious Attah | 2025-11-24 19:09 | 2025-11-24 19:13 | 207 | 2025-11-24 19:09 | 2025-11-24 19:13 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Site came up without any technical intervention
NOCINC0006459534 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-26 17:55 | Tunji Adejumo | 2025-11-26 17:54 | 2025-11-26 17:58 | 206 | 2025-11-26 17:54 | 2025-11-26 17:58 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006489044 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0009B | OS2689 | IBD | Ibadan | Osun | 3 - Low | OS0690 | WEST | Huawei 3G SiteDown@2025-11-30 18:11:22@UOS2689 | 2025-11-30 18:28 | System Administrator | 2025-11-30 18:20 | 2025-11-30 18:24 | 206 | 2025-11-30 18:20 | 2025-11-30 18:24 | 0:03 | Energy Vision Nigeria | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Abiola Olanilokun |  |  | Oladotun Ogunleye | Osas Sunday |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006444517 | External Reconciliation | Site Down | P3 | IHS_OYO_1417B | - | - | Ibadan | Oyo | 3 - Low | OY1310 | WEST |  | 2025-11-24 23:01 | Damilola Paseda | 2025-11-24 22:59 | 2025-11-24 23:02 | 206 | 2025-11-24 22:59 | 2025-11-24 23:02 | 0:03 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Enoch Fidelis |  |  | Abiola Adegbiji | Habeeb Adepoju |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006461418 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST | NE Is Disconnected@2025-11-26 23:30:12@N3763 | 2025-11-26 23:44 | System Administrator | 2025-11-26 23:39 | 2025-11-26 23:42 | 205 | 2025-11-26 23:39 | 2025-11-26 23:42 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006470206 | External Reconciliation | Site Down | P1 | IHS_DEL_1034A | DL0318 | ASB | Asaba | Delta | 3 - Low | DL0721 | SOUTH SOUTH |  | 2025-11-28 06:57 | Patrick Okoro | 2025-11-28 06:57 | 2025-11-28 07:00 | 204 | 2025-11-28 06:57 | 2025-11-28 07:00 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Gabriel Akhamiogu |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site cleared without intervention | Site cleared without intervention
NOCINC0006481379 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0870A | T2742 | ASB | Asaba | Delta | 3 - Low | DL1269 | SOUTH SOUTH |  | 2025-11-29 16:30 | Ayomide Akindolie | 2025-11-29 16:30 | 2025-11-29 16:34 | 204 | 2025-11-29 16:30 | 2025-11-29 16:34 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006445799 | External Reconciliation | Site Down | P1 | IHS_ANA_0802A | T4037 | ASB | Asaba | Anambra | 3 - Low | AI0520 | SOUTH EAST |  | 2025-11-25 07:30 | Solomon Bankole | 2025-11-25 07:29 | 2025-11-25 07:32 | 203 | 2025-11-25 07:29 | 2025-11-25 07:32 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without any technical intervention | Site came up without any technical intervention
NOCINC0006461323 | External Reconciliation | Site Down | P1 | IHS_DEL_1107A | DL0092 | ASB | Asaba | Delta | 3 - Low | DL0660 | SOUTH SOUTH |  | 2025-11-26 23:17 | Tracy Osarumwense | 2025-11-26 23:17 | 2025-11-26 23:20 | 203 | 2025-11-26 23:17 | 2025-11-26 23:20 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Babatunde Jimoh� |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006465064 | External Reconciliation | Site Down | P1 | IHS_ASA_0702E | - | - | Asaba | Delta | 3 - Low | DL0690 | SOUTH SOUTH |  | 2025-11-27 13:25 | Uthman Akinola | 2025-11-27 13:25 | 2025-11-27 13:29 | 203 | 2025-11-27 13:25 | 2025-11-27 13:29 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Victor Ezeh |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006472531 | Internal Reconciliation | Site Down | P1 | IHS_OND_0775A | T3404 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 13:28 | Maureen Uchehorke | 2025-11-28 13:26 | 2025-11-28 13:30 | 203 | 2025-11-28 13:26 | 2025-11-28 13:30 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mercy Oni |  | Ojadua Olusegun | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006489033 | Internal Reconciliation | Site Down | P3 | IHS_EDO_1106C | ED5327 | IBD | Asaba | Edo | 3 - Low | ED0632 | SOUTH SOUTH |  | 2025-11-30 18:27 | Evelyn Emagurehor | 2025-11-30 18:26 | 2025-11-30 18:30 | 203 | 2025-11-30 18:26 | 2025-11-30 18:30 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | EKPU SUNDAY | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006476463 | Internal Reconciliation | Site Down | P2 | IHS_OSU_1047B | OS4769 | IBD | Ibadan | Osun | 3 - Low | OS0742 | WEST |  | 2025-11-29 00:11 | Sheriff Salami | 2025-11-29 00:08 | 2025-11-29 00:11 | 202 | 2025-11-29 00:08 | 2025-11-29 00:11 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Abdulsalami Onukaba Onukaba |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short outage duration, Site restored with no intervention
NOCINC0006459501 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-26 17:48 | Tunji Adejumo | 2025-11-26 17:48 | 2025-11-26 17:51 | 201 | 2025-11-26 17:48 | 2025-11-26 17:51 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006475770 | Internal Reconciliation | Site Down | P2 | IHS_ANA_0956A | T4860 | ASB | Asaba | Anambra | 3 - Low | AN0137 | SOUTH EAST |  | 2025-11-28 21:32 | Akachukwu Ugwu | 2025-11-28 21:29 | 2025-11-28 21:32 | 200 | 2025-11-28 21:29 | 2025-11-28 21:32 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Appeal John |  |  | Erik Nwodo | Nwigbo Chijioke |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | No passive issue at site. RMS evidence attached. | Short duration outage, no intervention
NOCINC0006456046 | External Reconciliation | Site Down | P2 | IHS_OYO_1278H | OY4461 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 08:49 | Oluwatomisin Ogunleye | 2025-11-26 08:49 | 2025-11-26 08:52 | 200 | 2025-11-26 08:49 | 2025-11-26 08:52 | 0:03 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006482611 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0851A | KW2339 | IBD | Ibadan | Kwara | 3 - Low | KW0413 | WEST |  | 2025-11-29 19:59 | Ayodele Oludare | 2025-11-29 19:56 | 2025-11-29 19:59 | 199 | 2025-11-29 19:56 | 2025-11-29 19:59 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | site came up without intervention
NOCINC0006486593 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0936A | T2991 | ASB | Asaba | Delta | 3 - Low | DL0750 | SOUTH SOUTH |  | 2025-11-30 12:16 | Ayomide Akindolie | 2025-11-30 12:15 | 2025-11-30 12:19 | 199 | 2025-11-30 12:15 | 2025-11-30 12:19 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Okoh Justus | Henry Emenuga | Henry Emenuga | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006471407 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1316B | AN3147 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 10:39 | Kehinde Akinbowale | 2025-11-28 10:37 | 2025-11-28 10:41 | 199 | 2025-11-28 10:37 | 2025-11-28 10:41 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006441574 | External Reconciliation | Site Down | P1 | IHS_EDO_0792A | T3250 | IBD | Asaba | Edo | 3 - Low | ED0165 | SOUTH SOUTH |  | 2025-11-24 15:50 | Evelyn Emagurehor | 2025-11-24 15:50 | 2025-11-24 15:53 | 198 | 2025-11-24 15:50 | 2025-11-24 15:53 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006470743 | External Reconciliation | Site Down | P2 | IHS_EDO_0928A | T3382 | IBD | Asaba | Edo | 3 - Low | ED0544 | SOUTH SOUTH |  | 2025-11-28 09:05 | Muhammed Hashirudeen | 2025-11-28 09:05 | 2025-11-28 09:08 | 198 | 2025-11-28 09:05 | 2025-11-28 09:08 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006463672 | External Reconciliation | Site Down | P3 | IHS_OYO_1118C | OY6537 | IBD | Ibadan | Oyo | 3 - Low | OY1490 | WEST |  | 2025-11-27 10:25 | Sheriff Salami | 2025-11-27 10:23 | 2025-11-27 10:26 | 198 | 2025-11-27 10:23 | 2025-11-27 10:26 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short outage duration, Site restored with no intervention
NOCINC0006487700 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 14:56 | Oluwatomisin Sogbesan | 2025-11-30 14:56 | 2025-11-30 14:59 | 198 | 2025-11-30 14:56 | 2025-11-30 14:59 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006446185 | External Reconciliation | Site Down | P1 | IHS_DEL_1017A | DL0111 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 09:04 | Tracy Osarumwense | 2025-11-25 09:04 | 2025-11-25 09:07 | 197 | 2025-11-25 09:04 | 2025-11-25 09:07 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006482840 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-29 20:49 | Okusanya Joseph | 2025-11-29 20:48 | 2025-11-29 20:51 | 197 | 2025-11-29 20:48 | 2025-11-29 20:51 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006474025 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1050A | OY2891 | IBD | Ibadan | Oyo | 3 - Low | OY1023 | WEST |  | 2025-11-28 17:07 | Praise Okezie | 2025-11-28 17:06 | 2025-11-28 17:09 | 196 | 2025-11-28 17:06 | 2025-11-28 17:09 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olapo Adebunmi |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006462128 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-27 03:34 | Precious Attah | 2025-11-27 03:34 | 2025-11-27 03:37 | 196 | 2025-11-27 03:34 | 2025-11-27 03:37 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006489134 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1174A | AN0558 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 18:50 | Aderonke Olowojoba | 2025-11-30 18:47 | 2025-11-30 18:50 | 195 | 2025-11-30 18:47 | 2025-11-30 18:50 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006443206 | External Reconciliation | Site Down | P4 | IHS_WAR_0747C | DL1078 | ASB | Asaba | Delta | 3 - Low | DL0884 | SOUTH SOUTH |  | 2025-11-24 19:09 | Tracy Osarumwense | 2025-11-24 19:09 | 2025-11-24 19:13 | 195 | 2025-11-24 19:09 | 2025-11-24 19:13 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006480273 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1190A | DL0432 | ASB | Asaba | Delta | 3 - Low | DL0565 | SOUTH SOUTH |  | 2025-11-29 13:53 | Quadri Ogundare | 2025-11-29 13:53 | 2025-11-29 13:56 | 195 | 2025-11-29 13:53 | 2025-11-29 13:56 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006458074 | External Reconciliation | Site Down | P3 | IHS_OYO_1315B | OY1016 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-26 14:04 | Ifechi Ugwueze | 2025-11-26 14:00 | 2025-11-26 14:04 | 195 | 2025-11-26 14:00 | 2025-11-26 14:04 | 0:03 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | ADEMOLA ADELEKE |  | Olumide Adebayo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify | 2 | Site was restored without intervention
NOCINC0006469760 | External Reconciliation | Site Down | P2 | IHS_OND_0777A | T3405 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 04:38 | Marvellous Emecheta | 2025-11-28 04:37 | 2025-11-28 04:40 | 195 | 2025-11-28 04:37 | 2025-11-28 04:40 | 0:03 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006439656 | External Reconciliation | Site Down | P3 | IHS_EDO_1321B | - | - | Asaba | Edo | 3 - Low | ED0833 | SOUTH SOUTH |  | 2025-11-24 11:57 | Evelyn Emagurehor | 2025-11-24 11:56 | 2025-11-24 12:00 | 194 | 2025-11-24 11:56 | 2025-11-24 12:00 | 0:03 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Asukwo Effiong | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006464704 | External Reconciliation | Site Down | P3 | IHS_ANA_1019A | T4813 | ASB | Asaba | Anambra | 3 - Low | AN0982 | SOUTH EAST | NE Is Disconnected@2025-11-27 12:09:48@AN0982 | 2025-11-27 12:31 | System Administrator | 2025-11-27 12:10 | 2025-11-27 12:13 | 193 | 2025-11-27 12:10 | 2025-11-27 12:13 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006461181 | External Reconciliation | Site Down | P2 | IHS_DEL_0964A | DL2989 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 22:44 | Tracy Osarumwense | 2025-11-26 22:44 | 2025-11-26 22:47 | 193 | 2025-11-26 22:44 | 2025-11-26 22:47 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006462061 | External Reconciliation | Site Down | P2 | IHS_ANA_1403H | AN0007 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 02:58 | Aderonke Olowojoba | 2025-11-27 02:55 | 2025-11-27 02:58 | 193 | 2025-11-27 02:55 | 2025-11-27 02:58 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006456108 | External Reconciliation | Site Down | P1 | IHS_ANA_0802A | T4037 | ASB | Asaba | Anambra | 3 - Low | AI0520 | SOUTH EAST |  | 2025-11-26 09:00 | Femi Olanipekun | 2025-11-26 09:00 | 2025-11-26 09:04 | 193 | 2025-11-26 09:00 | 2025-11-26 09:04 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006471911 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 11:47 | Quadri Ogundare | 2025-11-28 11:46 | 2025-11-28 11:49 | 193 | 2025-11-28 11:46 | 2025-11-28 11:49 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006447679 | External Reconciliation | Site Down | P2 | IHS_OSU_0849A | OS3974 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-25 11:35 | Marvellous Emecheta | 2025-11-25 11:33 | 2025-11-25 11:36 | 193 | 2025-11-25 11:33 | 2025-11-25 11:36 | 0:03 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ajibade Sikiru |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Short duration outage, site was up with no intervention.
NOCINC0006489220 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH |  | 2025-11-30 19:09 | Tracy Osarumwense | 2025-11-30 19:09 | 2025-11-30 19:12 | 193 | 2025-11-30 19:09 | 2025-11-30 19:12 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation) | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006458779 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 15:40 | Emmanuel Faleti | 2025-11-26 15:40 | 2025-11-26 15:43 | 192 | 2025-11-26 15:40 | 2025-11-26 15:43 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006471015 | External Reconciliation | Site Down | P4 | IHS_OYO_0036B | OY4298 | IBD | Ibadan | Oyo | 3 - Low | OY1674 | West |  | 2025-11-28 09:41 | Praise Okezie | 2025-11-28 09:40 | 2025-11-28 09:43 | 202 | 2025-11-28 09:40 | 2025-11-28 09:43 | 0:03 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006465225 | External Reconciliation | Site Down | P1 | IHS_AGB_0004B | DL0002 | ASB | Asaba | Delta | 3 - Low | DL0412 | SOUTH SOUTH |  | 2025-11-27 13:51 | Uthman Akinola | 2025-11-27 13:51 | 2025-11-27 13:54 | 191 | 2025-11-27 13:51 | 2025-11-27 13:54 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | Airtel NG, MTN NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006443769 | External Reconciliation | Site Down | P2 | IHS_ANA_1403H | AN0007 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 20:53 | Kehinde Akinbowale | 2025-11-24 20:50 | 2025-11-24 20:53 | 191 | 2025-11-24 20:50 | 2025-11-24 20:53 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006459036 | External Reconciliation | Site Down | P3 | IHS_ONT_0067B | AN0853 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 16:24 | Patrick Okoro | 2025-11-26 16:24 | 2025-11-26 16:28 | 191 | 2025-11-26 16:24 | 2025-11-26 16:28 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Idowu Dare |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without intervention
NOCINC0006489879 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0926A | OS2709 | IBD | Ibadan | Osun | 3 - Low | OS0755 | WEST |  | 2025-11-30 21:35 | Praise Okezie | 2025-11-30 21:33 | 2025-11-30 21:36 | 190 | 2025-11-30 21:33 | 2025-11-30 21:36 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006449220 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 14:44 | Emmanuel Faleti | 2025-11-25 14:43 | 2025-11-25 14:46 | 190 | 2025-11-25 14:43 | 2025-11-25 14:46 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006450061 | External Reconciliation | Site Down | P2 | IHS_KWA_0902A | KW4577 | IBD | Ibadan | Kwara | 3 - Low | KW0457 | WEST |  | 2025-11-25 16:35 | Precious Attah | 2025-11-25 16:35 | 2025-11-25 16:38 | 189 | 2025-11-25 16:35 | 2025-11-25 16:38 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006445528 | External Reconciliation | Site Down | P3 | IHS_OYO_0038B | OY4261 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 06:13 | Praise Okezie | 2025-11-25 06:12 | 2025-11-25 06:15 | 189 | 2025-11-25 06:12 | 2025-11-25 06:15 | 0:03 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mohammed Soliu |  | Abdulraman Odunola | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006459633 | External Reconciliation | Site Down | P3 | IHS_OYO_0046C | OY4165 | IBD | Ibadan | Oyo | 3 - Low | OY1036 | WEST |  | 2025-11-26 18:15 | Bosede Kutelu | 2025-11-26 18:15 | 2025-11-26 18:18 | 188 | 2025-11-26 18:15 | 2025-11-26 18:18 | 0:03 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olaitan Olajide | John Eze | John Eze | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006442200 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 16:47 | Ayomide Akindolie | 2025-11-24 16:45 | 2025-11-24 16:48 | 188 | 2025-11-24 16:45 | 2025-11-24 16:48 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006455127 | External Reconciliation | Site Down | P1 | IHS_OYO_1015A | OY2859 | IBD | Ibadan | Oyo | 3 - Low | OY1002 | WEST |  | 2025-11-26 05:41 | Ademola Alabi | 2025-11-26 05:39 | 2025-11-26 05:42 | 188 | 2025-11-26 05:39 | 2025-11-26 05:42 | 0:03 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention
NOCINC0006458756 | External Reconciliation | Site Down | P3 | IHS_OND_0705E | OD4731 | IBD | Ibadan | Ondo | 3 - Low | ON0812 | WEST | NE Is Disconnected@2025-11-26 15:24:03@LOD4731 | 2025-11-26 15:38 | System Administrator | 2025-11-26 15:24 | 2025-11-26 15:27 | 188 | 2025-11-26 15:24 | 2025-11-26 15:27 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site restored without technical intervention
NOCINC0006464900 | External Reconciliation | Site Down | P2 | IHS_OSU_0089C | OS4333 | IBD | Ibadan | Osun | 3 - Low | OS0974 | WEST |  | 2025-11-27 12:58 | Sheriff Salami | 2025-11-27 12:56 | 2025-11-27 12:59 | 187 | 2025-11-27 12:56 | 2025-11-27 12:59 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adejumobi Tunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Short outage duration, Site restored with no intervention
NOCINC0006465573 | External Reconciliation | Site Down | P2 | IHS_KWA_0769A | T3140 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 14:36 | Okusanya Joseph | 2025-11-27 14:36 | 2025-11-27 14:39 | 187 | 2025-11-27 14:36 | 2025-11-27 14:39 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006489841 | Internal Reconciliation | Site Down | P2 | IHS_ONT_0054B | AN0528 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 21:26 | Solomon Bankole | 2025-11-30 21:25 | 2025-11-30 21:28 | 187 | 2025-11-30 21:25 | 2025-11-30 21:28 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Esan Enoch | Femi Balogun | Femi Balogun | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention | Site came up without any technical intervention
NOCINC0006471869 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0904A | KW4575 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 11:38 | Praise Okezie | 2025-11-28 11:37 | 2025-11-28 11:40 | 187 | 2025-11-28 11:37 | 2025-11-28 11:40 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006442681 | External Reconciliation | Site Down | P2 | IHS_KWA_0902A | KW4577 | IBD | Ibadan | Kwara | 3 - Low | KW0457 | WEST |  | 2025-11-24 17:58 | Precious Attah | 2025-11-24 17:58 | 2025-11-24 18:01 | 187 | 2025-11-24 17:58 | 2025-11-24 18:01 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006445048 | External Reconciliation | Site Down | P1 | IHS_OYO_1041A | OY2368 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 02:38 | Praise Okezie | 2025-11-25 02:36 | 2025-11-25 02:39 | 186 | 2025-11-25 02:36 | 2025-11-25 02:39 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006463841 | External Reconciliation | Site Down | P3 | IHS_OGM_0002V | - | - | Ibadan | Oyo | 3 - Low | OY1059 | WEST |  | 2025-11-27 10:49 | Titus Tosin | 2025-11-27 10:49 | 2025-11-27 10:52 | 185 | 2025-11-27 10:49 | 2025-11-27 10:52 | 0:03 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006438257 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-24 07:21 | Okusanya Joseph | 2025-11-24 07:19 | 2025-11-24 07:22 | 185 | 2025-11-24 07:19 | 2025-11-24 07:22 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006439767 | External Reconciliation | Site Down | P1 | IHS_OND_1019C | OD6232 | IBD | Ibadan | Ondo | 3 - Low | ON0609 | WEST |  | 2025-11-24 12:24 | Oluwadara Bankole | 2025-11-24 12:20 | 2025-11-24 12:23 | 185 | 2025-11-24 12:20 | 2025-11-24 12:23 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Obuseh Williams |  |  | Ibrahim Akinpelu | Obuseh Williams |  | Lukman Amusat | Ibrahim Yekini | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006440055 | External Reconciliation | Site Down | P3 | IHS_EDO_1321B | - | - | Asaba | Edo | 3 - Low | ED0833 | SOUTH SOUTH |  | 2025-11-24 12:59 | Evelyn Emagurehor | 2025-11-24 12:57 | 2025-11-24 13:00 | 185 | 2025-11-24 12:57 | 2025-11-24 13:00 | 0:03 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Asukwo Effiong | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006476546 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0926A | OS2709 | IBD | Ibadan | Osun | 3 - Low | OS0755 | WEST |  | 2025-11-29 00:35 | Titus Tosin | 2025-11-29 00:31 | 2025-11-29 00:34 | 185 | 2025-11-29 00:31 | 2025-11-29 00:34 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Aniekan Ime |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006479410 | Internal Reconciliation | Site Down | P4 | IHS_OSU_0033B | OS2752 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-29 12:06 | Valentine Adinnu | 2025-11-29 12:05 | 2025-11-29 12:08 | 185 | 2025-11-29 12:05 | 2025-11-29 12:08 | 0:03 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ajibade Sikiru |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006483123 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-29 21:33 | Okusanya Joseph | 2025-11-29 21:33 | 2025-11-29 21:36 | 184 | 2025-11-29 21:33 | 2025-11-29 21:36 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006462008 | External Reconciliation | Site Down | P4 | IHS_ANA_1174A | AN0558 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 02:32 | Aderonke Olowojoba | 2025-11-27 02:30 | 2025-11-27 02:33 | 184 | 2025-11-27 02:30 | 2025-11-27 02:33 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006437575 | External Reconciliation | Site Down | P3 | IHS_ANA_1197A | AN0763 | ASB | Asaba | Anambra | 3 - Low | AN0681 | SOUTH EAST | CSL Fault@2025-11-24 03:13:40@AN0763_Km12 Plywood Mkt | 2025-11-24 03:26 | System Administrator | 2025-11-24 03:20 | 2025-11-24 03:23 | 183 | 2025-11-24 03:20 | 2025-11-24 03:23 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | ThankGod Amadi | Usen Sunday | Usen Sunday | Henry Wanogho | Ifeanyi Chukusa |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006463910 | External Reconciliation | Site Down | P2 | IHS_EDO_0747A | T0161 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-27 11:02 | Muhammed Hashirudeen | 2025-11-27 10:59 | 2025-11-27 11:02 | 182 | 2025-11-27 10:59 | 2025-11-27 11:02 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006440196 | External Reconciliation | Site Down | P3 | IHS_EDO_1216B | ED6219 | IBD | Asaba | Edo | 3 - Low | ED0750 | SOUTH SOUTH |  | 2025-11-24 13:10 | Evelyn Emagurehor | 2025-11-24 13:10 | 2025-11-24 13:13 | 181 | 2025-11-24 13:10 | 2025-11-24 13:13 | 0:03 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Asukwo Effiong | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006474979 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0878A | KW2381 | IBD | Ibadan | Kwara | 3 - Low | KW0530 | WEST |  | 2025-11-28 19:32 | Testimony Akinyemi | 2025-11-28 19:30 | 2025-11-28 19:33 | 180 | 2025-11-28 19:30 | 2025-11-28 19:33 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adelola Dagunduro |  |  | Paul Akpomie | Adelola Dagunduro |  | Rilwan Akeem | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | SHORT DURATION OUTAGE
NOCINC0006447885 | External Reconciliation | Site Down | P1 | IHS_EDO_0804A | T3230 | IBD | Asaba | Edo | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-25 11:50:21@T3230_Uje_Oro St_Uromi | 2025-11-25 12:03 | System Administrator | 2025-11-25 11:50 | 2025-11-25 11:53 | 180 | 2025-11-25 11:50 | 2025-11-25 11:53 | 0:03 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006471109 | External Reconciliation | Site Down | P4 | IHS_EDO_0860A | T3327 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 09:54 | Azeezat Badmus | 2025-11-28 09:52 | 2025-11-28 09:55 | 180 | 2025-11-28 09:52 | 2025-11-28 09:55 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adeoti Ogunbiyi |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | site cleared with no technical intervention
NOCINC0006457868 | External Reconciliation | Site Down | P2 | IHS_OYO_0932A | T3873 | IBD | Ibadan | Oyo | 3 - Low | OY1125 | WEST | The link between the server and the ME is broken@2025-11-26 12:47:50@OY1125(31125) | 2025-11-26 13:31 | System Administrator | 2025-11-26 12:48 | 2025-11-26 12:51 | 180 | 2025-11-26 12:48 | 2025-11-26 12:51 | 0:03 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site was restored without intervention
NOCINC0006475124 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0878A | KW2381 | IBD | Ibadan | Kwara | 3 - Low | KW0530 | WEST |  | 2025-11-28 19:56 | Testimony Akinyemi | 2025-11-28 19:54 | 2025-11-28 19:57 | 180 | 2025-11-28 19:54 | 2025-11-28 19:57 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adelola Dagunduro |  |  | Paul Akpomie | Adelola Dagunduro |  | Rilwan Akeem | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | SHORT DURATION OUTAGE
NOCINC0006471497 | Internal Reconciliation | Site Down | P3 | IHS_OSU_0059B | OS2661 | IBD | Ibadan | Osun | 3 - Low | OS0684 | WEST |  | 2025-11-28 10:46 | Okusanya Joseph | 2025-11-28 10:45 | 2025-11-28 10:48 | 179 | 2025-11-28 10:45 | 2025-11-28 10:48 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006462214 | External Reconciliation | Site Down | P2 | IHS_OSU_0091C | OS4340 | IBD | Ibadan | Osun | 3 - Low | OS0710 | WEST |  | 2025-11-27 04:13 | Precious Attah | 2025-11-27 04:11 | 2025-11-27 04:14 | 178 | 2025-11-27 04:11 | 2025-11-27 04:14 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Unachukwu Jude |  |  | Soye West | Ugwu Samuel Nnamdi |  | Busuyi Ogunyinka | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006455050 | External Reconciliation | Site Down | P3 | IHS_OYO_1118C | OY6537 | IBD | Ibadan | Oyo | 3 - Low | OY1490 | WEST |  | 2025-11-26 05:10 | Osarieme Charles | 2025-11-26 05:08 | 2025-11-26 05:11 | 178 | 2025-11-26 05:08 | 2025-11-26 05:11 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short outage duration, Site restored with no intervention
NOCINC0006472757 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1218B | - | - | Asaba | Delta | 3 - Low | DL0903 | SOUTH SOUTH |  | 2025-11-28 14:09 | Bukola Olabanji | 2025-11-28 14:09 | 2025-11-28 14:12 | 177 | 2025-11-28 14:09 | 2025-11-28 14:12 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006461463 | External Reconciliation | Site Down | P1 | IHS_DEL_0797A | T2636 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 23:52 | Ezinne Ubachukwu | 2025-11-26 23:50 | 2025-11-26 23:53 | 177 | 2025-11-26 23:50 | 2025-11-26 23:53 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006441402 | External Reconciliation | Site Down | P4 | IHS_DEL_0834A | T2706 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 15:23 | Ezinne Ubachukwu | 2025-11-24 15:22 | 2025-11-24 15:25 | 177 | 2025-11-24 15:22 | 2025-11-24 15:25 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006472998 | Internal Reconciliation | Site Down | P3 | IHS_OYO_0963A | T3808 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 14:46 | Oluwatomisin Ogunleye | 2025-11-28 14:44 | 2025-11-28 14:47 | 177 | 2025-11-28 14:44 | 2025-11-28 14:47 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Victor Olanrewaju |  |  | Paul Akpomie | Victor Olanrewaju |  | Michael Oguntimilehin | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without technical intervention
NOCINC0006440312 | External Reconciliation | Site Down | P1 | IHS_DEL_1020A | DL0113 | ASB | Asaba | Delta | 3 - Low | DL0742 | SOUTH SOUTH |  | 2025-11-24 13:14 | Tracy Osarumwense | 2025-11-24 13:12 | 2025-11-24 13:15 | 176 | 2025-11-24 13:12 | 2025-11-24 13:15 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006459338 | External Reconciliation | Site Down | P2 | IHS_ILO_0003B | KW2385 | IBD | Ibadan | Kwara | 3 - Low | KW0428 | WEST |  | 2025-11-26 17:20 | Titus Tosin | 2025-11-26 17:19 | 2025-11-26 17:22 | 175 | 2025-11-26 17:19 | 2025-11-26 17:22 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006448676 | External Reconciliation | Site Down | P1 | IHS_KWA_0749A | T3115 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 13:42 | Oluwatomisin Ogunleye | 2025-11-25 13:40 | 2025-11-25 13:43 | 175 | 2025-11-25 13:40 | 2025-11-25 13:43 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Jimoh Yusuf |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site restored without technical intervention
NOCINC0006483596 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-29 22:49 | Okusanya Joseph | 2025-11-29 22:49 | 2025-11-29 22:52 | 175 | 2025-11-29 22:49 | 2025-11-29 22:52 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006480988 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1185A | DL0719 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 15:36 | Ayomide Akindolie | 2025-11-29 15:36 | 2025-11-29 15:39 | 174 | 2025-11-29 15:36 | 2025-11-29 15:39 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006461813 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 01:02 | Tracy Osarumwense | 2025-11-27 01:02 | 2025-11-27 01:05 | 173 | 2025-11-27 01:02 | 2025-11-27 01:05 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006438309 | External Reconciliation | Site Down | P3 | IHS_LFG_0001B | KW4585 | IBD | Ibadan | Kwara | 3 - Low | KW0412 | WEST |  | 2025-11-24 07:37 | Okusanya Joseph | 2025-11-24 07:35 | 2025-11-24 07:38 | 173 | 2025-11-24 07:35 | 2025-11-24 07:38 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006461259 | External Reconciliation | Site Down | P4 | IHS_ANA_1174A | AN0558 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-26 22:52:20@AN0558_Ebenato Amichi | 2025-11-26 23:04 | System Administrator | 2025-11-26 22:58 | 2025-11-26 23:01 | 173 | 2025-11-26 22:58 | 2025-11-26 23:01 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006439748 | External Reconciliation | Site Down | P2 | IHS_DEL_0957A | T2919 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 12:21 | Ayokunle Samuel | 2025-11-24 12:21 | 2025-11-24 12:22 | 112 | 2025-11-24 12:20 | 2025-11-24 12:22 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site inter-fail and clear without any technical intervention. | Site inter-fail and clear without any technical intervention.
NOCINC0006448672 | External Reconciliation | Site Down | P1 | IHS_EDO_0804A | T3230 | IBD | Asaba | Edo | 3 - Low | - | - | NE Is Disconnected@2025-11-25 13:26:35@L3230 | 2025-11-25 13:42 | System Administrator | 2025-11-25 13:38 | 2025-11-25 13:41 | 172 | 2025-11-25 13:38 | 2025-11-25 13:41 | 0:03 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006449742 | External Reconciliation | Site Down | P3 | IHS_OYO_1424B | - | - | Ibadan | Oyo | 3 - Low | OY1305 | WEST |  | 2025-11-25 15:57 | Victor Otugo | 2025-11-25 15:57 | 2025-11-25 16:00 | 171 | 2025-11-25 15:57 | 2025-11-25 16:00 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Azeez Yusuf | John Eze | John Eze | Ogbuma Oluwafemi | Adekanmi Ajayi |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006439413 | External Reconciliation | Site Down | P2 | IHS_EDO_0918A | T3320 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 11:01 | Oluwatomisin Sogbesan | 2025-11-24 11:00 | 2025-11-24 11:03 | 171 | 2025-11-24 11:00 | 2025-11-24 11:03 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Osarieme Omoragbon |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006464387 | External Reconciliation | Site Down | P2 | IHS_OYO_0932A | T3873 | IBD | Ibadan | Oyo | 3 - Low | OY1125 | WEST | The link between the server and the ME is broken@2025-11-27 10:59:30@OY1125(31125) | 2025-11-27 11:56 | System Administrator | 2025-11-27 11:00 | 2025-11-27 11:02 | 170 | 2025-11-27 11:00 | 2025-11-27 11:02 | 0:03 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olumide Adebayo |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006440856 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-24 14:16 | Aderonke Olowojoba | 2025-11-24 14:14 | 2025-11-24 14:17 | 169 | 2025-11-24 14:14 | 2025-11-24 14:17 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention
NOCINC0006465559 | External Reconciliation | Site Down | P4 | IHS_ANA_0985A | T4171 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 14:35 | Akachukwu Ugwu | 2025-11-27 14:32 | 2025-11-27 14:35 | 169 | 2025-11-27 14:32 | 2025-11-27 14:35 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Wisdom Patrick |  |  | Erik Nwodo | Nwigbo Chijioke |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006458782 | External Reconciliation | Site Down | P1 | IHS_DEL_1072A | DL0331 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 15:41 | Femi Olanipekun | 2025-11-26 15:41 | 2025-11-26 15:43 | 169 | 2025-11-26 15:41 | 2025-11-26 15:43 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adedeji Olusegun |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006466120 | External Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 15:46 | Bukola Olabanji | 2025-11-27 15:46 | 2025-11-27 15:47 | 47 | 2025-11-27 15:44 | 2025-11-27 15:47 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006482813 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-29 20:43 | Okusanya Joseph | 2025-11-29 20:41 | 2025-11-29 20:43 | 167 | 2025-11-29 20:41 | 2025-11-29 20:43 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006462114 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-27 03:31 | Precious Attah | 2025-11-27 03:30 | 2025-11-27 03:33 | 165 | 2025-11-27 03:30 | 2025-11-27 03:33 | 0:03 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006468172 | External Reconciliation | Site Down | P2 | IHS_ANA_1403H | AN0007 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 21:49 | Oluwatoyin Fagite | 2025-11-27 21:48 | 2025-11-27 21:51 | 164 | 2025-11-27 21:48 | 2025-11-27 21:51 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006466446 | External Reconciliation | Site Down | P4 | IHS_WAR_0706E | T2745 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 16:41 | Bukola Olabanji | 2025-11-27 16:40 | 2025-11-27 16:43 | 163 | 2025-11-27 16:40 | 2025-11-27 16:43 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Shoret duration outage
NOCINC0006469524 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-28 02:43 | Tunji Adejumo | 2025-11-28 02:43 | 2025-11-28 02:46 | 163 | 2025-11-28 02:43 | 2025-11-28 02:46 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006443833 | External Reconciliation | Site Down | P2 | IHS_DEL_0731E | DL1019 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 21:02 | Solomon Bankole | 2025-11-24 21:02 | 2025-11-24 21:04 | 162 | 2025-11-24 21:02 | 2025-11-24 21:04 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention | Site came up without any technical intervention
NOCINC0006482618 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1054A | OY2803 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 20:01 | Favour Ahize | 2025-11-29 19:59 | 2025-11-29 20:02 | 162 | 2025-11-29 19:59 | 2025-11-29 20:02 | 0:03 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Alaba |  |  | Paul Akpomie | Oluwaseun Alaba |  | Luke Eke | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short Outage Duration
NOCINC0006481232 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1185A | DL0719 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 16:08 | Ayomide Akindolie | 2025-11-29 16:06 | 2025-11-29 16:09 | 161 | 2025-11-29 16:06 | 2025-11-29 16:09 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006438947 | External Reconciliation | Site Down | P2 | IHS_EDO_0794A | T3211 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 09:34 | Evelyn Emagurehor | 2025-11-24 09:31 | 2025-11-24 09:34 | 161 | 2025-11-24 09:31 | 2025-11-24 09:34 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006463554 | External Reconciliation | Site Down | P4 | IHS_DEL_1182A | DL0614 | ASB | Asaba | Delta | 3 - Low | DL0520 | SOUTH SOUTH |  | 2025-11-27 10:04 | Femi Olanipekun | 2025-11-27 10:04 | 2025-11-27 10:06 | 160 | 2025-11-27 10:04 | 2025-11-27 10:06 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006458299 | External Reconciliation | Site Down | P3 | IHS_EDO_1216B | ED6219 | IBD | Asaba | Edo | 3 - Low | ED0750 | SOUTH SOUTH |  | 2025-11-26 14:38 | Emmanuel Faleti | 2025-11-26 14:37 | 2025-11-26 14:40 | 160 | 2025-11-26 14:37 | 2025-11-26 14:40 | 0:03 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Asukwo Effiong | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006461136 | External Reconciliation | Site Down | P2 | IHS_IBA_0116C | OY4367 | IBD | Ibadan | Oyo | 3 - Low | OY1200 | WEST |  | 2025-11-26 22:33 | Victor Otugo | 2025-11-26 22:33 | 2025-11-26 22:36 | 158 | 2025-11-26 22:33 | 2025-11-26 22:36 | 0:03 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006480693 | Internal Reconciliation | Site Down | P1 | IHS_BEN_0057B | ED5096 | IBD | Asaba | Edo | 3 - Low | ED0664 | SOUTH SOUTH |  | 2025-11-29 14:47 | Azeezat Badmus | 2025-11-29 14:47 | 2025-11-29 14:49 | 156 | 2025-11-29 14:47 | 2025-11-29 14:49 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ismail Adeyinka |  |  | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | site cleared with no technical intervention
NOCINC0006473254 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 15:22 | Quadri Ogundare | 2025-11-28 15:19 | 2025-11-28 15:22 | 156 | 2025-11-28 15:19 | 2025-11-28 15:22 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Site cleared without any technical intervention
NOCINC0006457584 | External Reconciliation | Site Down | P1 | IHS_EDO_0996A | ED4860 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 12:45 | Azeezat Badmus | 2025-11-26 12:43 | 2025-11-26 12:46 | 156 | 2025-11-26 12:43 | 2025-11-26 12:46 | 0:03 | Huawei | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 1 / 1 | MTN NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Faulty ATS contactor was worked on. (No diesel outage after validation) | Faulty ATS contactor was worked on. (No diesel outage after validation)
NOCINC0006461732 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 00:47 | Tracy Osarumwense | 2025-11-27 00:47 | 2025-11-27 00:49 | 156 | 2025-11-27 00:47 | 2025-11-27 00:49 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006439850 | External Reconciliation | Site Down | P2 | IHS_DEL_1013A | DL0094 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 12:41 | Ezinne Ubachukwu | 2025-11-24 12:40 | 2025-11-24 12:43 | 155 | 2025-11-24 12:40 | 2025-11-24 12:43 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adedeji Olusegun |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006470849 | External Reconciliation | Site Down | P3 | IHS_DEL_0946A | T2912 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 09:14 | Bukola Olabanji | 2025-11-28 09:12 | 2025-11-28 09:14 | 153 | 2025-11-28 09:12 | 2025-11-28 09:14 | 0:03 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006459094 | External Reconciliation | Site Down | P2 | IHS_DEL_0731E | DL1019 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 16:36 | Patrick Okoro | 2025-11-26 16:36 | 2025-11-26 16:38 | 152 | 2025-11-26 16:36 | 2025-11-26 16:38 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ishaya Sunday |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without intervention
NOCINC0006450799 | External Reconciliation | Site Down | P4 | IHS_EDO_1106C | ED5327 | IBD | Asaba | Edo | 3 - Low | ED0632 | SOUTH SOUTH |  | 2025-11-25 18:26 | Oluwatomisin Sogbesan | 2025-11-25 18:26 | 2025-11-25 18:29 | 152 | 2025-11-25 18:26 | 2025-11-25 18:29 | 0:03 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | EKPU SUNDAY | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006472559 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0704E | ED5317 | IBD | Asaba | Edo | 3 - Low | ED0716 | SOUTH SOUTH |  | 2025-11-28 13:34 | Muhammed Hashirudeen | 2025-11-28 13:34 | 2025-11-28 13:36 | 152 | 2025-11-28 13:34 | 2025-11-28 13:36 | 0:03 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006472928 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0947A | T2279 | ASB | Asaba | Delta | 3 - Low | DL0251 | SOUTH SOUTH |  | 2025-11-28 14:36 | Abundance Otunola | 2025-11-28 14:36 | 2025-11-28 14:39 | 152 | 2025-11-28 14:36 | 2025-11-28 14:39 | 0:03 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006449127 | External Reconciliation | Site Down | P1 | IHS_DEL_0906A | T2725 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 14:35 | Ezinne Ubachukwu | 2025-11-25 14:32 | 2025-11-25 14:35 | 150 | 2025-11-25 14:32 | 2025-11-25 14:35 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006454497 | External Reconciliation | Site Down | P1 | IHS_EDO_0755A | T0230 | IBD | Asaba | Edo | 3 - Low | ED0450 | SOUTH SOUTH |  | 2025-11-26 01:28 | Evelyn Emagurehor | 2025-11-26 01:27 | 2025-11-26 01:30 | 150 | 2025-11-26 01:27 | 2025-11-26 01:30 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006448728 | External Reconciliation | Site Down | P4 | IHS_DEL_1046A | DL0420 | ASB | Asaba | Delta | 3 - Low | DL0911 | SOUTH SOUTH | Site Abis control link broken@2025-11-25 13:10:40@DL0911 | 2025-11-25 13:46 | System Administrator | 2025-11-25 13:11 | 2025-11-25 13:50 | 2349 | 2025-11-25 13:47 | 2025-11-25 13:50 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention
NOCINC0006484015 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-30 00:49 | Okusanya Joseph | 2025-11-30 00:46 | 2025-11-30 00:49 | 150 | 2025-11-30 00:46 | 2025-11-30 00:49 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006441400 | External Reconciliation | Site Down | P2 | IHS_EDO_0954A | ED2034 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 15:22 | Oluwatomisin Sogbesan | 2025-11-24 15:20 | 2025-11-24 15:23 | 149 | 2025-11-24 15:20 | 2025-11-24 15:23 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adisa Olamilekan |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006460821 | External Reconciliation | Site Down | P2 | IHS_DEL_0964A | DL2989 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 21:35 | Tracy Osarumwense | 2025-11-26 21:35 | 2025-11-26 21:37 | 149 | 2025-11-26 21:35 | 2025-11-26 21:37 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006476381 | Internal Reconciliation | Site Down | P3 | IHS_OYO_0046C | OY4165 | IBD | Ibadan | Oyo | 3 - Low | OY1036 | WEST |  | 2025-11-28 23:36 | Bosede Kutelu | 2025-11-28 23:35 | 2025-11-28 23:37 | 149 | 2025-11-28 23:35 | 2025-11-28 23:37 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olaitan Olajide | John Eze | John Eze | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006461526 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 00:07 | Tracy Osarumwense | 2025-11-27 00:05 | 2025-11-27 00:08 | 149 | 2025-11-27 00:05 | 2025-11-27 00:08 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006472548 | Internal Reconciliation | Site Down | P2 | IHS_IBA_0116C | OY4367 | IBD | Ibadan | Oyo | 3 - Low | OY1200 | WEST |  | 2025-11-28 13:32 | Mutmainnah Saba | 2025-11-28 13:30 | 2025-11-28 13:32 | 149 | 2025-11-28 13:30 | 2025-11-28 13:32 | 0:02 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adebiyi Ridwan |  | Yunus Ololade | Ridwan Adepoju | Ahmed Ibrahim |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006471287 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0972A | ED2071 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 10:20 | Azeezat Badmus | 2025-11-28 10:18 | 2025-11-28 10:21 | 148 | 2025-11-28 10:18 | 2025-11-28 10:21 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | site cleared with no technical intervention
NOCINC0006476072 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1084A | DL0601 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 22:18 | Femi Olanipekun | 2025-11-28 22:18 | 2025-11-28 22:21 | 148 | 2025-11-28 22:18 | 2025-11-28 22:21 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Okon Edidiong |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ishiekwene Nmor | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006464899 | External Reconciliation | Site Down | P2 | IHS_EDO_0727E | ED2054 | IBD | Asaba | Edo | 3 - Low | ED0705 | SOUTH SOUTH |  | 2025-11-27 12:58 | Muhammed Hashirudeen | 2025-11-27 12:55 | 2025-11-27 12:58 | 148 | 2025-11-27 12:55 | 2025-11-27 12:58 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Agboola Olawale |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006457339 | External Reconciliation | Site Down | P3 | IHS_EDO_1216B | ED6219 | IBD | Asaba | Edo | 3 - Low | ED0750 | SOUTH SOUTH |  | 2025-11-26 12:12 | Emmanuel Faleti | 2025-11-26 12:11 | 2025-11-26 12:13 | 147 | 2025-11-26 12:11 | 2025-11-26 12:13 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Asukwo Effiong | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006466042 | External Reconciliation | Site Down | P4 | IHS_ANA_1113A | AN0560 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 15:41 | Gbemisola Adedeji | 2025-11-27 15:38 | 2025-11-27 15:40 | 147 | 2025-11-27 15:38 | 2025-11-27 15:40 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Augustine Okoro | Ademola Adekunle | Ademola Adekunle | Henry Wanogho | Ifeanyi Chukusa |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006472116 | Internal Reconciliation | Site Down | P3 | IHS_DEL_1218B | - | - | Asaba | Delta | 3 - Low | DL0903 | SOUTH SOUTH |  | 2025-11-28 12:22 | Quadri Ogundare | 2025-11-28 12:22 | 2025-11-28 12:25 | 147 | 2025-11-28 12:22 | 2025-11-28 12:25 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006447696 | External Reconciliation | Site Down | P2 | IHS_ILO_0003B | KW2385 | IBD | Ibadan | Kwara | 3 - Low | KW0428 | WEST |  | 2025-11-25 11:38 | Precious Attah | 2025-11-25 11:38 | 2025-11-25 11:40 | 146 | 2025-11-25 11:38 | 2025-11-25 11:40 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006460770 | External Reconciliation | Site Down | P3 | IHS_OYO_1414B | - | - | Ibadan | Oyo | 3 - Low | OY1366 | WEST |  | 2025-11-26 21:24 | Precious Attah | 2025-11-26 21:23 | 2025-11-26 21:25 | 145 | 2025-11-26 21:23 | 2025-11-26 21:25 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006462412 | External Reconciliation | Site Down | P2 | IHS_WAR_0034B | DL0736 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 05:35 | Tracy Osarumwense | 2025-11-27 05:35 | 2025-11-27 05:37 | 145 | 2025-11-27 05:35 | 2025-11-27 05:37 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006482082 | Internal Reconciliation | Site Down | P3 | IHS_ANA_1156A | AN0745 | ASB | Asaba | Anambra | 3 - Low | AN0824 | SOUTH EAST | Huawei 2G SiteDown@2025-11-29 18:09:25@AN0745_Obuofia Ifite Nibo | 2025-11-29 18:24 | System Administrator | 2025-11-29 18:17 | 2025-11-29 18:19 | 145 | 2025-11-29 18:17 | 2025-11-29 18:19 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oladele Segun | David Ndubuisi | David Ndubuisi | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006449422 | External Reconciliation | Site Down | P4 | IHS_IBA_0086B | OY4185 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 15:09 | Victor Otugo | 2025-11-25 15:05 | 2025-11-25 15:07 | 144 | 2025-11-25 15:05 | 2025-11-25 15:07 | 0:02 | SPS | Equipment Repair | Passive | Infrastructure | Armoured Cable | 1 / 1 | MTN NG |  | Oremade Yusuf |  | Iyiola Azeez | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | burnt DC cable was worked on
NOCINC0006442815 | External Reconciliation | Site Down | P1 | IHS_DEL_0769A | T2603 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 18:12 | Tracy Osarumwense | 2025-11-24 18:12 | 2025-11-24 18:15 | 144 | 2025-11-24 18:12 | 2025-11-24 18:15 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kenneth Oboniye |  |  | Cornelius Yakubu | Jerry Igwe |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 23 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006489170 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0013B | EK2273 | IBD | Ibadan | Ekiti | 3 - Low | - | - | CSL Fault@2025-11-30 18:33:41@EK2273_Igbara Odo Rd Ilawe Ekiti | 2025-11-30 19:02 | System Administrator | 2025-11-30 18:41 | 2025-11-30 18:43 | 143 | 2025-11-30 18:41 | 2025-11-30 18:43 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006454479 | External Reconciliation | Site Down | P2 | IHS_OYO_1324B | OY1034 | IBD | Ibadan | Oyo | 3 - Low | OY1686 | WEST |  | 2025-11-26 01:26 | Aishat Oyedeji | 2025-11-26 01:24 | 2025-11-26 01:26 | 142 | 2025-11-26 01:24 | 2025-11-26 01:26 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, no intervention
NOCINC0006470986 | External Reconciliation | Site Down | P3 | IHS_EDO_1026A | ED2161 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 09:35 | Muhammed Hashirudeen | 2025-11-28 09:35 | 2025-11-28 09:37 | 142 | 2025-11-28 09:35 | 2025-11-28 09:37 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | ADELEKE OYE | Christopher Idehen | Bern Daniel | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Site restored without intervention.
NOCINC0006449834 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-25 16:08 | Tunji Adejumo | 2025-11-25 16:08 | 2025-11-25 16:10 | 142 | 2025-11-25 16:08 | 2025-11-25 16:10 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006479673 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1130A | DL0748 | ASB | Asaba | Delta | 3 - Low | DL0908 | SOUTH SOUTH |  | 2025-11-29 12:40 | Ayomide Akindolie | 2025-11-29 12:39 | 2025-11-29 12:41 | 140 | 2025-11-29 12:39 | 2025-11-29 12:41 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | HENRY OMELE | Henry Ikede | Henry Ikede | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006480036 | Internal Reconciliation | Site Down | P4 | IHS_PAT_0002B | KW4563 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-29 13:25 | Ayodele Oludare | 2025-11-29 13:24 | 2025-11-29 13:26 | 140 | 2025-11-29 13:24 | 2025-11-29 13:26 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006454916 | External Reconciliation | Site Down | P4 | IHS_DEL_1142A | DL0762 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 04:21 | Ayokunle Samuel | 2025-11-26 04:20 | 2025-11-26 04:22 | 138 | 2025-11-26 04:20 | 2025-11-26 04:22 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention.
NOCINC0006476440 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1050A | DL0403 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 00:01 | Femi Olanipekun | 2025-11-28 23:58 | 2025-11-29 | 137 | 2025-11-28 23:58 | 2025-11-29 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Confidence Osayamwen |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006466430 | External Reconciliation | Site Down | P2 | IHS_ONT_0054B | AN0528 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 16:39 | Femi Olanipekun | 2025-11-27 16:39 | 2025-11-27 16:41 | 137 | 2025-11-27 16:39 | 2025-11-27 16:41 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Esan Enoch | Femi Balogun | Femi Balogun | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006464400 | External Reconciliation | Site Down | P2 | IHS_EDO_0727E | ED2054 | IBD | Asaba | Edo | 3 - Low | ED0705 | SOUTH SOUTH |  | 2025-11-27 11:59 | Muhammed Hashirudeen | 2025-11-27 11:58 | 2025-11-27 12:00 | 136 | 2025-11-27 11:58 | 2025-11-27 12:00 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Agboola Olawale |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006449405 | External Reconciliation | Site Down | P1 | IHS_KWA_0752A | T3112 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 15:07 | Precious Attah | 2025-11-25 15:06 | 2025-11-25 15:08 | 136 | 2025-11-25 15:06 | 2025-11-25 15:08 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Bello Saheed |  |  | Soye West | Goddey Nwokedigbo Peter |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 1 | Site came up without any technical intervention
NOCINC0006457660 | External Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-26 12:52 | Tunji Adejumo | 2025-11-26 12:52 | 2025-11-26 12:54 | 135 | 2025-11-26 12:52 | 2025-11-26 12:54 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006459320 | External Reconciliation | Site Down | P4 | IHS_ANA_1086A | AN0009 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 17:14 | Oluwatoyin Fagite | 2025-11-26 17:13 | 2025-11-26 17:16 | 134 | 2025-11-26 17:13 | 2025-11-26 17:16 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006481010 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0929C | KW6372 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-29 15:38 | Ayodele Oludare | 2025-11-29 15:37 | 2025-11-29 15:40 | 133 | 2025-11-29 15:37 | 2025-11-29 15:40 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ayoola Yusuf |  |  | Ogbuma Oluwafemi | Solomon Agwu |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | site came up without intervention
NOCINC0006460861 | External Reconciliation | Site Down | P2 | IHS_DEL_1185A | DL0719 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 21:42 | Tracy Osarumwense | 2025-11-26 21:42 | 2025-11-26 21:44 | 133 | 2025-11-26 21:42 | 2025-11-26 21:44 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006456059 | External Reconciliation | Site Down | P2 | IHS_EKI_0747A | T3705 | IBD | Ibadan | Ekiti | 3 - Low | EK0496 | WEST |  | 2025-11-26 08:52 | Mary Elaigwu | 2025-11-26 08:50 | 2025-11-26 08:52 | 132 | 2025-11-26 08:50 | 2025-11-26 08:52 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Kayode Ayansola |  |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site was restored with no technical intervention
NOCINC0006448725 | External Reconciliation | Site Down | P4 | IHS_KWA_0904A | KW4575 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 13:46 | Oluwatomisin Ogunleye | 2025-11-25 13:46 | 2025-11-25 13:48 | 132 | 2025-11-25 13:46 | 2025-11-25 13:48 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site restored without technical intervention
NOCINC0006459709 | External Reconciliation | Site Down | P4 | IHS_EDO_1106C | ED5327 | IBD | Asaba | Edo | 3 - Low | ED0632 | SOUTH SOUTH |  | 2025-11-26 18:27 | Emmanuel Faleti | 2025-11-26 18:27 | 2025-11-26 18:29 | 132 | 2025-11-26 18:27 | 2025-11-26 18:29 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | EKPU SUNDAY | Achebe Chigozie | Omoragbon Austin | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006476373 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0874A | KW2380 | ABJ | Ibadan | Niger | 3 - Low | - | - |  | 2025-11-28 23:34 | Titus Tosin | 2025-11-28 23:33 | 2025-11-28 23:35 | 132 | 2025-11-28 23:33 | 2025-11-28 23:35 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Victor Agahiu |  |  | Soye West | Oboh Oseyeieomo |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006438848 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 09:22 | Ezinne Ubachukwu | 2025-11-24 09:22 | 2025-11-24 09:25 | 131 | 2025-11-24 09:22 | 2025-11-24 09:25 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006471888 | Internal Reconciliation | Site Down | P4 | IHS_KWA_0903A | KW4576 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-28 11:41 | Praise Okezie | 2025-11-28 11:40 | 2025-11-28 11:42 | 131 | 2025-11-28 11:40 | 2025-11-28 11:42 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006483707 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0834A | T3516 | IBD | Ibadan | Oyo | 3 - Low | OY1082 | WEST | Site Abis control link broken@2025-11-29 22:43:38@OY1082 | 2025-11-29 23:14 | System Administrator | 2025-11-29 22:44 | 2025-11-29 22:46 | 131 | 2025-11-29 22:44 | 2025-11-29 22:46 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Enoch Fidelis | Adewale Adejumo | Adewale Adejumo | Abiola Adegbiji | Habeeb Adepoju |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006468088 | External Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-27 21:22:21@T2719_30 Emevor Orogun Road | 2025-11-27 21:34 | System Administrator | 2025-11-27 21:28 | 2025-11-27 21:30 | 130 | 2025-11-27 21:28 | 2025-11-27 21:30 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site cleared without intervention | Site cleared without intervention
NOCINC0006464615 | External Reconciliation | Site Down | P1 | IHS_ANA_0820A | T4082/T6505 | ASB | Asaba | Anambra | 3 - Low | AN1097 | SOUTH EAST | NE Is Disconnected@2025-11-27 11:49:47@AN1097 | 2025-11-27 12:21 | System Administrator | 2025-11-27 11:50 | 2025-11-27 11:52 | 130 | 2025-11-27 11:50 | 2025-11-27 11:52 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Appeal John |  |  | Erik Nwodo | Nwigbo Chijioke |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006474571 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0726E | T3055 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-28 18:26 | Damilola Paseda | 2025-11-28 18:25 | 2025-11-28 18:27 | 130 | 2025-11-28 18:25 | 2025-11-28 18:27 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ngwueche Chukwunonye |  | Solomon Apute | Abiola Adegbiji | Yusuf Gyang |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006439310 | External Reconciliation | Site Down | P2 | IHS_ANA_1403H | AN0007 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 10:41 | Aderonke Olowojoba | 2025-11-24 10:39 | 2025-11-24 10:41 | 130 | 2025-11-24 10:39 | 2025-11-24 10:41 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006459280 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 17:10 | Patrick Okoro | 2025-11-26 17:09 | 2025-11-26 17:11 | 128 | 2025-11-26 17:09 | 2025-11-26 17:11 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site cleared without intervention
NOCINC0006468058 | External Reconciliation | Site Down | P4 | IHS_ANA_1112A | AN0760 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 21:30 | Oluwatoyin Fagite | 2025-11-27 21:29 | 2025-11-27 21:31 | 127 | 2025-11-27 21:29 | 2025-11-27 21:31 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Najib Musa | Kingsley Ohakwe | Kingsley Ohakwe | Fady Safwat | Aliyu Garuba |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006451302 | External Reconciliation | Site Down | P3 | IHS_LFG_0001B | KW4585 | IBD | Ibadan | Kwara | 3 - Low | KW0412 | WEST |  | 2025-11-25 19:59 | Precious Attah | 2025-11-25 19:59 | 2025-11-25 20:01 | 127 | 2025-11-25 19:59 | 2025-11-25 20:01 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006449815 | External Reconciliation | Site Down | P3 | IHS_EKI_0014B | EK2270 | IBD | Ibadan | Ekiti | 3 - Low | EK0452 | WEST |  | 2025-11-25 16:05 | Yewande Adeagbo | 2025-11-25 16:04 | 2025-11-25 16:06 | 127 | 2025-11-25 16:04 | 2025-11-25 16:06 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwafemi Oluwasegun |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site is up with no intervention.
NOCINC0006485138 | Internal Reconciliation | Site Down | P2 | IHS_EKI_0788A | T3763 | IBD | Ibadan | Ekiti | 3 - Low | EK0423 | WEST |  | 2025-11-30 07:42 | Kandervil Uwah | 2025-11-30 07:41 | 2025-11-30 07:43 | 127 | 2025-11-30 07:41 | 2025-11-30 07:43 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Sarafadeen Olasupo |  |  | Ibrahim Akinpelu | Sarafadeen Olasupo |  | Mohammed Momoh | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | site was up without intervention
NOCINC0006460090 | External Reconciliation | Site Down | P2 | IHS_BEN_0060B | ED5102 | IBD | Asaba | Edo | 3 - Low | ED0487 | SOUTH SOUTH |  | 2025-11-26 19:29 | Azeezat Badmus | 2025-11-26 19:29 | 2025-11-26 19:31 | 127 | 2025-11-26 19:29 | 2025-11-26 19:31 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Kazeem Ajiboye |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | site cleared with no technical intervention
NOCINC0006478249 | Internal Reconciliation | Site Down | P2 | IHS_OYO_1183H | OY2646 | IBD | Ibadan | Oyo | 3 - Low | OY1430 | WEST |  | 2025-11-29 09:33 | Aishat Oyedeji | 2025-11-29 09:33 | 2025-11-29 09:35 | 126 | 2025-11-29 09:33 | 2025-11-29 09:35 | 0:02 | SPS | Equipment Repair | Passive | Control Panel | ATS-AMF Issue | 2 / 2 | MTN NG, Airtel NG |  | Oremade Yusuf |  | Iyiola Azeez | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Faulty ATS was worked on | Faulty ATS was worked on
NOCINC0006467411 | External Reconciliation | Site Down | P1 | IHS_DEL_0853A | T2719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-27 19:17:21@T2719_30 Emevor Orogun Road | 2025-11-27 19:29 | System Administrator | 2025-11-27 19:24 | 2025-11-27 19:26 | 125 | 2025-11-27 19:24 | 2025-11-27 19:26 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006461512 | External Reconciliation | Site Down | P4 | IHS_DEL_0905A | T2768 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 00:04 | Ezinne Ubachukwu | 2025-11-27 00:03 | 2025-11-27 00:05 | 124 | 2025-11-27 00:03 | 2025-11-27 00:05 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006439226 | External Reconciliation | Site Down | P3 | IHS_EDO_1338B | - | - | Asaba | Edo | 3 - Low | ED0854 | SOUTH SOUTH |  | 2025-11-24 10:26 | Evelyn Emagurehor | 2025-11-24 10:25 | 2025-11-24 10:27 | 124 | 2025-11-24 10:25 | 2025-11-24 10:27 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Hammed Abubakar |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006465264 | External Reconciliation | Site Down | P3 | IHS_OND_0891A | OD2405 | IBD | Ibadan | Ondo | 3 - Low | ON0672 | WEST |  | 2025-11-27 13:56 | Iyesioluwa Ola | 2025-11-27 13:55 | 2025-11-27 13:57 | 124 | 2025-11-27 13:55 | 2025-11-27 13:57 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | John Fakayode |  | Dasaba Moses | Soye West | Ugwu Samuel Nnamdi |  | Ezekiel Sunday | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site restored without technical intervention
NOCINC0006439674 | External Reconciliation | Site Down | P1 | IHS_EDO_0755A | T0230 | IBD | Asaba | Edo | 3 - Low | ED0450 | SOUTH SOUTH |  | 2025-11-24 12:03 | Evelyn Emagurehor | 2025-11-24 12:03 | 2025-11-24 12:05 | 123 | 2025-11-24 12:03 | 2025-11-24 12:05 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006448852 | External Reconciliation | Site Down | P3 | IHS_AUC_0005B | ED4922 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 13:55 | Emmanuel Faleti | 2025-11-25 13:54 | 2025-11-25 13:56 | 123 | 2025-11-25 13:54 | 2025-11-25 13:56 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006474489 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0912A | T2782 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 18:16 | Abundance Otunola | 2025-11-28 18:15 | 2025-11-28 18:17 | 123 | 2025-11-28 18:15 | 2025-11-28 18:17 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Victor Ezeh |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006467049 | External Reconciliation | Site Down | P3 | IHS_EDO_1032A | ED4943 | IBD | Asaba | Edo | 3 - Low | ED0808 | SOUTH SOUTH |  | 2025-11-27 18:22 | Bukola Olabanji | 2025-11-27 18:20 | 2025-11-27 18:22 | 123 | 2025-11-27 18:20 | 2025-11-27 18:22 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | AZUBUIKE EMEH | Shagba Terkula | Emeh Azubike | Cornelius Yakubu | Elochukwu Umeohana |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006442399 | External Reconciliation | Site Down | P4 | IHS_DEL_1078A | DL0413 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-24 16:52:38@DL0413_Akwiewhe Owhe Comm | 2025-11-24 17:09 | System Administrator | 2025-11-24 16:58 | 2025-11-24 17:00 | 122 | 2025-11-24 16:58 | 2025-11-24 17:00 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Success Azuka |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter-fail and clear without any technical intervention. | Site inter-fail and clear without any technical intervention.
NOCINC0006486019 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 10:53 | Ayomide Akindolie | 2025-11-30 10:53 | 2025-11-30 10:55 | 122 | 2025-11-30 10:53 | 2025-11-30 10:55 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006481502 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0870A | T2742 | ASB | Asaba | Delta | 3 - Low | DL1269 | SOUTH SOUTH |  | 2025-11-29 16:49 | Ayomide Akindolie | 2025-11-29 16:49 | 2025-11-29 16:51 | 121 | 2025-11-29 16:49 | 2025-11-29 16:51 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006452224 | External Reconciliation | Site Down | P3 | IHS_OND_0722E | OD4844 | - | Ibadan | Ondo | 3 - Low | ON0694 | WEST |  | 2025-11-25 22:14 | Ihuoma Opurum | 2025-11-25 22:10 | 2025-11-25 22:12 | 120 | 2025-11-25 22:10 | 2025-11-25 22:12 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Usman Hammed |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage. Site was restored without intervention.
NOCINC0006451124 | External Reconciliation | Site Down | P4 | IHS_ANA_0795A | T4050 | ASB | Asaba | Anambra | 3 - Low | - | - | OML Fault@2025-11-25 19:00:35@T4050_CoSiteHotelMarina | 2025-11-25 19:13 | System Administrator | 2025-11-25 19:04 | 2025-11-25 19:06 | 120 | 2025-11-25 19:04 | 2025-11-25 19:06 | 0:02 | 3rd Party | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG | [7 empty] | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006456803 | External Reconciliation | Site Down | P4 | IHS_KWA_0904A | KW4575 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-26 11:08 | Titus Tosin | 2025-11-26 11:08 | 2025-11-26 11:10 | 120 | 2025-11-26 11:08 | 2025-11-26 11:10 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006482957 | Internal Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-29 21:06 | Okusanya Joseph | 2025-11-29 21:06 | 2025-11-29 21:08 | 120 | 2025-11-29 21:06 | 2025-11-29 21:08 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006460620 | External Reconciliation | Site Down | P2 | IHS_DEL_1185A | DL0719 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-26 20:46:51@DL0719_NO 6 Old Warri Road Okuvweri | 2025-11-26 20:59 | System Administrator | 2025-11-26 20:53 | 2025-11-26 20:55 | 120 | 2025-11-26 20:53 | 2025-11-26 20:55 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006473066 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 14:54 | Azeezat Badmus | 2025-11-28 14:52 | 2025-11-28 14:54 | 120 | 2025-11-28 14:52 | 2025-11-28 14:54 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | site cleared with no technical intervention
NOCINC0006456665 | External Reconciliation | Site Down | P1 | IHS_EKI_0835A | EK3388 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-26 10:39 | Iyesioluwa Ola | 2025-11-26 10:39 | 2025-11-26 10:41 | 120 | 2025-11-26 10:39 | 2025-11-26 10:41 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ajayi Samuel | Ajayi Samuel |  | Abiola Adegbiji | Babalola Babajide |  | Ayomide Adeyemo | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Site restored without technical intervention
NOCINC0006451925 | External Reconciliation | Site Down | P4 | IHS_OYO_0975A | T3575 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 21:10 | Ihuoma Opurum | 2025-11-25 21:09 | 2025-11-25 21:11 | 120 | 2025-11-25 21:09 | 2025-11-25 21:11 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Muhammad Aliyu |  |  | Paul Akpomie | Muhammad Aliyu |  | Uche Kanu | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site was restored without intervention.
NOCINC0006488864 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 17:59 | Tracy Osarumwense | 2025-11-30 17:59 | 2025-11-30 18:01 | 118 | 2025-11-30 17:59 | 2025-11-30 18:01 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006487599 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0925A | T2913 | ASB | Asaba | Delta | 3 - Low | DL0767 | SOUTH SOUTH | Site Abis control link broken@2025-11-30 14:15:22@DL0767 | 2025-11-30 14:44 | System Administrator | 2025-11-30 14:15 | 2025-11-30 14:46 | 1858 | 2025-11-30 14:44 | 2025-11-30 14:46 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006460559 | External Reconciliation | Site Down | P2 | IHS_DEL_1185A | DL0719 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 20:48 | Tracy Osarumwense | 2025-11-26 20:48 | 2025-11-26 20:50 | 118 | 2025-11-26 20:48 | 2025-11-26 20:50 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006469560 | External Reconciliation | Site Down | P3 | IHS_EDO_1087C | ED5376 | IBD | Asaba | Edo | 3 - Low | ED0734 | SOUTH SOUTH |  | 2025-11-28 02:57 | Emmanuel Faleti | 2025-11-28 02:57 | 2025-11-28 02:58 | 118 | 2025-11-28 02:57 | 2025-11-28 02:58 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Edwin Emehian | Achebe Chigozie | Omoragbon Austin | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006447397 | External Reconciliation | Site Down | P2 | IHS_OND_0934A | OD2516 | IBD | Ibadan | Ondo | 3 - Low | ON0578 | WEST |  | 2025-11-25 11:10 | Yewande Adeagbo | 2025-11-25 11:09 | 2025-11-25 11:11 | 117 | 2025-11-25 11:09 | 2025-11-25 11:11 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Anawanti Kingsley |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site is up with no intervention.
NOCINC0006480940 | Internal Reconciliation | Site Down | P2 | IHS_DEL_1185A | DL0719 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-29 15:31 | Quadri Ogundare | 2025-11-29 15:30 | 2025-11-29 15:32 | 117 | 2025-11-29 15:30 | 2025-11-29 15:32 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006481464 | Internal Reconciliation | Site Down | P2 | IHS_DEL_0870A | T2742 | ASB | Asaba | Delta | 3 - Low | DL1269 | SOUTH SOUTH |  | 2025-11-29 16:42 | Ayomide Akindolie | 2025-11-29 16:41 | 2025-11-29 16:43 | 116 | 2025-11-29 16:41 | 2025-11-29 16:43 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Taiwo Lawal |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006456465 | External Reconciliation | Site Down | P3 | IHS_ANA_0903A | T4182 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 10:07 | Oluwatoyin Fagite | 2025-11-26 10:07 | 2025-11-26 10:09 | 116 | 2025-11-26 10:07 | 2025-11-26 10:09 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obinna Festus | Festus Obinna | Festus Obinna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006439497 | External Reconciliation | Site Down | P2 | IHS_DEL_0957A | T2919 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 11:20 | Ezinne Ubachukwu | 2025-11-24 11:20 | 2025-11-24 11:22 | 116 | 2025-11-24 11:20 | 2025-11-24 11:22 | 0:02 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006489019 | Internal Reconciliation | Site Down | P1 | IHS_OYO_1015A | OY2859 | IBD | Ibadan | Oyo | 3 - Low | OY1002 | WEST |  | 2025-11-30 18:25 | Aishat Oyedeji | 2025-11-30 18:25 | 2025-11-30 18:27 | 115 | 2025-11-30 18:25 | 2025-11-30 18:27 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention
NOCINC0006470997 | External Reconciliation | Site Down | P4 | IHS_OYO_0036B | OY4298 | IBD | Ibadan | Oyo | 3 - Low | OY1674 | West |  | 2025-11-28 09:36 | Okusanya Joseph | 2025-11-28 09:36 | 2025-11-28 09:38 | 115 | 2025-11-28 09:36 | 2025-11-28 09:38 | 0:02 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006460448 | External Reconciliation | Site Down | P2 | IHS_DEL_0964A | DL2989 | ASB | Asaba | Delta | 3 - Low | - | - | CSL Fault@2025-11-26 20:12:51@DL2989_Azigbo_Lane_Sapele | 2025-11-26 20:26 | System Administrator | 2025-11-26 20:19 | 2025-11-26 20:20 | 115 | 2025-11-26 20:19 | 2025-11-26 20:20 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kelvin Nwanji | Onita Solomon | Onita Solomon | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006480524 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0816A | T3236 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-29 14:31 | Evelyn Emagurehor | 2025-11-29 14:31 | 2025-11-29 14:33 | 114 | 2025-11-29 14:31 | 2025-11-29 14:33 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006448037 | External Reconciliation | Site Down | P3 | IHS_BEN_0756E | ED5132 | IBD | Asaba | Edo | 3 - Low | ED0742 | SOUTH SOUTH |  | 2025-11-25 12:22 | Oluwatomisin Sogbesan | 2025-11-25 12:22 | 2025-11-25 12:24 | 113 | 2025-11-25 12:22 | 2025-11-25 12:24 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006471246 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0860A | T3327 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 10:16 | Muhammed Hashirudeen | 2025-11-28 10:15 | 2025-11-28 10:17 | 113 | 2025-11-28 10:15 | 2025-11-28 10:17 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adeoti Ogunbiyi |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006482576 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1054A | OY2803 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-29 19:52 | Favour Ahize | 2025-11-29 19:51 | 2025-11-29 19:52 | 113 | 2025-11-29 19:51 | 2025-11-29 19:52 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Alaba |  |  | Paul Akpomie | Oluwaseun Alaba |  | Luke Eke | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short Duration Outage
NOCINC0006448897 | External Reconciliation | Site Down | P4 | IHS_KWA_0908A | KW4573 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-25 14:00 | Yewande Adeagbo | 2025-11-25 14:00 | 2025-11-25 14:02 | 112 | 2025-11-25 14:00 | 2025-11-25 14:02 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adelola Dagunduro |  |  | Paul Akpomie | Adelola Dagunduro |  | Rilwan Akeem | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site is up with no intervention.
NOCINC0006443560 | External Reconciliation | Site Down | P4 | IHS_KWA_0903A | KW4576 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-24 20:13 | Azeezat Adekunle | 2025-11-24 20:12 | 2025-11-24 20:13 | 111 | 2025-11-24 20:12 | 2025-11-24 20:13 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006439286 | External Reconciliation | Site Down | P3 | IHS_EDO_1224B | ED6178 | IBD | Asaba | Edo | 3 - Low | ED0807 | SOUTH SOUTH |  | 2025-11-24 10:39 | Evelyn Emagurehor | 2025-11-24 10:35 | 2025-11-24 10:37 | 110 | 2025-11-24 10:35 | 2025-11-24 10:37 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Hammed Abubakar |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006463381 | External Reconciliation | Site Down | P1 | IHS_KWA_0776A | T3142 | IBD | Ibadan | Kwara | 3 - Low | - | - |  | 2025-11-27 09:37 | Titus Tosin | 2025-11-27 09:35 | 2025-11-27 09:37 | 110 | 2025-11-27 09:35 | 2025-11-27 09:37 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Faturiti Olakunle |  |  | Soye West | Goddey Nwokedigbo Peter |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify | 8 | Short duration outage. Site was up with no intervention
NOCINC0006467073 | External Reconciliation | Site Down | P1 | IHS_DEL_1020A | DL0113 | ASB | Asaba | Delta | 3 - Low | DL0742 | SOUTH SOUTH |  | 2025-11-27 18:28 | Bukola Olabanji | 2025-11-27 18:27 | 2025-11-27 18:28 | 110 | 2025-11-27 18:27 | 2025-11-27 18:28 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006486188 | Internal Reconciliation | Site Down | P2 | IHS_OND_0934A | OD2516 | IBD | Ibadan | Ondo | 3 - Low | ON0578 | WEST |  | 2025-11-30 11:18 | Yewande Adeagbo | 2025-11-30 11:17 | 2025-11-30 11:18 | 110 | 2025-11-30 11:17 | 2025-11-30 11:18 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Anawanti Kingsley |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site is up with no intervention.
NOCINC0006450758 | External Reconciliation | Site Down | P3 | IHS_OND_0705E | OD4731 | IBD | Ibadan | Ondo | 3 - Low | ON0812 | WEST |  | 2025-11-25 18:17 | Yewande Adeagbo | 2025-11-25 18:16 | 2025-11-25 18:18 | 110 | 2025-11-25 18:16 | 2025-11-25 18:18 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site is up with no intervention.
NOCINC0006452377 | External Reconciliation | Site Down | P2 | IHS_KWA_0865A | KW2378 | IBD | Ibadan | Kwara | 3 - Low | KW0388 | WEST |  | 2025-11-25 22:49 | Azeezat Adekunle | 2025-11-25 22:48 | 2025-11-25 22:50 | 109 | 2025-11-25 22:48 | 2025-11-25 22:50 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Bolariwa Taiwo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 2 | Site came up without any technical intervention
NOCINC0006475873 | Internal Reconciliation | Site Down | P2 | IHS_OND_0777A | T3405 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-28 21:46 | Iyesioluwa Ola | 2025-11-28 21:45 | 2025-11-28 21:47 | 109 | 2025-11-28 21:45 | 2025-11-28 21:47 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored without technical intervention
NOCINC0006464344 | External Reconciliation | Site Down | P3 | IHS_ANA_1219A | AN0603 | ASB | Asaba | Anambra | 3 - Low | AN0959 | SOUTH EAST |  | 2025-11-27 11:50 | Gbemisola Adedeji | 2025-11-27 11:49 | 2025-11-27 11:50 | 108 | 2025-11-27 11:49 | 2025-11-27 11:50 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006458424 | External Reconciliation | Site Down | P2 | IHS_EDO_0708E | ED5092 | IBD | Asaba | Edo | 3 - Low | ED0568 | SOUTH SOUTH |  | 2025-11-26 14:56 | Emmanuel Faleti | 2025-11-26 14:54 | 2025-11-26 14:56 | 108 | 2025-11-26 14:54 | 2025-11-26 14:56 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | SAHEED SHONDE | Babatunde Olayiwola | Shonde Saheed | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006471821 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0902A | KW4577 | IBD | Ibadan | Kwara | 3 - Low | KW0457 | WEST |  | 2025-11-28 11:31 | Praise Okezie | 2025-11-28 11:30 | 2025-11-28 11:32 | 107 | 2025-11-28 11:30 | 2025-11-28 11:32 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006457485 | External Reconciliation | Site Down | P3 | IHS_OSU_0993C | OS4733 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 12:31 | Sheriff Salami | 2025-11-26 12:31 | 2025-11-26 12:33 | 106 | 2025-11-26 12:31 | 2025-11-26 12:33 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short outage duration, Site restored with no intervention
NOCINC0006465403 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 14:13 | Bukola Olabanji | 2025-11-27 14:13 | 2025-11-27 14:14 | 105 | 2025-11-27 14:13 | 2025-11-27 14:14 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Short duration outage
NOCINC0006451246 | External Reconciliation | Site Down | P3 | IHS_OYO_1414B | - | - | Ibadan | Oyo | 3 - Low | OY1366 | WEST |  | 2025-11-25 19:51 | Precious Attah | 2025-11-25 19:50 | 2025-11-25 19:51 | 105 | 2025-11-25 19:50 | 2025-11-25 19:51 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006456145 | External Reconciliation | Site Down | P4 | IHS_ANA_0795A | T4050 | ASB | Asaba | Anambra | 3 - Low | - | - | OML Fault@2025-11-26 08:57:15@T4050_CoSiteHotelMarina | 2025-11-26 09:10 | System Administrator | 2025-11-26 09:08 | 2025-11-26 09:10 | 105 | 2025-11-26 09:08 | 2025-11-26 09:10 | 0:02 | 3rd Party | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG | [7 empty] | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention
NOCINC0006460080 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-26 19:14:20@T0286_Hotel Marina Off Sokoto road O | 2025-11-26 19:26 | System Administrator | 2025-11-26 19:23 | 2025-11-26 19:25 | 105 | 2025-11-26 19:23 | 2025-11-26 19:25 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006486645 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0940A | T2439 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-30 12:28 | Tracy Osarumwense | 2025-11-30 12:28 | 2025-11-30 12:30 | 104 | 2025-11-30 12:28 | 2025-11-30 12:30 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006483708 | Internal Reconciliation | Site Down | P2 | IHS_KWA_0874A | KW2380 | ABJ | Ibadan | Niger | 3 - Low | - | - |  | 2025-11-29 23:15 | Okusanya Joseph | 2025-11-29 23:15 | 2025-11-29 23:16 | 104 | 2025-11-29 23:15 | 2025-11-29 23:16 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Victor Agahiu |  |  | Soye West | Oboh Oseyeieomo |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006472153 | Internal Reconciliation | Site Down | P2 | IHS_OSU_0042B | OS4285 | IBD | Ibadan | Osun | 3 - Low | OS0738 | WEST |  | 2025-11-28 12:29 | Praise Okezie | 2025-11-28 12:28 | 2025-11-28 12:30 | 104 | 2025-11-28 12:28 | 2025-11-28 12:30 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006439849 | External Reconciliation | Site Down | P2 | IHS_EDO_1013A | ED2165 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-24 12:41 | Oluwatomisin Sogbesan | 2025-11-24 12:41 | 2025-11-24 12:43 | 103 | 2025-11-24 12:41 | 2025-11-24 12:43 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006463879 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-27 10:26:00@OY1229 | 2025-11-27 10:56 | System Administrator | 2025-11-27 10:26 | 2025-11-27 10:28 | 103 | 2025-11-27 10:26 | 2025-11-27 10:28 | 0:02 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006462979 | External Reconciliation | Site Down | P2 | IHS_DEL_1025A | DL0333 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 08:02 | Tracy Osarumwense | 2025-11-27 08:02 | 2025-11-27 08:04 | 102 | 2025-11-27 08:02 | 2025-11-27 08:04 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | EMMANUEL NDINYENMA |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006458560 | External Reconciliation | Site Down | P3 | IHS_AUC_0005B | ED4922 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-26 15:14 | Emmanuel Faleti | 2025-11-26 15:13 | 2025-11-26 15:15 | 100 | 2025-11-26 15:13 | 2025-11-26 15:15 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006459070 | External Reconciliation | Site Down | P2 | IHS_ANA_0843A | T4140 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 16:31 | Patrick Okoro | 2025-11-26 16:30 | 2025-11-26 16:32 | 100 | 2025-11-26 16:30 | 2025-11-26 16:32 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without intervention
NOCINC0006463550 | External Reconciliation | Site Down | P4 | IHS_OSU_0875A | OS3995 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-27 10:03 | Okusanya Joseph | 2025-11-27 10:01 | 2025-11-27 10:03 | 100 | 2025-11-27 10:01 | 2025-11-27 10:03 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006448667 | External Reconciliation | Site Down | P3 | IHS_OSU_0715E | OS2634 | IBD | Ibadan | Osun | 3 - Low | OS0744 | WEST |  | 2025-11-25 13:41 | Marvellous Emecheta | 2025-11-25 13:39 | 2025-11-25 13:41 | 100 | 2025-11-25 13:39 | 2025-11-25 13:41 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Odufu Friday |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006462437 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-27 05:21:35@T0286_Hotel Marina Off Sokoto road O | 2025-11-27 05:43 | System Administrator | 2025-11-27 05:41 | 2025-11-27 05:43 | 100 | 2025-11-27 05:41 | 2025-11-27 05:43 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006474976 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1364B | OY1004 | IBD | Ibadan | Oyo | 3 - Low | OY1596 | WEST |  | 2025-11-28 19:31 | Mutmainnah Saba | 2025-11-28 19:30 | 2025-11-28 19:32 | 100 | 2025-11-28 19:30 | 2025-11-28 19:32 | 0:02 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | BANKOLE SODIQ |  | Filani Oluwatobi | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006474325 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0940A | T2439 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 17:52 | Quadri Ogundare | 2025-11-28 17:51 | 2025-11-28 17:52 | 99 | 2025-11-28 17:51 | 2025-11-28 17:52 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 1 | Short duration outage
NOCINC0006448731 | External Reconciliation | Site Down | P3 | IHS_AUC_0005B | ED4922 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 13:47 | Emmanuel Faleti | 2025-11-25 13:46 | 2025-11-25 13:48 | 98 | 2025-11-25 13:46 | 2025-11-25 13:48 | 0:02 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mohammed Idris | Oluwadamilare Bamidele | Oluwadamilare Bamidele | Deepak Kumar | Peter Anekwe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006437473 | External Reconciliation | Site Down | P2 | IHS_OSU_0928A | OS2627 | IBD | Ibadan | Osun | 3 - Low | OS0865 | WEST |  | 2025-11-24 02:21 | Okusanya Joseph | 2025-11-24 02:20 | 2025-11-24 02:21 | 98 | 2025-11-24 02:20 | 2025-11-24 02:21 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006470115 | External Reconciliation | Site Down | P3 | IHS_OSU_0993C | OS4733 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-28 06:29 | Marvellous Emecheta | 2025-11-28 06:29 | 2025-11-28 06:30 | 97 | 2025-11-28 06:29 | 2025-11-28 06:30 | 0:02 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006483076 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0834A | T3516 | IBD | Ibadan | Oyo | 3 - Low | OY1082 | WEST | Site Abis control link broken@2025-11-29 20:56:47@OY1082 | 2025-11-29 21:26 | System Administrator | 2025-11-29 20:57 | 2025-11-29 20:58 | 96 | 2025-11-29 20:57 | 2025-11-29 20:58 | 0:02 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Enoch Fidelis | Adewale Adejumo | Adewale Adejumo | Abiola Adegbiji | Habeeb Adepoju |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006461113 | External Reconciliation | Site Down | P1 | IHS_EDO_1164H | ED2101 | IBD | Asaba | Edo | 3 - Low | ED0956 | SOUTH SOUTH |  | 2025-11-26 22:26 | Oluwatomisin Sogbesan | 2025-11-26 22:26 | 2025-11-26 22:28 | 96 | 2025-11-26 22:26 | 2025-11-26 22:28 | 0:02 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006489782 | Internal Reconciliation | Site Down | P4 | IHS_OYO_1444B | - | - | Ibadan | Oyo | 3 - Low | OY1564 | WEST |  | 2025-11-30 21:16 | Valentine Adinnu | 2025-11-30 21:15 | 2025-11-30 21:17 | 95 | 2025-11-30 21:15 | 2025-11-30 21:17 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Effiong Asukwo |  |  |  | Effiong Asukwo |  | Victor Olanrewaju | Sanjib Sen | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006465324 | External Reconciliation | Site Down | P2 | IHS_EKI_0856A | EK2285 | IBD | Ibadan | Ekiti | 3 - Low | EK0401 | WEST |  | 2025-11-27 14:02 | Kandervil Uwah | 2025-11-27 13:59 | 2025-11-27 14:00 | 95 | 2025-11-27 13:59 | 2025-11-27 14:00 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Onewokae Ajiri |  |  | Ibrahim Akinpelu | Onewokae Ajiri |  | Sheriff Bolajoko | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site was up without intervention.
NOCINC0006446713 | External Reconciliation | Site Down | P3 | IHS_ANA_0903A | T4182 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-25 09:49 | Oluwatoyin Fagite | 2025-11-25 09:48 | 2025-11-25 09:49 | 95 | 2025-11-25 09:48 | 2025-11-25 09:49 | 0:02 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obinna Festus | Festus Obinna | Festus Obinna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006458459 | External Reconciliation | Site Down | P2 | IHS_OND_0717E | OD2062 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 15:01 | Tunji Adejumo | 2025-11-26 15:01 | 2025-11-26 15:02 | 95 | 2025-11-26 15:01 | 2025-11-26 15:02 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | John Kunamon |  |  | Ibrahim Akinpelu | John Kunamon |  | Fagbemi Solomon | Ibrahim Yekini | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site restored with no intervention
NOCINC0006482549 | Internal Reconciliation | Site Down | P2 | IHS_OYO_0701E | OY4307 | IBD | Ibadan | Oyo | 3 - Low | OY0911 | WEST |  | 2025-11-29 19:47 | Aishat Oyedeji | 2025-11-29 19:47 | 2025-11-29 19:48 | 93 | 2025-11-29 19:47 | 2025-11-29 19:48 | 0:02 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | BASHIR ABDULRASAQ |  |  | Ridwan Adepoju | Adewumi Akinpelu |  | Monjolaoluwa Omotoso | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, no intervention
NOCINC0006446043 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-25 07:52:16@OY1229 | 2025-11-25 08:44 | System Administrator | 2025-11-25 07:52 | 2025-11-25 07:54 | 91 | 2025-11-25 07:52 | 2025-11-25 07:54 | 0:02 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006442911 | External Reconciliation | Site Down | P3 | IHS_OND_0705E | OD4731 | IBD | Ibadan | Ondo | 3 - Low | ON0812 | WEST |  | 2025-11-24 18:23 | Yewande Adeagbo | 2025-11-24 18:23 | 2025-11-24 18:24 | 90 | 2025-11-24 18:23 | 2025-11-24 18:24 | 0:02 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site is up with no intervention.
NOCINC0006437174 | External Reconciliation | Site Down | P1 | IHS_OYO_0034B | OY4245 | IBD | Ibadan | Kwara | 3 - Low | KW0313 | WEST | WCDMA BASE STATION OUT OF USE@2025-11-24 00:56:01@W_KW0313 | 2025-11-24 01:16 | System Administrator | 2025-11-24 00:56 | 2025-11-24 00:58 | 90 | 2025-11-24 00:56 | 2025-11-24 00:58 | 0:02 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mohammed Soliu |  | Abdulraman Odunola | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006439869 | External Reconciliation | Site Down | P3 | IHS_EDO_1061C | ED6114 | IBD | Asaba | Edo | 3 - Low | ED0953 | SOUTH SOUTH |  | 2025-11-24 12:44 | Ayomide Akindolie | 2025-11-24 12:44 | 2025-11-24 12:46 | 89 | 2025-11-24 12:44 | 2025-11-24 12:46 | 0:01 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006471212 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 10:11 | Bukola Olabanji | 2025-11-28 10:08 | 2025-11-28 10:09 | 89 | 2025-11-28 10:08 | 2025-11-28 10:09 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 3 | Short duration outage
NOCINC0006471101 | External Reconciliation | Site Down | P4 | IHS_ANA_1084A | AN0312 | ASB | Asaba | Anambra | 3 - Low | AN0772 | SOUTH EAST |  | 2025-11-28 09:53 | Gbemisola Adedeji | 2025-11-28 09:52 | 2025-11-28 09:54 | 88 | 2025-11-28 09:52 | 2025-11-28 09:54 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Philip Oko | Philip Okoh | Philip Okoh | Henry Wanogho | Ifeanyi Chukusa |  | Quadri Olatokunbo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006443239 | External Reconciliation | Site Down | P2 | IHS_KWA_0902A | KW4577 | IBD | Ibadan | Kwara | 3 - Low | KW0457 | WEST |  | 2025-11-24 19:18 | Precious Attah | 2025-11-24 19:18 | 2025-11-24 19:19 | 88 | 2025-11-24 19:18 | 2025-11-24 19:19 | 0:01 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006451253 | External Reconciliation | Site Down | P3 | IHS_LFG_0001B | KW4585 | IBD | Ibadan | Kwara | 3 - Low | KW0412 | WEST |  | 2025-11-25 19:53 | Precious Attah | 2025-11-25 19:52 | 2025-11-25 19:53 | 87 | 2025-11-25 19:52 | 2025-11-25 19:53 | 0:01 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Musa Mohammed Mohammed |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Ibrahim Akinpelu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006461099 | External Reconciliation | Site Down | P3 | IHS_EDO_1205B | ED6221 | IBD | Asaba | Edo | 3 - Low | ED0733 | SOUTH SOUTH |  | 2025-11-26 22:21 | Oluwatomisin Sogbesan | 2025-11-26 22:21 | 2025-11-26 22:22 | 87 | 2025-11-26 22:21 | 2025-11-26 22:22 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006456843 | External Reconciliation | Site Down | P4 | IHS_DEL_0905A | T2768 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 11:14 | Patrick Okoro | 2025-11-26 11:13 | 2025-11-26 11:15 | 87 | 2025-11-26 11:13 | 2025-11-26 11:15 | 0:01 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Justine Onovughakpor |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006439625 | External Reconciliation | Site Down | P1 | IHS_DEL_0993A | DL0005 | ASB | Asaba | Delta | 3 - Low | DL1260 | SOUTH SOUTH |  | 2025-11-24 11:46 | Ayomide Akindolie | 2025-11-24 11:46 | 2025-11-24 11:48 | 86 | 2025-11-24 11:46 | 2025-11-24 11:48 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Chinedu Nwaowulor | Ugochukwu Ahukanna | Ugochukwu Ahukanna | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006461646 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 00:22 | Tracy Osarumwense | 2025-11-27 00:22 | 2025-11-27 00:23 | 85 | 2025-11-27 00:22 | 2025-11-27 00:23 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006458463 | External Reconciliation | Site Down | P2 | IHS_EDO_1167H | ED2057 | IBD | Asaba | Edo | 3 - Low | ED0735 | SOUTH SOUTH |  | 2025-11-26 15:01 | Emmanuel Faleti | 2025-11-26 15:01 | 2025-11-26 15:02 | 84 | 2025-11-26 15:01 | 2025-11-26 15:02 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | MTN NG |  | Abdulrasheed Saheed |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006473541 | Internal Reconciliation | Site Down | P4 | IHS_DEL_1082A | DL0083 | ASB | Asaba | Delta | 3 - Low | - | - | Huawei 2G SiteDown@2025-11-28 15:52:06@ | 2025-11-28 16:05 | System Administrator | 2025-11-28 15:56 | 2025-11-28 15:58 | 84 | 2025-11-28 15:56 | 2025-11-28 15:58 | 0:01 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Johnson Ejeh | Dare Oguyemi | Dare Oguyemi | Akanbi Oluwafemi | Jerry Igwe |  | Taiwo Durodola | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006440494 | External Reconciliation | Site Down | P1 | IHS_DEL_0886A | T2716 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 13:28 | Tracy Osarumwense | 2025-11-24 13:28 | 2025-11-24 13:29 | 84 | 2025-11-24 13:28 | 2025-11-24 13:29 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Emuesiri� Sunday | Ojo Emuda | Ojo Emuda | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 5 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006451144 | External Reconciliation | Site Down | P3 | IHS_BEN_0016V | - | - | Asaba | Edo | 3 - Low | ED0812 | SOUTH SOUTH |  | 2025-11-25 19:19 | Emmanuel Faleti | 2025-11-25 19:18 | 2025-11-25 19:20 | 83 | 2025-11-25 19:18 | 2025-11-25 19:20 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006446620 | External Reconciliation | Site Down | P3 | IHS_ANA_1487B | - | - | Asaba | Anambra | 3 - Low | AN0819 | SOUTH EAST |  | 2025-11-25 09:35 | Patrick Okoro | 2025-11-25 09:35 | 2025-11-25 09:37 | 83 | 2025-11-25 09:35 | 2025-11-25 09:37 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify | 2 | Site cleared without intervention | Site cleared without intervention
NOCINC0006463203 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 08:56 | Uthman Akinola | 2025-11-27 08:56 | 2025-11-27 08:58 | 81 | 2025-11-27 08:56 | 2025-11-27 08:58 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006471272 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0704E | ED5317 | IBD | Asaba | Edo | 3 - Low | ED0716 | SOUTH SOUTH |  | 2025-11-28 10:18 | Muhammed Hashirudeen | 2025-11-28 10:18 | 2025-11-28 10:19 | 79 | 2025-11-28 10:18 | 2025-11-28 10:19 | 0:01 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006470708 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-28 08:08:04@OY1229 | 2025-11-28 08:59 | System Administrator | 2025-11-28 08:08 | 2025-11-28 08:09 | 77 | 2025-11-28 08:08 | 2025-11-28 08:09 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006483557 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0882A | T3304 | IBD | Asaba | Edo | 3 - Low | ED0654 | SOUTH SOUTH |  | 2025-11-29 22:37 | Muhammed Hashirudeen | 2025-11-29 22:36 | 2025-11-29 22:37 | 76 | 2025-11-29 22:36 | 2025-11-29 22:37 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Omobolaji JELILI |  |  | Erik Nwodo | John Wekpe |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006476093 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1002A | T4877 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-28 22:24 | Femi Olanipekun | 2025-11-28 22:24 | 2025-11-28 22:25 | 73 | 2025-11-28 22:24 | 2025-11-28 22:25 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obinna Clinton |  |  | Erik Nwodo | Nwigbo Chijioke |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006467346 | External Reconciliation | Site Down | P4 | IHS_DEL_1186A | DL0488 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 19:13 | Bukola Olabanji | 2025-11-27 19:13 | 2025-11-27 19:14 | 73 | 2025-11-27 19:13 | 2025-11-27 19:14 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006473078 | Internal Reconciliation | Site Down | P3 | IHS_EKI_0818A | T3774 | IBD | Ibadan | Ekiti | 3 - Low | EK0480 | WEST |  | 2025-11-28 14:56 | Testimony Akinyemi | 2025-11-28 14:56 | 2025-11-28 14:57 | 72 | 2025-11-28 14:56 | 2025-11-28 14:57 | 0:01 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | SHORT DURATION OUTAGE
NOCINC0006485872 | Internal Reconciliation | Site Down | P1 | IHS_EDO_0804A | T3230 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-30 10:15 | Oluwatomisin Sogbesan | 2025-11-30 10:14 | 2025-11-30 10:15 | 72 | 2025-11-30 10:14 | 2025-11-30 10:15 | 0:01 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006467481 | External Reconciliation | Site Down | P2 | IHS_OSU_0089C | OS4333 | IBD | Ibadan | Osun | 3 - Low | OS0974 | WEST |  | 2025-11-27 19:43 | Sheriff Salami | 2025-11-27 19:34 | 2025-11-27 19:35 | 70 | 2025-11-27 19:34 | 2025-11-27 19:35 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Adejumobi Tunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify | 1 | Short outage duration, Site restored with no intervention
NOCINC0006463581 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-27 09:17:17@OY1229 | 2025-11-27 10:09 | System Administrator | 2025-11-27 09:17 | 2025-11-27 09:18 | 68 | 2025-11-27 09:17 | 2025-11-27 09:18 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006452808 | External Reconciliation | Site Down | P1 | IHS_DEL_0797A | T2636 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 23:39 | Ayokunle Samuel | 2025-11-25 23:39 | 2025-11-25 23:40 | 67 | 2025-11-25 23:39 | 2025-11-25 23:40 | 0:01 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter failed and cleared without any technical intervention. | Site inter failed and cleared without any technical intervention.
NOCINC0006467889 | External Reconciliation | Site Down | P3 | IHS_ANA_1316B | AN3147 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-27 20:53 | Oluwatoyin Fagite | 2025-11-27 20:53 | 2025-11-27 20:54 | 66 | 2025-11-27 20:53 | 2025-11-27 20:54 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ukoha Lekwa |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006466489 | External Reconciliation | Site Down | P3 | IHS_WAR_0023B | DL0771 | ASB | Asaba | Delta | 3 - Low | DL0595 | SOUTH SOUTH |  | 2025-11-27 16:46 | Mary Odefemi | 2025-11-27 16:46 | 2025-11-27 16:47 | 66 | 2025-11-27 16:46 | 2025-11-27 16:47 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006472633 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1159A | AN0758 | ASB | Asaba | Anambra | 3 - Low | - | - | CSL Fault@2025-11-28 13:36:44@AN0758_Egbeme Isi afor Road | 2025-11-28 13:49 | System Administrator | 2025-11-28 13:43 | 2025-11-28 13:44 | 64 | 2025-11-28 13:43 | 2025-11-28 13:44 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Henry Ikede | Ayeni Banabas | Ayeni Banabas | Henry Wanogho | Ifeanyi Chukusa |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006487528 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0960A | DL2994 | ASB | Asaba | Delta | 3 - Low | DL0799 | SOUTH SOUTH | Site Abis control link broken@2025-11-30 13:51:57@DL0799 | 2025-11-30 14:31 | System Administrator | 2025-11-30 13:52 | 2025-11-30 14:42 | 3004 | 2025-11-30 14:41 | 2025-11-30 14:42 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006487307 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0705E | DL0737 | ASB | Asaba | Delta | 3 - Low | DL0575 | SOUTH SOUTH |  | 2025-11-30 13:50 | Ayomide Akindolie | 2025-11-30 13:50 | 2025-11-30 13:51 | 64 | 2025-11-30 13:50 | 2025-11-30 13:51 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Urhoma Joseph |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006438459 | External Reconciliation | Site Down | P1 | IHS_OYO_0034B | OY4245 | IBD | Ibadan | Kwara | 3 - Low | KW0313 | WEST | WCDMA BASE STATION OUT OF USE@2025-11-24 08:01:46@W_KW0313 | 2025-11-24 08:21 | System Administrator | 2025-11-24 08:02 | 2025-11-24 08:03 | 64 | 2025-11-24 08:02 | 2025-11-24 08:03 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mohammed Soliu |  | Abdulraman Odunola | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006451336 | External Reconciliation | Site Down | P1 | IHS_OYO_1015A | OY2859 | IBD | Ibadan | Oyo | 3 - Low | OY1002 | WEST |  | 2025-11-25 20:06 | Victor Otugo | 2025-11-25 20:06 | 2025-11-25 20:07 | 62 | 2025-11-25 20:06 | 2025-11-25 20:07 | 0:01 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olaitan Olajide |  |  | Abiola Adegbiji | Yusuf Gyang |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, Site came up without intervention
NOCINC0006438282 | External Reconciliation | Site Down | P1 | IHS_ANA_0788A | T0286 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 07:31 | Uthman Akinola | 2025-11-24 07:30 | 2025-11-24 07:31 | 62 | 2025-11-24 07:30 | 2025-11-24 07:31 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Obele Kingsley |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006469188 | External Reconciliation | Site Down | P2 | IHS_KWA_0874A | KW2380 | ABJ | Ibadan | Niger | 3 - Low | - | - | CSL Fault@2025-11-28 00:37:42@KW2380_Nepa Hydro Staion Jebba | 2025-11-28 00:50 | System Administrator | 2025-11-28 00:43 | 2025-11-28 00:44 | 61 | 2025-11-28 00:43 | 2025-11-28 00:44 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Victor Agahiu |  |  | Soye West | Oboh Oseyeieomo |  | Taofiq Agboola | Mofoluso Ogunseye | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short outage duration, Site restored with no intervention
NOCINC0006482928 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-29 20:40:02@OY1229 | 2025-11-29 21:01 | System Administrator | 2025-11-29 20:40 | 2025-11-29 20:41 | 61 | 2025-11-29 20:40 | 2025-11-29 20:41 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006461508 | External Reconciliation | Site Down | P3 | IHS_OYO_1414B | - | - | Ibadan | Oyo | 3 - Low | OY1366 | WEST |  | 2025-11-27 00:03 | Precious Attah | 2025-11-27 00:03 | 2025-11-27 00:04 | 59 | 2025-11-27 00:03 | 2025-11-27 00:04 | 0:01 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site came up without any technical intervention
NOCINC0006461462 | External Reconciliation | Site Down | P1 | IHS_DEL_0941A | T2449 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-26 23:52 | Tracy Osarumwense | 2025-11-26 23:52 | 2025-11-26 23:53 | 57 | 2025-11-26 23:52 | 2025-11-26 23:53 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Odili Ifeanyichukwu | Emmanuel Iwegbue | Emmanuel Iwegbue | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006482880 | Internal Reconciliation | Site Down | P1 | IHS_OYO_0034B | OY4245 | IBD | Ibadan | Kwara | 3 - Low | KW0313 | WEST | WCDMA BASE STATION OUT OF USE@2025-11-29 20:17:33@W_KW0313 | 2025-11-29 20:54 | System Administrator | 2025-11-29 20:18 | 2025-11-29 20:19 | 57 | 2025-11-29 20:18 | 2025-11-29 20:19 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Mohammed Soliu |  | Abdulraman Odunola | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006483421 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-29 21:50:10@OY1229 | 2025-11-29 22:16 | System Administrator | 2025-11-29 21:50 | 2025-11-29 21:51 | 57 | 2025-11-29 21:50 | 2025-11-29 21:51 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006438369 | External Reconciliation | Site Down | P3 | IHS_KWA_0900A | KW4610 | IBD | Ibadan | Kwara | 3 - Low | KW0477 | WEST |  | 2025-11-24 07:51 | Okusanya Joseph | 2025-11-24 07:51 | 2025-11-24 07:52 | 55 | 2025-11-24 07:51 | 2025-11-24 07:52 | 0:01 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oluwaseun Makinde |  |  | Ogbuma Oluwafemi | Benny Harcourt |  | Sodiq Yakubu | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006468584 | External Reconciliation | Site Down | P3 | IHS_OND_0959A | OD2521 | IBD | Ibadan | Ondo | 3 - Low | ON0590 | WEST |  | 2025-11-27 23:12 | Mary Elaigwu | 2025-11-27 23:11 | 2025-11-27 23:12 | 55 | 2025-11-27 23:11 | 2025-11-27 23:12 | 0:01 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Oluwaseun Awolope |  |  | Ibrahim Akinpelu | Oluwaseun Awolope |  | John Momoh | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site was restored with no technical intervention
NOCINC0006488319 | Internal Reconciliation | Site Down | P1 | IHS_OSU_0793A | T3039 | IBD | Ibadan | Osun | 3 - Low | OS0834 | WEST |  | 2025-11-30 16:31 | Favour Ahize | 2025-11-30 16:22 | 2025-11-30 16:23 | 54 | 2025-11-30 16:22 | 2025-11-30 16:23 | 0:01 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Taiwo Hazzan |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Jelili Salami | Sanjib Sen | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short Duration Outage
NOCINC0006471162 | Internal Reconciliation | Site Down | P4 | IHS_EDO_0860A | T3327 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-28 10:04 | Muhammed Hashirudeen | 2025-11-28 10:03 | 2025-11-28 10:04 | 54 | 2025-11-28 10:03 | 2025-11-28 10:04 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Adeoti Ogunbiyi |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006457592 | External Reconciliation | Site Down | P3 | IHS_OSU_0063B | OS2656 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 12:46 | Marvellous Emecheta | 2025-11-26 12:45 | 2025-11-26 12:46 | 53 | 2025-11-26 12:45 | 2025-11-26 12:46 | 0:01 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Abdulsalami Onukaba Onukaba |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006487115 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0960A | DL2994 | ASB | Asaba | Delta | 3 - Low | DL0799 | SOUTH SOUTH | Site Abis control link broken@2025-11-30 13:06:05@DL0799 | 2025-11-30 13:26 | System Administrator | 2025-11-30 13:06 | 2025-11-30 13:40 | 2031 | 2025-11-30 13:39 | 2025-11-30 13:40 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | James Victor |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006448385 | External Reconciliation | Site Down | P1 | IHS_DEL_0835A | T2664 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 13:08 | Tracy Osarumwense | 2025-11-25 13:08 | 2025-11-25 13:08 | 51 | 2025-11-25 13:08 | 2025-11-25 13:08 | 0:01 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006463029 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-27 07:42:10@OY1229 | 2025-11-27 08:16 | System Administrator | 2025-11-27 07:42 | 2025-11-27 07:43 | 51 | 2025-11-27 07:42 | 2025-11-27 07:43 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006437297 | External Reconciliation | Site Down | P3 | IHS_OYO_0719E | - | - | Ibadan | Oyo | 3 - Low | OY1116 | WEST | WCDMA BASE STATION OUT OF USE@2025-11-24 01:03:46@W_OY1116 | 2025-11-24 01:24 | System Administrator | 2025-11-24 01:04 | 2025-11-24 01:05 | 49 | 2025-11-24 01:04 | 2025-11-24 01:05 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Aramide Kazeem |  | Aramide Kazeem | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006450973 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | NodeB is out of service@2025-11-25 18:22:45@OY1229 | 2025-11-25 18:56 | System Administrator | 2025-11-25 18:23 | 2025-11-25 18:24 | 49 | 2025-11-25 18:23 | 2025-11-25 18:24 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006456120 | External Reconciliation | Site Down | P3 | IHS_BEN_0016V | - | - | Asaba | Edo | 3 - Low | ED0812 | SOUTH SOUTH |  | 2025-11-26 09:03 | Emmanuel Faleti | 2025-11-26 09:02 | 2025-11-26 09:03 | 47 | 2025-11-26 09:02 | 2025-11-26 09:03 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | DELE ASAGUNLA |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006486668 | Internal Reconciliation | Site Down | P2 | IHS_OND_0878A | OD3392 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 12:33 | Yewande Adeagbo | 2025-11-30 12:31 | 2025-11-30 12:32 | 47 | 2025-11-30 12:31 | 2025-11-30 12:32 | 0:01 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Ajibade Sikiru |  | Dasaba Moses | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site is up with no intervention.
NOCINC0006483619 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | The link between the server and the ME is broken@2025-11-29 22:27:49@OY1229(31229) | 2025-11-29 22:54 | System Administrator | 2025-11-29 22:28 | 2025-11-29 22:29 | 46 | 2025-11-29 22:28 | 2025-11-29 22:29 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006437978 | External Reconciliation | Site Down | P4 | IHS_OSU_0946A | OS2639 | IBD | Ibadan | Osun | 3 - Low | OS0933 | WEST | NE3SWS AGENT NOT RESPONDING TO REQUESTS@2025-11-24 05:35:55@MRBTS-801499 | 2025-11-24 05:56 | System Administrator | 2025-11-24 05:36 | 2025-11-24 05:37 | 44 | 2025-11-24 05:36 | 2025-11-24 05:37 | 0:01 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Lawal Adetunji |  |  | Ogbuma Oluwafemi | Olorundare Peter |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006464979 | External Reconciliation | Site Down | P3 | IHS_OYO_0889A | T3855 | IBD | Ibadan | Oyo | 3 - Low | OY1174 | WEST |  | 2025-11-27 13:10 | Titus Tosin | 2025-11-27 13:10 | 2025-11-27 13:10 | 42 | 2025-11-27 13:10 | 2025-11-27 13:10 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | KELLY VWEDE |  | Ededem Asuquo | Ridwan Adepoju | Ahmed Ibrahim |  | Adedayo Adejengbe | Mofoluso Ogunseye | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006483315 | Internal Reconciliation | Site Down | P2 | IHS_BEN_0072C | ED5117 | IBD | Asaba | Edo | 3 - Low | ED0467 | SOUTH SOUTH |  | 2025-11-29 21:58 | Muhammed Hashirudeen | 2025-11-29 21:58 | 2025-11-29 21:58 | 38 | 2025-11-29 21:58 | 2025-11-29 21:58 | 0:01 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | SIMON SUNDAY | Opayemi Segun | Ismaila Adeyinka | Erik Nwodo | Elochukwu Umeohana |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006475219 | Internal Reconciliation | Site Down | P3 | IHS_BEN_0751E | ED5323 | IBD | Asaba | Edo | 3 - Low | ED0602 | SOUTH SOUTH |  | 2025-11-28 20:12 | Muhammed Hashirudeen | 2025-11-28 20:11 | 2025-11-28 20:12 | 35 | 2025-11-28 20:11 | 2025-11-28 20:12 | 0:01 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Olusoji Megbodofo |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site restored without intervention.
NOCINC0006489071 | Internal Reconciliation | Site Down | P4 | IHS_EKI_0013B | EK2273 | IBD | Ibadan | Ekiti | 3 - Low | - | - |  | 2025-11-30 18:35 | Oluwadara Bankole | 2025-11-30 18:34 | 2025-11-30 18:34 | 34 | 2025-11-30 18:34 | 2025-11-30 18:34 | 0:01 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwafemi Dare |  |  | Ibrahim Akinpelu |  |  | Oluwafemi Dare | Ibrahim Yekini | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site came up without any technical intervention. | Short duration outage. Site came up without any technical intervention.
NOCINC0006449273 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-25 14:27:33@OY1229 | 2025-11-25 14:51 | System Administrator | 2025-11-25 14:28 | 2025-11-25 14:28 | 33 | 2025-11-25 14:28 | 2025-11-25 14:28 | 0:01 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006457479 | External Reconciliation | Site Down | P3 | IHS_OND_0705E | OD4731 | IBD | Ibadan | Ondo | 3 - Low | ON0812 | WEST | NE Is Disconnected@2025-11-26 12:16:15@LOD4731 | 2025-11-26 12:30 | System Administrator | 2025-11-26 12:16 | 2025-11-26 12:17 | 32 | 2025-11-26 12:16 | 2025-11-26 12:17 | 0:01 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site restored without technical intervention
NOCINC0006455712 | External Reconciliation | Site Down | P2 | IHS_OND_0777A | T3405 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-26 07:38 | Ihuoma Opurum | 2025-11-26 07:38 | 2025-11-26 07:39 | 30 | 2025-11-26 07:38 | 2025-11-26 07:39 | 0:00 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Marvellous Oyefeso |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was restored without intervention.
NOCINC0006438444 | External Reconciliation | Site Down | P4 | IHS_DEL_0968A | DL0008 | ASB | Asaba | Delta | 3 - Low | DL0930 | SOUTH SOUTH |  | 2025-11-24 08:16 | Uthman Akinola | 2025-11-24 08:15 | 2025-11-24 08:16 | 26 | 2025-11-24 08:15 | 2025-11-24 08:16 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | SITE RESTORED WITHOUT TECHNICAL INTERVENTION
NOCINC0006460016 | External Reconciliation | Site Down | P3 | IHS_OSU_0715E | OS2634 | IBD | Ibadan | Osun | 3 - Low | OS0744 | WEST |  | 2025-11-26 19:14 | Marvellous Emecheta | 2025-11-26 19:13 | 2025-11-26 19:13 | 25 | 2025-11-26 19:13 | 2025-11-26 19:13 | 0:00 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Odufu Friday |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site was up with no intervention.
NOCINC0006450682 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-25 17:22:53@OY1229 | 2025-11-25 18:01 | System Administrator | 2025-11-25 17:23 | 2025-11-25 17:23 | 24 | 2025-11-25 17:23 | 2025-11-25 17:23 | 0:00 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006482695 | Internal Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-29 19:55:53@OY1229 | 2025-11-29 20:19 | System Administrator | 2025-11-29 19:56 | 2025-11-29 19:56 | 23 | 2025-11-29 19:56 | 2025-11-29 19:56 | 0:00 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006474053 | Internal Reconciliation | Site Down | P3 | IHS_OND_0705E | OD4731 | IBD | Ibadan | Ondo | 3 - Low | ON0812 | WEST | NodeB Unavailable@2025-11-28 16:57:32@UOD4731 | 2025-11-28 17:13 | System Administrator | 2025-11-28 16:58 | 2025-11-28 16:58 | 23 | 2025-11-28 16:58 | 2025-11-28 16:58 | 0:00 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Philip Zakari |  |  | Ibrahim Akinpelu | Philip Zakari |  | Ahmed Omosebi | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site restored without technical intervention
NOCINC0006440343 | External Reconciliation | Site Down | P1 | IHS_DEL_1055A | DL0416 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-24 13:16 | Tracy Osarumwense | 2025-11-24 13:16 | 2025-11-24 13:16 | 21 | 2025-11-24 13:16 | 2025-11-24 13:16 | 0:00 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Mark Chibogu |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify | 2 | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006449068 | External Reconciliation | Site Down | P1 | IHS_EDO_0755A | T0230 | IBD | Asaba | Edo | 3 - Low | ED0450 | SOUTH SOUTH |  | 2025-11-25 14:30 | Oluwatomisin Sogbesan | 2025-11-25 14:30 | 2025-11-25 14:30 | 21 | 2025-11-25 14:30 | 2025-11-25 14:30 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | Airtel NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006464299 | External Reconciliation | Site Down | P3 | IHS_OYO_0719E | - | - | Ibadan | Oyo | 3 - Low | OY1116 | WEST | WCDMA BASE STATION OUT OF USE@2025-11-27 11:19:58@W_OY1116 | 2025-11-27 11:44 | System Administrator | 2025-11-27 11:20 | 2025-11-27 11:20 | 20 | 2025-11-27 11:20 | 2025-11-27 11:20 | 0:00 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Aramide Kazeem |  | Aramide Kazeem | Ridwan Adepoju | Olufemi Akinlusi |  | Ahmed Solihu | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage, site restored without intervention
NOCINC0006448270 | External Reconciliation | Site Down | P2 | IHS_OND_0934A | OD2516 | IBD | Ibadan | Ondo | 3 - Low | ON0578 | WEST |  | 2025-11-25 12:52 | Yewande Adeagbo | 2025-11-25 12:52 | 2025-11-25 12:52 | 17 | 2025-11-25 12:52 | 2025-11-25 12:52 | 0:00 | Biswal | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Anawanti Kingsley |  |  | Abiola Adegbiji | Ojuekaiye Abidemi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage, site is up with no intervention.
NOCINC0006450711 | External Reconciliation | Site Down | P2 | IHS_EDO_1193H | ED2097 | IBD | Asaba | Edo | 3 - Low | ED0498 | SOUTH SOUTH |  | 2025-11-25 18:08 | Oluwatomisin Sogbesan | 2025-11-25 18:06 | 2025-11-25 18:06 | 16 | 2025-11-25 18:06 | 2025-11-25 18:06 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | OYEYODE MUIDEEN |  |  | Erik Nwodo | John Wekpe |  | Bolurin Sunday | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006441721 | External Reconciliation | Site Down | P1 | IHS_ANA_0922A | T4179 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-24 16:18 | Aderonke Olowojoba | 2025-11-24 16:17 | 2025-11-24 16:17 | 16 | 2025-11-24 16:17 | 2025-11-24 16:17 | 0:00 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Uchenna Asadu | Asadu Uchenna | Asadu Uchenna | Henry Wanogho | Ifeanyi Chukusa |  | Oghenekaro Okpako | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention
NOCINC0006477278 | Internal Reconciliation | Site Down | P3 | IHS_EDO_0704E | ED5317 | IBD | Asaba | Edo | 3 - Low | ED0716 | SOUTH SOUTH |  | 2025-11-29 05:46 | Elizabeth Apata | 2025-11-29 05:45 | 2025-11-29 05:45 | 9 | 2025-11-29 05:45 | 2025-11-29 05:45 | 0:00 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | SAMSON AYOKANMI | Egbo Osokanachi | Cyril Okogun | Cornelius Yakubu | Elochukwu Umeohana |  | Ayo Ade | Taofeek Lawal | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site restored without technical intervention.
NOCINC0006465802 | External Reconciliation | Site Down | P4 | IHS_ANA_1185A | AN0665 | ASB | Asaba | Anambra | 3 - Low | AN1133 | SOUTH EAST |  | 2025-11-27 15:11 | Gbemisola Adedeji | 2025-11-27 15:05 | 2025-11-27 15:05 | 8 | 2025-11-27 15:05 | 2025-11-27 15:05 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Ezimeruwe ANTHONY |  |  | Erik Nwodo | Nwigbo Chijioke |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Short duration outage, site came up without technical intervention | Short duration outage, site came up without technical intervention
NOCINC0006481336 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1032A | DL0344 | ASB | Asaba | Delta | 3 - Low | DL1259 | SOUTH SOUTH |  | 2025-11-29 16:23 | Quadri Ogundare | 2025-11-29 16:18 | 2025-11-29 16:18 | 7 | 2025-11-29 16:18 | 2025-11-29 16:18 | 0:00 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 2 / 2 | MTN NG, Airtel NG |  | Arinze� Okafor |  |  | Cornelius Yakubu | Jerry Igwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention
NOCINC0006459765 | External Reconciliation | Site Down | P3 | IHS_OSU_0063B | OS2656 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 18:37 | Sheriff Salami | 2025-11-26 18:36 | 2025-11-26 18:36 | 6 | 2025-11-26 18:36 | 2025-11-26 18:36 | 0:00 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Abdulsalami Onukaba Onukaba |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Lateef Alao | Sanjib Sen | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short outage duration, Site restored with no intervention
NOCINC0006452003 | External Reconciliation | Site Down | P4 | IHS_OYO_1000A | T3892 | IBD | Ibadan | Oyo | 3 - Low | - | - |  | 2025-11-25 21:22 | Ihuoma Opurum | 2025-11-25 21:22 | 2025-11-25 21:22 | 5 | 2025-11-25 21:22 | 2025-11-25 21:22 | 0:00 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Muhammad Aliyu |  |  | Paul Akpomie | Muhammad Aliyu |  | Uche Kanu | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site was restored without intervention.
NOCINC0006467541 | External Reconciliation | Site Down | P1 | IHS_OND_0900A | T3647 | IBD | Ibadan | Osun | 3 - Low | - | - | Cascaded Incident from TTO6752574 - Cascade Removed From TTO6752574 | 2025-11-27 19:52 | Bosede Kutelu | 2025-11-27 19:44 | 2025-11-27 19:44 | 3 | 2025-11-27 19:44 | 2025-11-27 19:44 | 0:00 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Abdulsalami Onukaba Onukaba |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P1 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006489128 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1076A | AN0058 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-30 18:48 | Abundance Otunola | 2025-11-30 18:46 | 2025-11-30 18:46 | 1 | 2025-11-30 18:46 | 2025-11-30 18:46 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Moses Kenechukwu | Kenneth Ogbodo | Kenneth Ogbodo | Fady Safwat | Aliyu Garuba |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006447815 | External Reconciliation | Site Down | P1 | IHS_ANA_1001A | T4870 | ASB | Asaba | Anambra | 3 - Low | AN0530 | SOUTH EAST |  | 2025-11-25 11:53 | Patrick Okoro | 2025-11-25 11:48 | 2025-11-25 11:48 | 1 | 2025-11-25 11:48 | 2025-11-25 11:48 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Esan Enoch | Kenneth Nlerum | Kenneth Nlerum | Fady Safwat | Aliyu Garuba |  | Francisca Onyenwe | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006454672 | External Reconciliation | Site Down | P3 | IHS_DEL_1224B | - | - | Asaba | Delta | 3 - Low | DL0925 | SOUTH SOUTH |  | 2025-11-26 01:58 | Ayomide Akindolie | 2025-11-26 01:58 | 2025-11-26 01:58 | 1 | 2025-11-26 01:58 | 2025-11-26 01:58 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | David Uja |  |  | Erik Nwodo | John Wekpe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006477610 | Internal Reconciliation | Site Down | P4 | IHS_OND_0849A | T3940 | IBD | Ibadan | Ondo | 3 - Low | - | - | CSL Fault@2025-11-29 07:12:42@T3940_EmureIleTown | 2025-11-29 07:25 | System Administrator | 2025-11-29 07:20 | 2025-11-29 07:20 | 1 | 2025-11-29 07:20 | 2025-11-29 07:20 | 0:00 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Kadiri Victor |  |  | Ogbuma Oluwafemi | Chiedozie Ekwueme |  | Enoch Ajekiigbe | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Site restored without technical intervention
NOCINC0006440916 | External Reconciliation | Site Down | P1 | IHS_WAR_0740C | DL1063 | ASB | Asaba | Delta | 3 - Low | DL0937 | SOUTH SOUTH |  | 2025-11-24 14:27 | Tracy Osarumwense | 2025-11-24 14:26 | 2025-11-24 14:26 | 1 | 2025-11-24 14:26 | 2025-11-24 14:26 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006443497 | External Reconciliation | Site Down | P1 | IHS_BEN_0726E | ED6177 | IBD | Asaba | Edo | 3 - Low | ED0473 | SOUTH SOUTH |  | 2025-11-24 20:02 | Evelyn Emagurehor | 2025-11-24 20:02 | 2025-11-24 20:02 | 1 | 2025-11-24 20:02 | 2025-11-24 20:02 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | Airtel NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006472281 | Internal Reconciliation | Site Down | P1 | IHS_DEL_0872A | T2780 | ASB | Asaba | Delta | 3 - Low | - | - | Cascaded Incident from TTO6757900 - Cascade Removed From TTO6757900 | 2025-11-28 12:50 | Abundance Otunola | 2025-11-28 12:45 | 2025-11-28 12:45 | 1 | 2025-11-28 12:45 | 2025-11-28 12:45 | 0:00 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Tobore Ganyoran | Tobore Ganyoran | Tobore Ganyoran | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006470677 | External Reconciliation | Site Down | P3 | IHS_WAR_0740C | DL1063 | ASB | Asaba | Delta | 3 - Low | DL0937 | SOUTH SOUTH |  | 2025-11-28 08:54 | Bukola Olabanji | 2025-11-28 08:54 | 2025-11-28 08:54 | 1 | 2025-11-28 08:54 | 2025-11-28 08:54 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Egbo Osokanachi |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006474176 | Internal Reconciliation | Site Down | P3 | IHS_WAR_0744C | DL1072 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-28 17:32 | Bukola Olabanji | 2025-11-28 17:31 | 2025-11-28 17:31 | 1 | 2025-11-28 17:31 | 2025-11-28 17:31 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Shrt duration outage
NOCINC0006448035 | External Reconciliation | Site Down | P4 | IHS_DEL_0955A | T2713 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 12:21 | Ezinne Ubachukwu | 2025-11-25 12:21 | 2025-11-25 12:21 | 1 | 2025-11-25 12:21 | 2025-11-25 12:21 | 0:00 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KELECHI LEWIS |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up without technical intervention | Site came up without technical intervention
NOCINC0006466204 | External Reconciliation | Site Down | P1 | IHS_DEL_1107A | DL0092 | ASB | Asaba | Delta | 3 - Low | DL0660 | SOUTH SOUTH | Huawei 2G SiteDown@2025-11-27 15:45:24@DL0092 | 2025-11-27 16:00 | System Administrator | 2025-11-27 15:47 | 2025-11-27 15:47 | 1 | 2025-11-27 15:47 | 2025-11-27 15:47 | 0:00 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Babatunde Jimoh� |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006458381 | External Reconciliation | Site Down | P3 | IHS_ANA_1427H | AN0604 | ASB | Asaba | Anambra | 3 - Low | AN0720 | SOUTH EAST |  | 2025-11-26 14:50 | Akachukwu Ugwu | 2025-11-26 14:48 | 2025-11-26 14:48 | 1 | 2025-11-26 14:48 | 2025-11-26 14:48 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Onyema Ojimba |  |  | Erik Nwodo | Nwigbo Chijioke |  | Peter Ezeoke | Alioke Onyedikachukwu | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without any technical intervention (No diesel outage after validation) | Site cleared without any technical intervention (No diesel outage after validation)
NOCINC0006454963 | External Reconciliation | Site Down | P1 | IHS_DEL_1058A | DL0437 | ASB | Asaba | Delta | 3 - Low | DL0818 | SOUTH SOUTH |  | 2025-11-26 04:53 | Ayomide Akindolie | 2025-11-26 04:53 | 2025-11-26 04:53 | 1 | 2025-11-26 04:53 | 2025-11-26 04:53 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Iniobong Attat |  | Okon Edidiong | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006448278 | External Reconciliation | Site Down | P4 | IHS_DEL_0878A | T2722 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-25 12:54 | Patrick Okoro | 2025-11-25 12:27 | 2025-11-25 12:54 | 1599 | 2025-11-25 12:54 | 2025-11-25 12:54 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Monday Agha | Igwe Samuel | Igwe Samuel | Akanbi Oluwafemi | Jerry Igwe |  | Mary-Ann Okwukwe | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without intervention
NOCINC0006465468 | External Reconciliation | Site Down | P2 | IHS_OSU_0071B | OS4380 | IBD | Ibadan | Osun | 3 - Low | OS0864 | WEST |  | 2025-11-27 14:21 | Titus Tosin | 2025-11-27 14:20 | 2025-11-27 14:20 | 1 | 2025-11-27 14:20 | 2025-11-27 14:20 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | KENNET EPIH |  |  | Soye West | Ugwu Samuel Nnamdi |  | Yahaya Ambali | Paul Akpomie | Adegoke Abdulrahman | P2 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006459333 | External Reconciliation | Site Down | P1 | IHS_ANA_0786A | T0285/T6512 | ASB | Asaba | Anambra | 3 - Low | - | - |  | 2025-11-26 17:19 | Akachukwu Ugwu | 2025-11-26 17:16 | 2025-11-26 17:17 | 1 | 2025-11-26 17:16 | 2025-11-26 17:17 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Henry Ubawuchi |  |  | Erik Nwodo | Nwigbo Chijioke |  | Pascal Ojehomon | Cletus Enwefa | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, no intervention | Short duration outage, no intervention
NOCINC0006447085 | External Reconciliation | Site Down | P3 | IHS_DEL_1236B | - | - | Asaba | Delta | 3 - Low | DL0945 | SOUTH SOUTH |  | 2025-11-25 10:39 | Oluwatobiloba Are | 2025-11-25 10:38 | 2025-11-25 10:38 | 1 | 2025-11-25 10:38 | 2025-11-25 10:38 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | Airtel NG |  | Kehinde Adekanbi |  |  | Erik Nwodo | John Wekpe |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up without technical intervention. | Site came up without technical intervention.
NOCINC0006447784 | External Reconciliation | Site Down | P4 | IHS_WAR_0933B | DL3314 | ASB | Asaba | Delta | 3 - Low | DL0823 | SOUTH SOUTH |  | 2025-11-25 11:48 | Patrick Okoro | 2025-11-25 11:48 | 2025-11-25 11:48 | 1 | 2025-11-25 11:48 | 2025-11-25 11:48 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Kingsley Ekene |  |  | Erik Nwodo | John Wekpe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006439258 | External Reconciliation | Site Down | P3 | IHS_EDO_1061C | ED6114 | IBD | Asaba | Edo | 3 - Low | ED0953 | SOUTH SOUTH |  | 2025-11-24 10:33 | Ayomide Akindolie | 2025-11-24 10:33 | 2025-11-24 10:34 | 48 | 2025-11-24 10:33 | 2025-11-24 10:33 | 0:00 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Jude Audu | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006449810 | External Reconciliation | Site Down | P3 | IHS_EDO_0783A | T3263 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 16:04 | Oluwatomisin Sogbesan | 2025-11-25 16:01 | 2025-11-25 16:01 | 1 | 2025-11-25 16:01 | 2025-11-25 16:01 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Solomon Obaka |  |  | Erik Nwodo | John Wekpe |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify | 1 | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006472297 | Internal Reconciliation | Site Down | P4 | IHS_ANA_1071A | AN0307 | ASB | Asaba | Anambra | 3 - Low | - | - | Cascaded Incident from TTO6757900 - Cascade Removed From TTO6757900 | 2025-11-28 12:52 | Abundance Otunola | 2025-11-28 12:45 | 2025-11-28 12:45 | 1 | 2025-11-28 12:45 | 2025-11-28 12:45 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ime Francis | Lawrence Atuegbu | Lawrence Atuegbu | Fady Safwat | Aliyu Garuba |  | Doris Onoakpoyovwire | Alioke Onyedikachukwu | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006472766 | Internal Reconciliation | Site Down | P1 | IHS_DEL_1022A | DL0099 | ASB | Asaba | Delta | 3 - Low | DL0744 | SOUTH SOUTH |  | 2025-11-28 14:10 | Abundance Otunola | 2025-11-28 14:00 | 2025-11-28 14:00 | 1 | 2025-11-28 14:00 | 2025-11-28 14:00 | 0:00 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | ATORI ONOKPASA | Emmanuel Asuquo | Emmanuel Asuquo | Cornelius Yakubu | Elochukwu Umeohana |  | Efetobor Bobor | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation) | Site inter-failed and cleared on short duration without intervention. (No diesel outage after validation)
NOCINC0006449796 | External Reconciliation | Site Down | P1 | IHS_EDO_0797A | T3262 | IBD | Asaba | Edo | 3 - Low | - | - |  | 2025-11-25 16:03 | Oluwatomisin Sogbesan | 2025-11-25 16:01 | 2025-11-25 16:01 | 1 | 2025-11-25 16:01 | 2025-11-25 16:01 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Abiola Olabisi | Taofeek Lawal | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short Duration Outage, No Intervention | Short Duration Outage, No Intervention
NOCINC0006457803 | External Reconciliation | Site Down | P4 | IHS_OSU_0732E | OS4698 | IBD | Ibadan | Osun | 3 - Low | - | - |  | 2025-11-26 13:18 | Titus Tosin | 2025-11-26 13:18 | 2025-11-26 13:18 | 1 | 2025-11-26 13:18 | 2025-11-26 13:18 | 0:00 | IPT | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Ayodeji Oluwatayo |  |  | Ogbuma Oluwafemi | Sodiq Olabode |  | Toluwase Dada | Mofoluso Ogunseye | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site was up with no intervention
NOCINC0006466573 | External Reconciliation | Site Down | P1 | IHS_DEL_0772A | T2012 | ASB | Asaba | Delta | 3 - Low | - | - |  | 2025-11-27 16:59 | Mary Odefemi | 2025-11-27 16:59 | 2025-11-27 16:59 | 1 | 2025-11-27 16:59 | 2025-11-27 16:59 | 0:00 | BJ Bison NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oscar Ifeanyi |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Ray Erezi | Hygiene Ogor | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site cleared without technical intervention
NOCINC0006470666 | External Reconciliation | Site Down | P2 | IHS_EDO_0879A | T3332 | IBD | Asaba | Edo | 3 - Low | ED0563 | SOUTH SOUTH | Cascaded Incident from TTO6756114 - Cascade Removed From TTO6756114 | 2025-11-28 08:52 | Gbemisola Adedeji | 2025-11-28 08:47 | 2025-11-28 08:47 | 1 | 2025-11-28 08:47 | 2025-11-28 08:47 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 3 | MTN NG |  | Fatai Sherrif |  |  | Erik Nwodo | John Wekpe |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | site cleared with no technical intervention
NOCINC0006469770 | External Reconciliation | Site Down | P3 | IHS_OYO_1129B | OY1057 | IBD | Ibadan | Oyo | 3 - Low | OY1229 | WEST | Site Abis control link broken@2025-11-28 04:00:41@OY1229 | 2025-11-28 04:44 | System Administrator | 2025-11-28 04:01 | 2025-11-28 04:01 | 1 | 2025-11-28 04:01 | 2025-11-28 04:01 | 0:00 | SPS | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | ADEMOLA ADELEKE |  | Imole-Ayo Amoo | Ridwan Adepoju | ANIMASAHUN TOLULOPE |  | David Ojetokun | Paul Akpomie | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Site was restored without intervention
NOCINC0006462678 | External Reconciliation | Site Down | P1 | IHS_ANA_1065A | AN0202 | ASB | Asaba | Anambra | 3 - Low | AN0827 | SOUTH EAST |  | 2025-11-27 06:45 | Aderonke Olowojoba | 2025-11-27 06:45 | 2025-11-27 06:45 | 1 | 2025-11-27 06:45 | 2025-11-27 06:45 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Oladele Segun | David Ndubuisi | David Ndubuisi | Fady Safwat | Aliyu Garuba |  | Ifeanyi Oleh | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Short duration outage, site came up without any technical intervention | Short duration outage, site came up without any technical intervention
NOCINC0006468425 | External Reconciliation | Site Down | P4 | IHS_EDO_1051C | ED6129 | IBD | Asaba | Edo | 3 - Low | - | - | Cascaded Incident from TTO6753594 - Cascade Removed From TTO6753594 | 2025-11-27 22:32 | Emmanuel Faleti | 2025-11-27 22:23 | 2025-11-27 22:23 | 1 | 2025-11-27 22:23 | 2025-11-27 22:23 | 0:00 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | KINGSLEY OSHIOGWEMOH |  |  | Cornelius Yakubu | Elochukwu Umeohana |  | Evelyn Obafaiye | Taofeek Lawal | Abiodun Samuel | P4 | Nigeria | Do Not Notify |  | Site cleared without technical intervention | Site cleared without technical intervention
NOCINC0006455195 | External Reconciliation | Site Down | P3 | IHS_OND_0039B | OD4837 | IBD | Ibadan | Ondo | 3 - Low | ON0692 | WEST |  | 2025-11-26 05:54 | Testimony Akinyemi | 2025-11-26 05:50 | 2025-11-26 05:50 | 1 | 2025-11-26 05:50 | 2025-11-26 05:50 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Olatunde Babatunde |  |  | Soye West | Ugwu Samuel Nnamdi |  | Ibraheem Adeyekun | Opeyemi Adeagbo | Adegoke Abdulrahman | P3 | Nigeria | Do Not Notify |  | Short duration outage
NOCINC0006485790 | Internal Reconciliation | Site Down | P4 | IHS_OND_0951A | OD2528 | IBD | Ibadan | Ondo | 3 - Low | - | - |  | 2025-11-30 10:03 | Ihuoma Opurum | 2025-11-30 10:03 | 2025-11-30 10:03 | 1 | 2025-11-30 10:03 | 2025-11-30 10:03 | 0:00 | Inhouse | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 1 | MTN NG |  | Oluwaseun Awolope |  |  | Ibrahim Akinpelu | Oluwaseun Awolope |  | John Momoh | Opeyemi Adeagbo | Adegoke Abdulrahman | P4 | Nigeria | Do Not Notify |  | Short duration outage. Site was restored without intervention.
NOCINC0006479658 | Internal Reconciliation | Site Down | P1 | IHS_ANA_0976A | T4028 | ASB | Asaba | Anambra | 3 - Low | AN0735 | SOUTH EAST |  | 2025-11-29 12:37 | Kehinde Akinbowale | 2025-11-29 12:35 | 2025-11-29 12:35 | 1 | 2025-11-29 12:35 | 2025-11-29 12:35 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Moses Kenechukwu | Kenneth Ogbodo | Kenneth Ogbodo | Fady Safwat | Aliyu Garuba |  | Emmanuel Odo | Alioke Onyedikachukwu | Abiodun Samuel | P1 | Nigeria | Do Not Notify |  | Site was restored without technical intervention | Site was restored without technical intervention
NOCINC0006486453 | Internal Reconciliation | Site Down | P2 | IHS_EDO_1219B | ED6214 | IBD | Asaba | Edo | 3 - Low | ED0738 | SOUTH SOUTH |  | 2025-11-30 11:59 | Ayomide Akindolie | 2025-11-30 11:57 | 2025-11-30 11:57 | 1 | 2025-11-30 11:57 | 2025-11-30 11:57 | 0:00 | MPI NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Alade Olufemi Olufem | Kayode Emmanuel | Kayode Emmanuel | Deepak Kumar | Peter Anekwe |  | Clinton Duru | Hygiene Ogor | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | Site came up with no technical intervention (No diesel outage after validation)
NOCINC0006448638 | External Reconciliation | Site Down | P3 | IHS_DEL_0842A | T2703 | ASB | Asaba | Delta | 3 - Low | DL0228 | SOUTH SOUTH |  | 2025-11-25 13:37 | Patrick Okoro | 2025-11-25 13:36 | 2025-11-25 13:36 | 1 | 2025-11-25 13:36 | 2025-11-25 13:36 | 0:00 | Tyllium NGA | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | MTN NG |  | Victor Ezeh |  |  | Akanbi Oluwafemi | Jerry Igwe |  | Ebinipre Kosuowei | Cletus Enwefa | Abiodun Samuel | P3 | Nigeria | Do Not Notify |  | Site cleared without intervention | Site cleared without intervention
NOCINC0006443682 | External Reconciliation | Site Down | P2 | IHS_EDO_1023A | ED4913 | IBD | Asaba | Edo | 3 - Low | ED0497 | SOUTH SOUTH | Site Abis control link broken@2025-11-24 20:15:37@ED0497 | 2025-11-24 20:34 | System Administrator | 2025-11-24 20:16 | 2025-11-24 20:16 | 1 | 2025-11-24 20:16 | 2025-11-24 20:16 | 0:00 | Huawei | Short Duration Outage (SDO) | No Intervention | No Intervention | No Intervention | 1 / 2 | Airtel NG |  | Austin Egbase |  |  | Erik Nwodo | Elochukwu Umeohana |  | Kesiena Ogbodu | Taofeek Lawal | Abiodun Samuel | P2 | Nigeria | Do Not Notify |  | site cleared with no technical intervention